## CoverSheet
EDB Information Disclosure Requirements
Information Templates
Schedule 10a
| Company Name | Powerco Limited
| Disclosure Date | 2025-08-31
| Disclosure Year (year ended) | 2025-03-31
Template for Schedule 10a
Prepared 16 February 2024.

## TOC
Table of Contents
Schedule | Schedule name
10a | REPORT ON INTERRUPTIONS

## Instructions
Disclosure Template Instructions
This document forms Schedule 10a to the Electricity Distribution Information Disclosure (Targeted Review 2024) Amendment Determination 2024 [2024] NZCC 2.
The Schedules take the form of templates for use by EDBs when making disclosures under subclause 2.5.1 of the Electricity Distribution Information Disclosure Determination 2012.
Company Name and Dates
To prepare the templates for disclosure, the supplier's company name should be entered in cell C8, the date of the last day of the current (disclosure) year should be entered in cell C12, and the date on which the information is disclosed should be entered in cell C10 of the CoverSheet worksheet.
The cell C12 entry (current year) is used to calculate disclosure years in the column headings that show above some of the tables and in labels adjacent to some entry cells. It is also used to calculate the ‘For year ended’ date in the template title blocks (the title blocks are the light green shaded areas at the top of each template). The cell C8 entry (company name) is used in the template title blocks. Dates should be entered in day/month/year order (Example -"1 April 2023").
Data Entry Cells and Calculated Cells
Data entered into this workbook may be entered only into the data entry cells. Data entry cells are the bordered, unshaded areas (white cells) in each template. Under no circumstances should data be entered into the workbook outside a data entry cell.
In some cases, where the information for disclosure is able to be ascertained from disclosures elsewhere in the workbook, such information is disclosed in a calculated cell.
Validation Settings on Data Entry Cells
To maintain a consistency of format and to help guard against errors in data entry, some data entry cells test keyboard entries for validity and accept only a limited range of values. For example, entries may be limited to a list of category names, to values between 0% and 100%, or either a numeric entry or the text entry “N/A”. Where this occurs, a validation message will appear when data is being entered. These checks are applied to keyboard entries only and not, for example, to entries made using Excel’s copy and paste facility.
Inserting Additional Rows and Columns
The schedule 10a template may require additional rows to be inserted in tables marked 'include additional rows if needed' or similar. Column A schedule references should not be entered in additional rows, and should be deleted from additional rows that are created by copying and pasting rows that have schedule references.
Additional rows in the schedule 10a template must not be inserted directly above the first row or below the last row of a table. This is to ensure that entries made in the new row are included in the totals.
Description of Calculation References
Calculation cell formulas contain links to other cells within the same template or elsewhere in the workbook. Key cell references are described in a column to the right of each template. These descriptions are provided to assist data entry. Cell references refer to the row of the template and not the schedule reference.

## S10a.Interruptions
[15 empty] | Company Name | Powerco Limited
[15 empty] | For Year Ended | 2025-03-31
SCHEDULE 10a: REPORT ON INTERRUPTIONS
This schedule requires raw interruption data for the disclosure year. SAIDI and SAIFI is to be recorded using the multi-count approach.Where multiple feeders are affected, the interruption record is to be split into multiple interruptions, ie, one interruption record per feeder. This information is part of audited disclosure information (as defined in section 1.4 of this ID determination), and so is subject to the assurance report required by section 2.8.
sch ref
7 | 10a(i): Raw interruption data
8 |  | Interruption identifier | Circuit location | Sub-network (where applicable) | Feeder(s) affected by interruption | Start date (dd/mm/yyyy) | Start time (hh:mm:ss) | End date (dd/mm/yyyy) | End time (hh:mm:ss) | SAIDI value | SAIFI value | Number of ICPs interrupted | ICP interruption minutes | Planned or unplanned interruption (Class B or C) | Cause | Any explanation to help clarify the context of the interruption, including what the cause is if recorded as 'Other cause' | .
9 |  | JE25006966 | BURNSIDE | Western | BURNSIDE | 2025-03-31 | 9:58 | 2025-03-31 | 14:55 | 0.051469 | 0.00017381 | 63 | 18655 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Change 11kv pole 811023
10 |  | JE25008328 | EAST ST | Western | EAST ST | 2025-03-31 | 8:31 | 2025-03-31 | 15:15 | 0.082822 | 0.00085252 | 218 | 30019 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv pole 818515 with new top mount Entec switch | .
11 |  | JE25010272 | 692 DEVON ROAD, NEW PLYMOUTH | Western | KATERE 11 | 2025-03-31 | 0:14 | 2025-03-31 | 4:28 | 0.018789 | 0.00028417 | 103 | 6810 | Unplanned | ADVERSE ENVIRONMENT - FIRE | Tree on Fire in lines report by fire Services Event # F4181709 Feeder Tripped 00:14 O/C Isolated At Sw/gear 563/3 & 12376/1 Plus ABS 199 One tree trimming, other is either a noted or Protected tree. On call manager contacted, advised to trim second tree enough to clear issue. FM informed on how to proceed Lines cleared from trees., power restored | .
12 |  | JE25010277 | 295 FOREST ROAD,PAREWANUI,BULLS | Western | PAREWANUI | 2025-03-31 | 6:18 | 2025-03-31 | 7:51 | 0.00050936 | 5.5179e-06 | 2 | 185 | Unplanned | WILDLIFE - BIRD | Fuses Location: 4146 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 07:50 Cause: Bird Strike Weather (wind/rain): N Follow up required (select advisory)?N | .
13 |  | JE25010295 | 2679B LAKE FERRY ROAD,PIRINOA,FEATHERSTON | Western | PIRINOA | 2025-03-31 | 9:04 | 2025-03-31 | 9:33 | 0.041614 | 0.0014043 | 509 | 15083 | Unplanned | HUMAN ERROR - POTENTIAL SWITCHING ERROR | FM carrying out switching under NAPA 117051. FM operated incorrect ABS causing loss of supply to section of feeder. ABS S533 mistakenly opened instead of ABS S553. Once mistake discovered ABS S533 was closed & NAPA 117051 switching recommenced. | .
14 |  | JE25010467 | FORDELL | Western | FORDELL | 2025-03-31 | 19:39 | 2025-03-31 | 21:06 | 0.0021548 | 2.4831e-05 | 9 | 781 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 045 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 2105 Cause: Unknown Weather (wind/rain): fine Follow up required (select advisory)? | .
15 |  | JE25008042 | BIDEFORD | Western | BIDEFORD | 2025-03-30 | 9:15 | 2025-03-30 | 10:23 | 0.00093989 | 1.3795e-05 | 5 | 341 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install new mid span pole between pole 839444 and T2591 | .
16 |  | JE25010240 | 2 MOKOIA ROAD,MOKOIA,HAWERA | Western | MANAWAPOU RD | 2025-03-30 | 1:26 | 2025-03-30 | 4:19 | 0.014088 | 8.5528e-05 | 31 | 5106 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Fuses Location: Fuses WH105 No. Fuses: 2 Fuse Amp Size: TIME CLOSED: Cause: Blown Jumpers at Fuses WH 105 & WH 166 Weather (wind/rain): Calm Isolated at Fuses WH105 Fuses 6512 Open Then Fuses WH105 Closed | .
17 |  | JE25010246 | 89 PONGAKAWA SCHOOL ROAD,PONGAKAWA,TE PUKE | Eastern | OTAMARAKAU | 2025-03-30 | 1:56 | 2025-03-30 | 8:18 | 0.11981 | 0.0010374 | 376 | 43425 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11KV CB 2 Protection flags (nil where none): A B C Phase E/F CAUSE: Car V Pole Location: pole 218786 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): 2503025 Circuit patrolled and type: operational Weather (wind/rain): Fine LFI (Y/N + Comments): Yes but not in the area Follow up Required (select advisory)? Additional fault restoration comments: ABS SE7-018 would not open so had to take isolated area out some more DNO Number 2503025. Line was isolated at ABS's SE7-013, SE7-017, SE7-019, SE7-025, SE7-026 & IP746 to replace pole 218786 hit by car. | .
18 |  | JE25010268 | 2803 STATE HIGHWAY 4,MANGAMAHU,WANGANUI | Western | MAKIRIKIRI | 2025-03-30 | 20:51 | 2025-03-30 | 22:30 | 0.0021791 | 2.2072e-05 | 8 | 790 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 882 No. Fuses: 2 Fuse Amp Size: 8 Amp TIME CLOSED: 22:29 Cause: UNknown Weather (wind/rain): Raining Follow up required (select advisory)? N | .
19 |  | JE25006987 | WAITARA RD | Western | WAITARA RD | 2025-03-29 | 8:26 | 2025-03-29 | 9:45 | 0.00043831 | 5.5179e-06 | 2 | 159 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Tx 1319. Investigate low oil, repair if possible and top up oil | .
20 |  | JE25009956 | FEILDING 1 33kV | Western | FEILDING 1 33kV | 2025-03-29 | 23:01 | 2025-03-30 | 23:03 | 0.031901 | 0.018849 | 3416 | 11563 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Correct phasing on new 33kV switchboard so that matches existing site. This requires and A & C shift on the incoming circuit and also both out going circuits(tie cable and Sanson) | .
21 |  | JE25010228 | FEEDEF FAULT - KAURI POINT - LINDERMAN RD - SEC13513 | Eastern | LINDERMANN RD | 2025-03-29 | 18:19 | 2025-03-29 | 19:35 | 0.020768 | 0.00027314 | 99 | 7527 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11KV Sec 13513 Protection flags (nil where none): B & C Phase O/C E/F CAUSE: Unknown Location: Unknown Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): Fine Calm LFI (Y/N + Comments): Not in area Follow up Required (select advisory)? Additional fault restoration comments: Ground Mounted CB 13021-3 did a Auto Reclose at same time SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
22 |  | JE25010237 | 130 CANAL WEST ROAD,WAITAKARURU,THAMES | Eastern | PUHUNGA ISLAND RD | 2025-03-29 | 23:24 | 2025-03-29 | 23:25 | 0.00045047 | 0.00035039 | 127 | 163 | Unplanned | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | Voltage & Device ID: 11KV Rec 13066/2 Protection flags (nil where none): E/F Weather (wind/rain): Fine Follow up required (select advisory): LFI Activation: Y/N | .
23 |  | JE25010238 | 508 OMOKOROA ROAD,OMOKOROA,TAURANGA | Eastern | BARRETT RD | 2025-03-29 | 23:46 | 2025-03-30 | 7:17 | 0.24095 | 0.0031038 | 1125 | 87332 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: Recloser 9764 & Sec 9695 Protection flags (nil where none): A Phase O/C CAUSE: Sw/Gear 14317 Blown Up Location: Sw/Gear 14317 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: operational Weather (wind/rain): Fine LFI (Y/N + Comments): Yes and working Well Follow up Required (select advisory)? No Additional fault restoration comments: Line was isolated at Links 9695/6 & Sw/Gear 14044/1 to replace Sw/Gear 14317. | .
24 |  | JE25006192 | LONGBUSH | Western | LONGBUSH | 2025-03-28 | 9:00 | 2025-03-28 | 14:12 | 0.021534 | 6.8974e-05 | 25 | 7805 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles , hardware and conductors past ABS 67 | .
25 |  | JE25006320 | COLLEGE | Western | COLLEGE | 2025-03-28 | 9:15 | 2025-03-28 | 14:32 | 0.029703 | 9.3805e-05 | 34 | 10766 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install line break at pole 705522, replace xarms at pole 705516 & remove line break | .
26 |  | JE25007325 | MAHOE | Western | MAHOE | 2025-03-28 | 8:46 | 2025-03-28 | 16:01 | 0.052235 | 0.00012139 | 44 | 18933 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace ABS 5975 with new Entec sectionaliser 12758/2, links/4 (Open point). Remove ABS 5996, install new recloser 12768/2, Bypass ABS /1, Links/4,/6. | .
27 |  | JE25007468 | AWAITI | Eastern | AWAITI | 2025-03-28 | 9:04 | 2025-03-28 | 13:21 | 0.016992 | 6.6215e-05 | 24 | 6159 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace LV conductor between poles O366 & O377 | .
28 |  | JE25008065 | NGATEA | Eastern | NGATEA | 2025-03-28 | 10:16 | 2025-03-28 | 12:25 | 0.0078795 | 6.0697e-05 | 22 | 2856 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV G/M Transformer TP3676 - leaking oil from HV bushing. | .
29 |  | JE25009421 | KOHETE RD | Western | KOHETE RD | 2025-03-28 | 9:04 | 2025-03-28 | 12:27 | 0.012312 | 6.0697e-05 | 22 | 4463 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV crossarm at pole 760215 | .
30 |  | JE25010153 | 32 RANGE RD, MARTINBOROUGH | Western | TUTURUMURI | 2025-03-28 | 13:59 | 2025-03-28 | 14:24 | 0.00048797 | 1.9313e-05 | 7 | 177 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FM check sites Confirmed binders broken at 2 sites Poles 848313, 848316 Binders still holding conductor to insulators Also cross arm split at pole 811092 Cross arm not broken, but does need replacing On isolating 11kV, lines still tested live. 33kV lines above work areas FM to apply for urgent switching fuses closed 2R - left open | .
31 |  | JE25010196 | 106B POHANGINA RD, POHANGINA, PALMERSTON NORTH, 4470 | Western | POHANGINA | 2025-03-28 | 18:56 | 2025-03-29 | 17:00 | 0.0048089 | 2.4831e-05 | 5 | 1743 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Broken cross arm / Burning pole (Private Pole) Isolated at Fuses F17 Line break cut at Pole 483881, Customer on T4/21 left off, he will get a contractor in to replace his burnt pole tomorrow, Downer will supply some one to hold AP Assurance issued for customer to complete works. Isolated at Fuses F17 to close TLB and restore | .
32 |  | JE25010203 | unknown SOUTH ROAD,Opunake,Opunake | Western | SOUTH RD NGARIKI | 2025-03-28 | 23:02 | 2025-03-29 | 1:31 | 0.007304 | 7.4492e-05 | 27 | 2647 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: NG384 No. Fuses: 1 Fuse Amp Size: 20 TIME CLOSED: 00:38 Cause: unknown Weather (wind/rain): calm Follow up required (select advisory)?n Fuses Location: 12019 No. Fuses: 2 Fuse Amp Size: 8 TIME CLOSED: 01:30 Cause: unknown Weather (wind/rain): calm Follow up required (select advisory)?n faultman checked TFR 5628E fuses, when he opened the fuse box the fuses fell apart due to corrosion, fuses not blown Replaced 3 x 100A Fuses at TFR 5628E | .
33 |  | JE25005395 | LEEDSTOWN 22KV | Western | LEEDSTOWN 22KV | 2025-03-27 | 9:31 | 2025-03-27 | 12:46 | 0.035459 | 0.00018209 | 66 | 12852 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Relocate ABS 4066 from pole 805581 to 805582 then liven new W50 11kv-22kv tx New transformer W50 was never tested with load on it as there is problem with the earthing of the TFR. Scott Bullock & Mike Carson are investigating a solution and then with put in applications to sort earthing and store the transformer. | .
34 |  | JE25006426 | PIONEER | Western | PIONEER | 2025-03-27 | 8:30 | 2025-03-27 | 13:49 | 0.006145 | 1.9313e-05 | 7 | 2227 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV poles & crossarms between poles P42424 and P42443 | .
35 |  | JE25006765 | BRUNSWICK | Western | BRUNSWICK | 2025-03-27 | 8:50 | 2025-03-27 | 12:19 | 0.00057557 | 2.759e-06 | 1 | 209 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 6.6kV transformer Y309 | .
36 |  | JE25007323 | COROGLEN | Eastern | COROGLEN | 2025-03-27 | 9:31 | 2025-03-27 | 13:46 | 0.0070294 | 2.759e-05 | 10 | 2548 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Recon 498304-W2012. Replace xarms various sites past FC4133 | .
37 |  | JE25007345 | LINDERMANN RD | Eastern | LINDERMANN RD | 2025-03-27 | 9:21 | 2025-03-27 | 15:00 | 0.061832 | 0.00018209 | 66 | 22411 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove 11kv O/H from poles 204620 to new TX site TB1-015. Remove 11kv & l.v poles & connect UG | .
38 |  | JE25007350 | MATAKANA RD | Eastern | MATAKANA RD | 2025-03-27 | 9:00 | 2025-03-27 | 9:31 | 0.0033051 | 0.0001076 | 39 | 1198 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Reconductor HV from 427403 (ex 202016) to 202049. Remove Temp HV XArm and Temporary P/M Links TEMP64 | .
39 |  | JE25009982 | 26A PUTORINO ROAD,HUNTERVILLE,MARTON | Western | ARAHINA 33KV | 2025-03-27 | 9:30 | 2025-03-27 | 9:41 | 0.023592 | 0.0023203 | 841 | 8551 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | CB 3035 tripped on B & C phase O/C when ABS 2529 was opened at the Substation under NAPA 118933, Switching was stopped while Rata Sub was restored with CB 1350 opened by Controller and CB 3035 was closed and then CB 1350 closed to restore supply. ABS 2529 was isolated under JE25010006 and found to have broken insulator and has been DNO'd (DNO TAG 2503020) | .
40 |  | JE25009991 | 1835 27 ,PATETONGA,MORRINSVILLE | Eastern | PATETONGA | 2025-03-27 | 9:37 | 2025-03-27 | 11:58 | 0.00077868 | 5.5179e-06 | 2 | 282 | Unplanned | WILDLIFE - BIRD | Fuses Location: FC4221 No. Fuses: 2 Fuse Amp Size: 15A TIME CLOSED: 1158 Cause: bird strike Weather (wind/rain): Fine Follow up required (select advisory)? Restored | .
41 |  | JE25009993 | KAI IWI SUB - MAXWELL - KAI IWI/5 | Western | MAXWELL | 2025-03-27 | 9:43 | 2025-03-27 | 10:09 | 0.017849 | 0.0006787 | 246 | 6470 | Unplanned | HUMAN ERROR - POTENTIAL SWITCHING ERROR | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 5 Protection flags (nil where none): A, B Ph Fault CAUSE: Live Line work Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Live line work being done on Feeder, Unable to contact team FM sent to check on team LLP 120509-01 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
42 |  | JE25010023 | 353 TE AWAITI ROAD, TE AWAITI, MARTINBOROUGH, 5782 | Western | TUTURUMURI | 2025-03-27 | 15:30 | 2025-03-27 | 18:04 | 0.013099 | 8.5528e-05 | 31 | 4748 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolated at Fuses 8064 Control of network handed over to FM due to comms issues in area Burnt cross arm replaced at Pole 816758 Network control returned to NOC Fuses 8064 closed | .
43 |  | JE25010053 | 266A MANAWARU ROAD,MANAWARU,TE AROHA | Eastern | MAUNGAKAWA ROAD | 2025-03-27 | 16:56 | 2025-03-27 | 19:10 | 0.0007406 | 5.5179e-06 | 2 | 268 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: FP 173 TIME CLOSED: 19:10 Cause: Fire on top of Transformer - Isolated for work on the LV - Fire Cause from Deterioration of LV Fuse Holder - Caught Birds nest on fire. Weather (wind/rain): Fine Replaced Lv Fuses Main Leads and Reterminated Cable | .
44 |  | JE25010065 | 260 HOT SPRINGS ROAD,TAHAWAI,KATIKATI | Eastern | KATIKATI | 2025-03-27 | 22:20 | 2025-03-27 | 23:41 | 0.0011063 | 1.3795e-05 | 5 | 401 | Unplanned | VEGETATION - OUTSIDE ZONE | F4179830 50 Min ETA TREE HAS COME DOWN ON LINES LINES ARCING & SPARKING No access issues or dogs Advised cust to keep clear and treat as live at all times. Line Isolate to Clear away trees - No Lines Down False Report 2 x Fuses Replaced fuses opended 22:20 closed 23:40 | .
45 |  | JE25010066 | 220 SOMERSET ROAD,PARKVALE,CARTERTON | Western | SOMERSET RD | 2025-03-27 | 21:06 | 2025-03-27 | 22:16 | 0.00019295 | 2.759e-06 | 1 | 70 | Unplanned | WILDLIFE - OTHER | Fuses Location: FP7619 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 22:16 Cause: Lines clashing from bulls rubbing agaisnt pole and guy wire Weather (wind/rain): Fine Follow up required (select advisory)? NIL | .
46 |  | JE25006159 | NO 3 LINE | Western | NO 3 LINE | 2025-03-26 | 9:01 | 2025-03-26 | 15:06 | 0.090578 | 0.00024831 | 90 | 32831 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace multiple defects between poles 792139 & 792041 | .
47 |  | JE25006167 | TUTURUMURI | Western | TUTURUMURI | 2025-03-26 | 10:01 | 2025-03-26 | 13:44 | 0.0024592 | 1.1036e-05 | 4 | 891 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re sag and repair 11kV and LV lines between poles 810505 and 810506 (T1151) | .
48 |  | JE25007107 | AWAITI | Eastern | AWAITI | 2025-03-26 | 9:00 | 2025-03-26 | 15:00 | 0.0049668 | 1.3795e-05 | 5 | 1800 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Poles O421, O423, O12418 (TC402), O426, O427, O428. Replace cross arms O425, O429, O12417. Tripping On Recloser RC22 in Morning as Faultman did not put Regulators into Manual Neutral tap Correctly Tripping on Recloser RC 22 in Afternoon as Faultman Did not see 1 Of the solid Links out at Regulators Safety Manger Required | .
49 |  | JE25007147 | BARRETT RD | Eastern | BARRETT RD | 2025-03-26 | 8:50 | 2025-03-26 | 14:26 | 0.0027783 | 8.2769e-06 | 3 | 1007 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | cut trees between poles 209692 & 209693 | .
50 |  | JE25007292 | COROGLEN | Eastern | COROGLEN | 2025-03-26 | 9:15 | 2025-03-26 | 15:06 | 0.068639 | 0.00019589 | 71 | 24878 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove pole W1771 by installing twp 12.5 M poles changing span at poles W1770 W12830. Shift Reclose 9512 one span to new pole recommission. | .
51 |  | JE25009831 | unknown WANI ROAD,Netherton,Rural | Eastern | AWAITI | 2025-03-26 | 7:09 | 2025-03-26 | 7:14 | 0.00244 | 0.00048834 | 177 | 884 | Unplanned | HUMAN ERROR - POTENTIAL SWITCHING ERROR | Switching error Tripping On Recloser RC22 in Morning as Faultman did not put Regulators into Manual Neutral tap Correctly | .
52 |  | JE25009833 | 1493 KAIHERE ROAD,KAIHERE,NGATEA | Eastern | AWAITI | 2025-03-26 | 7:14 | 2025-03-26 | 7:16 | 0.00098227 | 0.00048834 | 177 | 356 | Unplanned | HUMAN ERROR - POTENTIAL SWITCHING ERROR | Switching error Tripping On Recloser RC22 in Morning as Faultman did not put Regulators into Manual Neutral tap Correctly | .
53 |  | JE25009880 | 457 RANGE ROAD,PONGAROA,PONGAROA | Western | HOROEKA | 2025-03-26 | 12:23 | 2025-03-26 | 13:24 | 0.001015 | 1.6554e-05 | 6 | 368 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Broken deadend found at Pole P06230 Isolated at Fuses V18 Deadend replaced, full power restored | .
54 |  | JE25009894 | TP MARTON - TUTAENUI - REC 554 | Western | TUTAENUI | 2025-03-26 | 13:23 | 2025-03-26 | 15:07 | 0.011317 | 0.00011036 | 40 | 4102 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: Recloser 554 Protection flags (nil where none): EF, Phase A -OC CAUSE: Old Telecom wire on 11kV lines Location: Pole 804455 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Patrolled sectionalized. Found an old telecoms wire on the 11kV line, Removed with Hot Stick SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): N/A Circuit that tripped: N/A DTF (KM):N/A | .
55 |  | JE25009918 | 16 RACECOURSE WAY,GATE PA,TAURANGA | Eastern | CAMBRIDGE RD TAURANGA | 2025-03-26 | 19:46 | 2025-03-26 | 21:20 | 0.00091161 | 1.1036e-05 | 4 | 330 | Unplanned | WILDLIFE - BIRD | Replaced 3 x 11kV Fuses in Sw/Gear 9612/2 3 x 16A Fuses Feathers Found - Cause Birds Weather Fine Larger outage area required due to Sw/Gear9612 being oil switch. | .
56 |  | JE25009919 | 1493 KAIHERE ROAD,KAIHERE,NGATEA | Eastern | AWAITI | 2025-03-26 | 15:34 | 2025-03-26 | 15:38 | 0.0018801 | 0.00048834 | 177 | 681 | Unplanned | HUMAN ERROR - POTENTIAL SWITCHING ERROR | Tripping on Recloser RC 22 in Afternoon as Faultman Did not see 1 Of the solid Links out at Regulators | .
57 |  | JE25009933 | 1152 29 ,LOWER KAIMAI,TAURANGA | Eastern | KAIMAI DRIVE | 2025-03-26 | 20:06 | 2025-03-27 | 2:30 | 0.22372 | 0.0028693 | 635 | 81087 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 11 - 11kV REC 9275/2 Protection flags (nil where none): A B OC CAUSE: Lines Twisted Together Mid Span - Bird Strike on river crossing Location: Between Poles - 211588 & 879092 PERFORMANCE DETAIL DNO (number or state No): NIL Circuit patrolled and type: Cursory Weather (wind/rain): Fine LFI (Y/N + Comments): NIL Follow up Required (select advisory)? Protection Additional fault restoration comments: Couple of things to note here Firstly CB11 cleared the fault and tripped open before Recloser 9275 completed its reclose cycle With this auto reclose was showing disabled on CB 11, Transpower unsure on whether this was meant to be disabled or not and when it was disbaled, it has been left as enabled for the present time, protection team to investigate if we need cb11 auto reclose enabled or disabled. Secondly pyes pa 8 was back feeding majority of CB 11, Pyes pa had a seperate fault not caused by the backfeed into TGA CB 11, This Fault is under JE25009942, Cracked Insulator at ABS SE3-050, This caused the restored section of feeder to loose power. some section where able to be re energized. Thirdly Sw/Gear 15014 voltage reading is between 7 - 8kV depending on back feed direction, at the time of the fault i couldn't be certain if we had lost a phase or n | .
58 |  | JE25009942 | 58 MATAKOKIRI DRIVE,TAURIKO,TAURANGA | Eastern | KEENAN RD | 2025-03-26 | 21:59 | 2025-03-27 | 3:36 | 0.24172 | 0.0029135 | 769 | 87614 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 8 Protection flags (nil where none): C PH Ground - E/F CAUSE: Broken Insulator / Jumper Location: ABS SE3-050 PERFORMANCE DETAIL DNO (number or state No): 2503019 Circuit patrolled and type: Cursory Weather (wind/rain): Fine LFI (Y/N + Comments): NIL Follow up Required (select advisory)? NIL Additional fault restoration comments: Cracked insulator on the ABS SE3 - 050 - Blew Jumper Termination aswell, Temporary fix in place, 3m arm and outside phase, Insulator used on arm, Switch is non operational. Pyes Pa CB 8 was back feeding TGA CB 11 and drop additional ICP Off, this job was JE25009933 Replacement of SE3-050 to be actioned under DNO | .
59 |  | JE25002426 | RONGOMAI | Western | RONGOMAI | 2025-03-25 | 9:51 | 2025-03-25 | 10:23 | 0.00070004 | 2.2072e-05 | 8 | 254 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace pole P03127 Pole not replaced, equipment issues, new application required | .
60 |  | JE25006134 | LONGBUSH | Western | LONGBUSH | 2025-03-25 | 9:00 | 2025-03-25 | 15:08 | 0.02533 | 6.8974e-05 | 25 | 9181 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles , hardware and conductors past ABS 67 | .
61 |  | JE25006155 | OTAKEHO | Western | OTAKEHO | 2025-03-25 | 9:16 | 2025-03-25 | 14:07 | 0.01767 | 6.0697e-05 | 22 | 6405 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace poles 717547, 717596 & 717599. re-arm pole 717595 | .
62 |  | JE25006615 | SEAWARD COAST | Western | SEAWARD COAST | 2025-03-25 | 8:31 | 2025-03-25 | 13:45 | 0.047539 | 0.00015174 | 55 | 17231 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Defect 50345072 - Replacement of crossarms and structures between poles 757142 & 757098. (No transformer pole replacements) | .
63 |  | JE25006956 | APATA | Eastern | APATA | 2025-03-25 | 9:31 | 2025-03-25 | 14:01 | 0.023848 | 8.8287e-05 | 32 | 8644 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replacing Poles 205286,205287,205288 Replacing arms and hardware on poles 205280,205285 | .
64 |  | JE25006959 | LINDERMANN RD | Eastern | LINDERMANN RD | 2025-03-25 | 8:56 | 2025-03-25 | 14:32 | 0.026859 | 8.001e-05 | 29 | 9735 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv/400vt cross arms @ 204542, 204543, 204545,204548,204549, &204550. Isolation point @ SB1-047. | .
65 |  | JE25006962 | MATAKANA RD | Eastern | MATAKANA RD | 2025-03-25 | 9:01 | 2025-03-25 | 13:45 | 0.030614 | 0.0001076 | 39 | 11096 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Reconductor HV from 427403 (ex 202016) to 202061 | .
66 |  | JE25007533 | PURANGI | Eastern | PURANGI | 2025-03-25 | 8:31 | 2025-03-25 | 16:01 | 0.12742 | 0.00028417 | 103 | 46185 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install new Switchgear 15055. Install new transformer TC4965. Replace Pole W13599 and W13608. Relocate existing LV circuit into new RDL. Terminate new cable from Replacement Pole at W13608 to 15055/3. Terminate new cable from TC4965 to 15055/2. Terminate new cable from replacement Pole at W13599 to 15055/1. Streetlight circuits to be terminated into new streetlight pillar. When ABS 2109 was closed, Recloser 9278/2 tripped on E/F, after Sectionalizer 13690/2 was opened Recloser 9278/2 was closed, ABS 2109 is not an easy ABS to close hence the tripping. | .
67 |  | JE25008510 | KAIMATA | Western | KAIMATA | 2025-03-25 | 10:00 | 2025-03-25 | 12:51 | 0.0070457 | 4.1384e-05 | 15 | 2554 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 33kV and 11kV crossarms at pole 760567 | .
68 |  | JE25009701 | 220 SOMERSET ROAD,PARKVALE,CARTERTON | Western | SOMERSET RD | 2025-03-25 | 5:52 | 2025-03-25 | 7:03 | 0.0001957 | 2.759e-06 | 1 | 71 | Unplanned | WILDLIFE - OTHER | Fuses Location: Fuses 7619 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 0703 Cause: live stock rubbing on the pole making it swing Weather (wind/rain): drizzle Follow up required (select advisory)? Restored | .
69 |  | JE25009751 | 7 OMAHURU ROAD,OKAIAWA,HAWERA | Western | MATAPU | 2025-03-25 | 12:03 | 2025-03-25 | 15:34 | 0.00058251 | 2.759e-06 | 1 | 211 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: Transformer K4272 No. Fuses: 2 Fuse Amp Size: TIME CLOSED: Cause: Weather (wind/rain): Follow up required (select advisory)? Fuses changed at Transformer K4272 not K4271 Reload reliven failed, to replace Transformer Transformer replaced 25/03/25 Power off 13:52 Power on 15:23 | .
70 |  | JE25009759 | KAIRANGA SUB - TREMAINE AVE - KAIRANGA/24 | Western | TREMAINE AVE | 2025-03-25 | 11:35 | 2025-03-25 | 15:25 | 0.2474 | 0.0030624 | 1110 | 89673 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: CB 24 Protection flags (nil where none): E/F, IDMT CAUSE: cable termination fault Location: P42293 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): 2503018 Circuit patrolled and type: op Weather (wind/rain): calm LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: line patrolled, faulty cable termination on yellow phase found at pole P42293, Isolated at ABS A16, A18 & Links 10950/4, cable disconnected from Poles P42293 & P42217, full power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
71 |  | JE25009769 | CLAREVILLE SUB - PARK RD - C422/2 | Western | PARK RD | 2025-03-25 | 12:20 | 2025-03-25 | 13:15 | 0.031998 | 0.0005987 | 217 | 11598 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec C422/2 Protection flags (nil where none): E/F CAUSE: unknown Location: na Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: op Weather (wind/rain): calm LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Rec C422/2 had a HLT on due to CAC 120392-01, Tree contractor told to stand down, line patrolled, no fault found, feeder restored, HLT reapplied, contractor commenced work Possible bird strike as a lot of magpies around this feeder SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
72 |  | JE25009816 | 351 CANAL EAST ROAD,WAITAKARURU,THAMES | Eastern | NGATEA | 2025-03-25 | 18:38 | 2025-03-25 | 20:02 | 0.022081 | 0.00026486 | 96 | 8003 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Faultman found burning jumper at Fuses FC768, line was isolated at ABS's 509 2572, LINS 14402/4 & 13151/4 to replace the burnt jumper and replace center phase insulator that was also damaged. | .
73 |  | JE25005937 | LONGBUSH | Western | LONGBUSH | 2025-03-24 | 9:00 | 2025-03-24 | 14:29 | 0.022686 | 6.8974e-05 | 25 | 8223 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles , hardware and conductors past ABS 67 | .
74 |  | JE25006093 | MANGAWEKA | Western | MANGAWEKA | 2025-03-24 | 9:53 | 2025-03-24 | 13:11 | 0.0010921 | 5.5179e-06 | 2 | 396 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re-conductor Low Voltage between poles 453526 & 812180 | .
75 |  | JE25006099 | MANGAWEKA | Western | MANGAWEKA | 2025-03-24 | 9:20 | 2025-03-24 | 11:16 | 0.00096053 | 8.2769e-06 | 3 | 348 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re-conductor Low Voltage between poles 812210 & 810411 | .
76 |  | JE25006568 | PIONEER | Western | PIONEER | 2025-03-24 | 8:46 | 2025-03-24 | 15:24 | 0.013849 | 3.5867e-05 | 13 | 5020 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace crossarms and poles between poles P42437 and P42448, Longburn & Rongatea Rd Child job will not restore, not sure why. Cannot complete the job | .
77 |  | JE25006599 | SEAWARD COAST | Western | SEAWARD COAST | 2025-03-24 | 9:30 | 2025-03-24 | 14:10 | 0.023938 | 8.5528e-05 | 31 | 8676 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Defect 50345072 - Crossarm and pole change at 757036 & 757021 | .
78 |  | JE25007109 | AWAITI | Eastern | AWAITI | 2025-03-24 | 9:00 | 2025-03-24 | 15:05 | 0.018123 | 4.9661e-05 | 18 | 6569 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace cross arms O404, 383791, and O12428 .Replace poles 877443, O406, O411, O12416. Straighten poles 858328, O408,Â O415, O416, O417, 858342, and O419 | .
79 |  | JE25007163 | MATAKANA RD | Eastern | MATAKANA RD | 2025-03-24 | 11:33 | 2025-03-24 | 12:01 | 0.0019037 | 6.6215e-05 | 24 | 690 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install LFI at poles 496640 , 381859 & 202008 | .
80 |  | JE25009552 | KEREPIHI SUB - HAURAKI RD - 9161/2 | Eastern | HAURAKI RD | 2025-03-24 | 6:56 | 2025-03-24 | 11:34 | 0.11415 | 0.0010815 | 392 | 41375 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV Recloser 9161 Protection flags (nil where none): EF CAUSE: Lines Down at Pole 856094 Location: Pole 856094 Temp generation (state details when used): NIL PERFORMANCE DETAIL DNO (number or state No): NIL Circuit patrolled and type: NIL - Report of lines down by firecomms Weather (wind/rain): Fine LFI (Y/N + Comments): Yes Sap13587087 & sap 13587082 Follow up Required (select advisory)? Additional fault restoration comments: Overhead line crossing between Links LC504 and Pole 248643 1 phase down, line got flown into by a duck, Repaired all three conductors, 40mm squirrel conductor and sleeves used. F4176717 - FENZ advised 10 minutes ETA | .
81 |  | JE25009555 | 1493 KAIHERE ROAD,KAIHERE,NGATEA | Eastern | AWAITI | 2025-03-24 | 7:12 | 2025-03-24 | 7:19 | 0.0033541 | 0.00048834 | 177 | 1216 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Recloser RC22 Tripped on Reverse E/F when opening ABS TEMP053 | .
82 |  | JE25009556 | 1433 KAIHERE ROAD,KAIHERE,NGATEA | Eastern | AWAITI | 2025-03-24 | 7:14 | 2025-03-24 | 7:19 | 0.00013596 | 3.3108e-05 | 12 | 49 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Recloser RC22 Tripped on Reverse E/F when opening ABS TEMP053 | .
83 |  | JE25009588 | unknown GOULD ROAD,Te Aroha,Te Aroha | Eastern | MOUNTAIN | 2025-03-24 | 10:04 | 2025-03-24 | 14:50 | 0.014977 | 5.242e-05 | 19 | 5429 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | All Hv Lead Blown - Fuses Replaced and Transformer unknown cause of damage | .
84 |  | JE25009602 | unknown ONGO ROAD,Hunterville,Rural | Western | LEEDSTOWN 22KV | 2025-03-24 | 11:08 | 2025-03-24 | 12:33 | 0.0013945 | 1.6554e-05 | 6 | 505 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: Fuses 250 No. Fuses: 2 Fuse Amp Size: 3a TIME CLOSED: 1232 Cause: wind and rain Weather (wind/rain): windy and rainy Follow up required (select advisory)? Restored | .
85 |  | JE25009623 | TP WAVERLEY - WAITOTARA - 1406 | Western | WAITOTARA | 2025-03-24 | 12:43 | 2025-03-24 | 19:21 | 0.075812 | 0.00019037 | 69 | 27479 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: REC 1406 Protection flags (nil where none): A Phase EF CAUSE: Digger hit the lines Location: Pole 780364 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): rain LFI (Y/N + Comments): n/a Follow up Required (select advisory)? Additional fault restoration comments: | .
86 |  | JE25009666 | 219 TE ORE ORE ROAD,TE ORE ORE,MASTERTON | Western | WERAITI | 2025-03-24 | 16:14 | 2025-03-24 | 20:35 | 0.10169 | 0.00096012 | 348 | 36858 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV Pole 827653 Protection flags (nil where none): B,C Phase O/C CAUSE: Location: Bird hooked up in line against pole top caused fire Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Fault rung in Weather (wind/rain): Fine LFI (Y/N + Comments): nil Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
87 |  | JE25009683 | 129 RUAHIHI ROAD,LOWER KAIMAI,TAURANGA | Eastern | KAIMAI DRIVE | 2025-03-24 | 23:05 | 2025-03-25 | 13:24 | 0.0023699 | 2.759e-06 | 1 | 859 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Cable Fault - Confirmed Under Test Permit Customer has his own Gen running since 18:30 24/03/25 Powerco Generation Installed at 12:57 25/03/25 DNO 2503017 Created for repairs Job is Logged agaisnt Wrong Transformer Attempted to create a job in oms but would not work. | .
88 |  | JE25009691 | 1349 CAMERON ROAD,GATE PA,TAURANGA | Eastern | KAIMAI DRIVE | 2025-03-24 | 20:04 | 2025-03-24 | 21:55 | 0.11815 | 0.0017492 | 634 | 42825 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: CB 11 & Recloser 9275 Protection flags (nil where none): O/C A,B,C CAUSE: Suspect Bird Strike Caused Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: curse Weather (wind/rain): Fine LFI (Y/N + Comments): Nil Operated Follow up Required (select advisory)? Additional fault restoration comments: Recloser 9275 seen the fault & Auto reclosed, But CB 11 Opened, Discrimination issue between the CB's SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
89 |  | JE25009510 | unknown TRAMLINE ROAD,Patetonga,Rural | Eastern | PATETONGA | 2025-03-23 | 5:36 | 2025-03-23 | 7:58 | 0.00078429 | 5.5179e-06 | 2 | 284 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses FP189 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 07:58 Cause: Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? No | .
90 |  | JE25009523 | 459 MID PUNIHO ROAD,OKATO,NEW PLYMOUTH | Western | PARIHAKA | 2025-03-23 | 13:02 | 2025-03-23 | 14:17 | 0.0065862 | 8.8287e-05 | 32 | 2387 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: Deterioration of HV fuses Location: TX P4425, Pole 704058 Isolation: PU413 Backfeeds: N/A Materials Used: Replaced 3x HV fuses & 3x 6A HV fuse links Weather: Calm Additional Info: | .
91 |  | JE25009538 | 372 BEACONSFIELD ROAD, STRATFORD, STRATFORD, 4394 | Western | CLOTON RD SOUTH | 2025-03-23 | 19:48 | 2025-03-24 | 0:30 | 0.031811 | 0.00011312 | 41 | 11530 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Car vs Pole Replace Pole 740592 NDR to follow | .
92 |  | JE25009437 | 110 TORA FARM SETTLEMENT ROAD, MARTINBOROUGH, 5782 | Western | TUTURUMURI | 2025-03-22 | 8:31 | 2025-03-22 | 9:21 | 0.0037544 | 7.4492e-05 | 27 | 1361 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cross arm at Pole 362805 is tracking and there is some burning on the cross arm. The cross arm will need to be replaced but can wait until the morning. Cross arm replaced at Pole 362805 | .
93 |  | JE25009473 | 625 OTARAOA ROAD,TIKORANGI,WAITARA | Western | OTARAOA RD | 2025-03-22 | 12:40 | 2025-03-22 | 13:22 | 0.00023313 | 5.5179e-06 | 2 | 85 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Repair HV jumper at Tfr 3112T | .
94 |  | JE25003828 | NGATI MARU | Eastern | NGATI MARU | 2025-03-21 | 11:07 | 2025-03-23 | 14:27 | 0.016971 | 1.1036e-05 | 2 | 6151 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace old Reyrolle Switchgear with new Metering unit & ABB CFCF Switchgear. Temporary generation will connected to the distribution board for offices . | .
95 |  | JE25005863 | MANGAWEKA | Western | MANGAWEKA | 2025-03-21 | 9:01 | 2025-03-21 | 15:50 | 0.022592 | 5.5179e-05 | 20 | 8189 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re-conductor 11KV between poles 812176 & 812118 | .
96 |  | JE25005900 | LONGBUSH | Western | LONGBUSH | 2025-03-21 | 9:01 | 2025-03-21 | 15:10 | 0.025472 | 6.8974e-05 | 25 | 9233 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV poles, hardware and conductor past ABS S67 | .
97 |  | JE25006662 | PAHOIA | Eastern | PAHOIA | 2025-03-21 | 9:16 | 2025-03-21 | 11:21 | 0.0024138 | 1.9313e-05 | 7 | 875 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Cut trees between 11kV poles 209505 & 209507. | .
98 |  | JE25006760 | MATAKANA RD | Eastern | MATAKANA RD | 2025-03-21 | 9:00 | 2025-03-21 | 14:16 | 0.033933 | 0.0001076 | 39 | 12299 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Reconductor HV & LV from 427403 (ex 202016) to 202044 (TC3-077) | .
99 |  | JE25007136 | FEILDING-SANSON 33KV | Western | FEILDING-SANSON 33KV | 2025-03-21 | 23:01 | 2025-03-21 | 23:02 | 0.0086558 | 0.0060118 | 2179 | 3137 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Stage 3- Connect TP Feilding 2 33kV circuit to new CB3122, liven and commission new 33kV switchboard. Liven emergency tie cable from CB3232 â€¢ Cut into 630mm cables coming from pole P32354 and joint new cables from CB3122 â€¢ Remove 240mm CU cables from pole P32354 and abandon â€¢ Carry out line diff testing between CB3122 & CB2222 â€¢ Liven and commission new 33kV switchboard from Transpower via CB3122 â€¢ Soak test 33 cables and switchboard for 24hrs minimum | .
100 |  | JE25007280 | HORRELLS RD | Eastern | HORRELLS RD | 2025-03-21 | 8:55 | 2025-03-21 | 14:31 | 0.058329 | 0.00017381 | 63 | 21142 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | PQI - To replace transformer structure TC3918 with a double pole 100kVA transformer | .
101 |  | JE25008957 | HULL RD | Eastern | HULL RD | 2025-03-21 | 17:31 | 2025-03-21 | 18:41 | 0.0084976 | 0.00012139 | 44 | 3080 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv x-arm at pole 213796 | .
102 |  | JE25009277 | 700 OMATA ROAD, WAVERLEY, 4592 | Western | WAITOTARA | 2025-03-21 | 14:35 | 2025-03-21 | 19:23 | 0.001587 | 5.5179e-06 | 2 | 575 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Straighten Pole 359384 Isolated at Fuses 696 Pole Straighten and lines re-hung | .
103 |  | JE25009334 | unknown unknown,Patetonga,Rural | Eastern | PATETONGA | 2025-03-21 | 5:02 | 2025-03-21 | 6:09 | 0.00036501 | 5.5179e-06 | 2 | 132 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: FP189 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 06:08 Cause: Unknown Weather (wind/rain): Fine Follow up required (select advisory)? | .
104 |  | JE25009340 | 390 MANAWAPOU ROAD,HAWERA,HAWERA | Western | MANAWAPOU RD | 2025-03-21 | 8:22 | 2025-03-21 | 9:53 | 0.00049781 | 5.5179e-06 | 2 | 180 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faultman found lines down at pole 440969, caused by deuteriation, line was isolated at Fuses WH819 to repair the lines. | .
105 |  | JE25009341 | 211 SHARP ROAD,AONGATETE,KATIKATI | Eastern | WILLS RD | 2025-03-21 | 7:59 | 2025-03-21 | 10:06 | 0.0042082 | 3.3108e-05 | 12 | 1525 | Unplanned | WILDLIFE - BIRD | Fuses Location: SB2-069 No. Fuses: 2 Fuse Amp Size: 15a TIME CLOSED: 1006 Cause: bird Weather (wind/rain): beautiful Follow up required (select advisory)? ***Check JE25009342 on closure ***** | .
106 |  | JE25009456 | unknown NGARIKI ROAD,Rahotu,Rural | Western | NGARIKI RD | 2025-03-21 | 19:51 | 2025-03-21 | 22:21 | 0.0099588 | 6.6215e-05 | 24 | 3610 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Confirmed pole 711730 Damaged Isolated at ABS's NG455, NG326, NG425, & NG434 Pole Replaced | .
107 |  | JE25002250 | RAETIHI | Western | RAETIHI | 2025-03-20 | 9:15 | 2025-03-20 | 15:11 | 0.08543 | 0.00029245 | 106 | 30964 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 844290 & move X1978 from 844287 to new pole, dismantle 11kV line between 844290 & 844287 for safety | .
108 |  | JE25002672 | LONGBUSH | Western | LONGBUSH | 2025-03-20 | 9:00 | 2025-03-20 | 15:11 | 0.05011 | 0.00013519 | 49 | 18163 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV poles, hardware and conductors past ABS S333 | .
109 |  | JE25005435 | RAETIHI | Western | RAETIHI | 2025-03-20 | 8:45 | 2025-03-20 | 15:13 | 0.08675 | 0.00022348 | 81 | 31443 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Wire run for 3 phase upgrade from pole 777798,777809,777910,777811,777812,777815,777816,777817,777818,new pole 1,777819,777822,777828,777830. Remove. Existing TX X2977 & pole 777818 | .
110 |  | JE25005531 | TUTAENUI | Western | TUTAENUI | 2025-03-20 | 9:00 | 2025-03-20 | 14:03 | 0.00083518 | 2.759e-06 | 1 | 303 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 2 X Defected Poles 794326 & 794327 | .
111 |  | JE25005694 | KATERE 5 | Western | KATERE 5 | 2025-03-20 | 8:30 | 2025-03-20 | 15:50 | 0.030357 | 6.8974e-05 | 25 | 11003 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Intersection Henwood Rd and Manutahi Rd, systematic undergrounding of HV lines. This NAPA is for the outage requirements and work for Shut 2. Replace pole 748222. Remove O/H lines and ABS 456. Install 1 x new 11kV cables, from new AUTO switchgear 12777/1 as per plan. Day 1 outage to be completed first on NAPA 118780. | .
112 |  | JE25005727 | MIDDLEBROOK | Eastern | MIDDLEBROOK | 2025-03-20 | 9:31 | 2025-03-20 | 10:25 | 0.011421 | 0.00020968 | 76 | 4139 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install Eneida - TB2-075 | .
113 |  | JE25005756 | CLOTON RD NORTH | Western | CLOTON RD NORTH | 2025-03-20 | 8:37 | 2025-03-20 | 12:52 | 0.050602 | 0.00019865 | 72 | 18341 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 734529, HV arms 734521, 734533, 734513, ,LV term arm 734509, LV tx fuses 734516 | .
114 |  | JE25006120 | WHIRITOA | Eastern | WHIRITOA | 2025-03-20 | 9:53 | 2025-03-20 | 10:53 | 0.023678 | 0.00039453 | 143 | 8582 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install Eneida - TC2987 | .
115 |  | JE25006591 | LINDERMANN RD | Eastern | LINDERMANN RD | 2025-03-20 | 8:51 | 2025-03-20 | 15:30 | 0.0044097 | 1.1036e-05 | 4 | 1598 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv/400vt cross arms @ 204590,204591,204595 & 204592. Replace pole 204594. Isolation point @ SB1-065 | .
116 |  | JE25006609 | KAIHERE | Eastern | KAIHERE | 2025-03-20 | 9:17 | 2025-03-20 | 14:25 | 0.015325 | 4.9661e-05 | 18 | 5555 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace arms O388, O390, O392, and O393. Replace poles O394 (TC6116), O12431, O402, O403. Straighten poles O401, O400, O399, and O397. Run a new span of LV conductor to pole 486683 | .
117 |  | JE25006650 | COROGLEN | Eastern | COROGLEN | 2025-03-20 | 9:31 | 2025-03-20 | 16:37 | 0.051726 | 0.00012139 | 44 | 18748 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Pole change xarms and resag various sites The 309 Road past 13199 | .
118 |  | JE25009167 | 2127 TAIRUA WHITIANGA ROAD,COROGLEN,WHITIANGA | Eastern | COROGLEN | 2025-03-20 | 6:17 | 2025-03-20 | 9:00 | 0.0027019 | 1.6554e-05 | 6 | 979 | Unplanned | UNKNOWN - DATA QUALITY | Fuses Location: TC1121 No. Fuses: 3 Fuse Amp Size:2A TIME CLOSED: 0900 Cause: unknown Weather (wind/rain): fine Follow up required (select advisory)? 2R for barrel and 3xfuse wrong ICP for the tx TP3864 is might to be TC1121 have sent email to ai team and connections | .
119 |  | JE25009170 | 23 KAITAWA ROAD,PAHIATUA,PAHIATUA | Western | COONOOR | 2025-03-20 | 7:08 | 2025-03-20 | 10:21 | 0.08637 | 0.00061249 | 222 | 31305 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV Reclosure T21 Protection flags (nil where none): C Ph O/C, E/F CAUSE: Bird Strike brought line down Location: Pole 444554 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Isolated at ABS T28 & Q77/1, T42/1, Links T42/4, & Links Q77/4 Lines repaired SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
120 |  | JE25009175 | 132 BRIDGE STREET,TOKOROA,TOKOROA | Eastern | DALMENY ST | 2025-03-20 | 7:42 | 2025-03-20 | 9:19 | 0.11592 | 0.0019064 | 691 | 42015 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 4 Protection flags (nil where none): E/F CAUSE: Cable fault Location: Sw/Gears 9652/1 & IC1472 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): 2503015 Circuit patrolled and type: operational Weather (wind/rain): calm LFI (Y/N + Comments): Y - Sw/Gear 9896/3 Follow up Required (select advisory)? Yes Additional fault restoration comments: 2R to left open for crew to locate cable fault. After tripping NOC Controller found that the tripping indication was incorrect as on Scada indicated CB 4 had tripped but the customers that were off were on CB 8. After fault was located and supply was restored testing with Faultman of CB 4 & CB 8 was carried out to prove if the 2 feeders had been transposed and it was found that the 2 feeders had been transposed. (done under JE25009261) Wayne Hosking will investigate as to how this transposing has accord. 28/03/25 - Recreated outage under JE25010110 and linked. | .
121 |  | JE25009240 | 11 IRWIN ROAD,PAEROA,PAEROA | Eastern | RAILWAY ST | 2025-03-20 | 12:14 | 2025-03-20 | 20:39 | 0.0013934 | 2.759e-06 | 1 | 505 | Unplanned | UNKNOWN - DATA QUALITY | Digger Hit Cable Isolated At Fuses FC1077 Carried out repairs Tested all Good Liven at 20:38 | .
122 |  | JE25009272 | unknown WHANGAEHU VALLEY ROAD,Rangiwaea,Rural | Western | IRIRANGI | 2025-03-20 | 9:47 | 2025-03-20 | 12:15 | 0.0024468 | 1.6554e-05 | 6 | 887 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: 006 No. Fuses: 2 Fuse Amp Size: 6a TIME CLOSED: 1215 Cause: unknown Weather (wind/rain): windy Follow up required (select advisory)? | .
123 |  | JE25009314 | 403 MAIN DRAIN ROAD,RANGIOTU,PALMERSTON NORTH | Western | TAIKOREA | 2025-03-20 | 21:51 | 2025-03-20 | 23:16 | 0.0014131 | 1.6554e-05 | 6 | 512 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | faulty jumpers from main line to top of DDO's to TFR T1/544 at Pole P27085 Isolated at Fuses B53 2 x jumpers replaced, 1 x jumper repaired Full power restored | .
124 |  | JE25005224 | LONGBUSH | Western | LONGBUSH | 2025-03-19 | 8:30 | 2025-03-19 | 14:50 | 0.026208 | 6.8974e-05 | 25 | 9499 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV poles, hardware and conductor past ABS S67 | .
125 |  | JE25005510 | MT STEWART | Western | MT STEWART | 2025-03-19 | 9:20 | 2025-03-19 | 11:18 | 0.0081269 | 0.00014347 | 47 | 2946 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Maintain 33kv ABS X77 | .
126 |  | JE25006158 | COROGLEN | Eastern | COROGLEN | 2025-03-19 | 9:00 | 2025-03-19 | 13:18 | 0.019905 | 7.7251e-05 | 28 | 7215 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT spur line defects Kaimarama road . Xarms and resags various sites past ABS315 | .
127 |  | JE25006472 | LINDERMANN RD | Eastern | LINDERMANN RD | 2025-03-19 | 8:46 | 2025-03-19 | 14:28 | 0.053909 | 0.00015726 | 57 | 19540 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv cross arms @ 204556,204514,204527. | .
128 |  | JE25006499 | TOTMANS RD | Eastern | TOTMANS RD | 2025-03-19 | 9:45 | 2025-03-19 | 13:10 | 0.0039485 | 1.9313e-05 | 7 | 1431 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Shut 9 Reworks replace Insulator on H Structure HINTIR001/E12359 and re-sag Conductor | .
129 |  | JE25006516 | MATAKANA RD | Eastern | MATAKANA RD | 2025-03-19 | 9:00 | 2025-03-19 | 14:15 | 0.033881 | 0.0001076 | 39 | 12280 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Reconductor HV from 427403 (ex 202016) to 426780 (TC3-106) | .
130 |  | JE25007096 | MANGAMAIRE | Western | MANGAMAIRE | 2025-03-19 | 9:45 | 2025-03-19 | 14:41 | 0.044904 | 0.00015174 | 55 | 16276 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace TX arms at T7/143 upgrade earthing to Powerco spec's and Straighten pole 395100. | .
131 |  | JE25008850 | GOLDEN SANDS | Eastern | GOLDEN SANDS | 2025-03-19 | 8:57 | 2025-03-19 | 16:05 | 0.00047302 | 0.00014898 | 27 | 171 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove existing CFC and replace with an automated CFCC 15056 and install a new HV cable between new CFCC and existing RMU 9937/4 | .
132 |  | JE25009013 | PARK RD | Western | PARK RD | 2025-03-19 | 3:48 | 2025-03-19 | 4:55 | 0.0051758 | 7.7251e-05 | 28 | 1876 | Unplanned | WILDLIFE - POSSUM | REGULATORY INFORMATION Voltage & Device ID: REC C422 - B Ph E/F - SEC 11133 Tripped open Protection flags (nil where none): REC C422 - B Ph E/F - SEC 11133 Tripped open CAUSE: Possum at pole 819788 Location: as above Temp generation (state details when used): NIL PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): Fine LFI (Y/N + Comments): NIL Follow up Required (select advisory)? NIL Additional fault restoration comments: NIL | .
133 |  | JE25009014 | 53 EGMONT ROAD,WAIWHAKAIHO,NEW PLYMOUTH | Western | KATERE 11 | 2025-03-19 | 6:53 | 2025-03-19 | 14:12 | 0.094318 | 0.00028417 | 103 | 34186 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 11 Protection flags (nil where none): A, B ph O/C & E/f CAUSE: (Fault 1) Branch on lines. (Fault 2) Ampack and jumper failure Location: (Fault 1) Pole 746899 & (Fault 2) Pole 749014 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: Operational Weather (wind/rain): Rain LFI (Y/N + Comments): N Follow up Required (select advisory)? N Additional fault restoration comments: (F 1) line was isolated at ABS's 256 & 447 to remove the branch. (F 2) line was isolated at CB 11, ABS's 76, 199 & 8719 to replace ampack and jumper. | .
134 |  | JE25009064 | 1427 PAREWANUI ROAD,PAREWANUI,BULLS | Western | PAREWANUI | 2025-03-19 | 10:44 | 2025-03-19 | 13:17 | 0.038245 | 0.00025107 | 91 | 13862 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Received a call from Robin Smith of a broken dead - end at Fuses 563. Line was isolated at Links 2681 & ABS 2514 to replace the dead - end and resag lines. | .
135 |  | JE25009140 | sub_PAO | Eastern | MOTUMAOHO | 2025-03-19 | 18:38 | 2025-03-20 | 1:51 | 0.32566 | 0.0019561 | 525 | 118036 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 4 Protection flags (nil where none): C Ph E/F CAUSE: Broken Insulator and Cross Arm Location: Pole I1352 PERFORMANCE DETAIL Circuit patrolled and type: Cursory Weather (wind/rain): Rain LFI (Y/N + Comments): NIL Follow up Required (select advisory)? Yes Protection - the circuit was backfeed through Piako CB 2 Sectionliser 14290 - i back livened through an area that was patrolled and deemed safe to liven. Auto reclose was disabled on RC34 and there after Closed, It was at this time that RC34 did not see the fault however Sectionliser 14290 Saw and E/F and Tripped Open Breaking the load. Meanwhile RC34 Remained Closed. Can we have some clarity why RC34 did not see the fault in this situation. Fault was found between IC701 and Recloser RC34 Their was a verified fault that was livened onto when closing RC34 that was discovered after Sectionalizer had tripped. Additional fault restoration comments: Broken Glass Insulator on Double Strain Arm Termination - Cross Arms needed replacing. | .
136 |  | JE25009141 | 14 KOPU-HIKUAI ROAD,KOPU,THAMES | Eastern | KOPU | 2025-03-19 | 18:45 | 2025-03-19 | 19:31 | 0.00012605 | 2.759e-06 | 1 | 46 | Unplanned | WILDLIFE - BIRD | Fuses Location: FC4032 No. Fuses: 3 Fuse Amp Size: 3 amp TIME CLOSED:19:30pm Cause: Bird strike Weather (wind/rain): calm Follow up required (select advisory)?Power restored | .
137 |  | JE25009149 | 86 CORDELIA STREET,STRATFORD,STRATFORD | Western | CLOTON RD SOUTH | 2025-03-19 | 20:24 | 2025-03-19 | 22:25 | 0.0006663 | 5.5179e-06 | 2 | 242 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: 12803 No. Fuses: 2 Fuse Amp Size: 30 TIME CLOSED: 22:25 Cause: unknown Weather (wind/rain): calm Follow up required (select advisory)?n | .
138 |  | JE25009150 | 87 AHU AHU ROAD,KAITAKE,NEW PLYMOUTH | Western | SEAWARD COAST | 2025-03-19 | 20:49 | 2025-03-19 | 22:59 | 0.017313 | 0.00015174 | 55 | 6275 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fault indicators operated at Pole 756750 Fuses Location: 6564 No. Fuses: 1 Fuse Amp Size: 20 TIME CLOSED: 22:39 Cause: unknown Weather (wind/rain): calm Follow up required (select advisory)?n Fuses Location: 8461 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 22:59 Cause: unknown Weather (wind/rain): calm Follow up required (select advisory)?n Line patrolled | .
139 |  | JE25009156 | sub_MIK | Eastern | MCCABE ROAD | 2025-03-19 | 21:16 | 2025-03-20 | 0:34 | 0.041801 | 0.00061525 | 223 | 15151 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: Mikkelsen 11kV CB4 Protection flags (nil where none): B - C Ground CAUSE: Unknown Location: MIKK CB4 PERFORMANCE DETAIL Circuit patrolled and type: Cursory Weather (wind/rain): Rain LFI (Y/N + Comments): NIL Follow up Required (select advisory)? NIL Additional fault restoration comments: No Fault Found Call Log of events from silver fern Farms. 22:19 -Call from silver ferns Asking when power will be back on have advise i will give an update in 30 mins 22:50 - Updated Silver Fern Farms the Limited Restoration will occur in 1 hours time and faultman where patrolling their part of the feeder first. 00:02 - Called to advised a limited backfeed was in place and they could run at reduced load. 00:47 Called Silver fern Farms to advise Circuit returned to normal and they could countine bussiness with no restrictions. Longer Fault Response time as valley faultman where on fault job on piako feeder, had to ask downer hub to assign different faultman. | .
140 |  | JE25010341 | 605 EGMONT RD,HILLSBOROUGH,NEW PLYMOUTH | Western | KATERE 5 | 2025-03-19 | 13:30 | 2025-03-19 | 14:15 | 0.0017607 | 3.8625e-05 | 14 | 638 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | FM checked the line opened fuses 8196 to check check connects on the line nothing founded 19/03/25 07:58 First Call/ Job logged 19/03/25 13:29 Controller issued instructions to remove Fuses 8196 19/03/25 14:15 Closed back in | .
141 |  | JE25002827 | KAIHERE | Eastern | KAIHERE | 2025-03-18 | 9:16 | 2025-03-18 | 14:03 | 0.019013 | 6.6215e-05 | 24 | 6891 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replacing 11kV overhead equipment (poles and crossarms) between poles O336 and 496957/423433 | .
142 |  | JE25003074 | BURNSIDE | Western | BURNSIDE | 2025-03-18 | 8:30 | 2025-03-18 | 11:41 | 0.31977 | 0.0016802 | 609 | 115903 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace cross arms, re-sag and repair 11kV lines on Burnside Feeder | .
143 |  | JE25005151 | OTAUTU | Western | OTAUTU | 2025-03-18 | 9:00 | 2025-03-18 | 15:20 | 0.075532 | 0.00019865 | 72 | 27377 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 727345, 727346. Replace HV pin arm 727347 | .
144 |  | JE25005161 | RAETIHI | Western | RAETIHI | 2025-03-18 | 8:46 | 2025-03-18 | 15:34 | 0.022533 | 5.5179e-05 | 20 | 8167 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles & cross arms from pole 777758,777759, 777760,777761,777762,777765,777766,777768,777769 | .
145 |  | JE25005517 | KOHETE RD | Western | KOHETE RD | 2025-03-18 | 9:31 | 2025-03-18 | 15:52 | 0.023148 | 6.0697e-05 | 22 | 8390 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace xarms @ poles 760170,760171,760179,760181,760182,760184,760187,760186. Replace tx 3053T Switching incident (Safety Manager 1428370) Operation 7 | .
146 |  | JE25005567 | KATERE 5 | Western | KATERE 5 | 2025-03-18 | 8:32 | 2025-03-18 | 14:54 | 0.079773 | 0.00020968 | 76 | 28914 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Intersection Henwood Rd and Manutahi Rd, systematic undergrounding of HV lines. This NAPA is for the outage requirements and work for Shut 1. Replace Poles 374234 & 746480. Remove O/H lines and ABS's 35 &480. Install 2 x new 11kV cables, from new AUTO switchgear 12777 as per plan. Day 2 outage to follow on NAPA 118784. | .
147 |  | JE25006169 | PUHUNGA ISLAND RD | Eastern | PUHUNGA ISLAND RD | 2025-03-18 | 9:31 | 2025-03-18 | 13:20 | 0.0088652 | 3.8625e-05 | 14 | 3213 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Isolation for Franklin Trees to trim trees near 11kV lines between poles O13944 and O4188 | .
148 |  | JE25006726 | KAIMAI DRIVE | Eastern | KAIMAI DRIVE | 2025-03-18 | 8:46 | 2025-03-18 | 12:31 | 0.021732 | 9.6564e-05 | 35 | 7877 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove redundant 11kV overhead conductors between Poles 211632 & new pole where links 14962 are mounted. Remove ABS SE3-033 and P/M TX TE3-202 from Manawa Energy assets on Wairoa 33kv CB372-Ruahihi 2. | .
149 |  | JE25006946 | PIONEER | Western | PIONEER | 2025-03-18 | 8:31 | 2025-03-18 | 14:42 | 0.1107 | 0.00033108 | 120 | 40124 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace multiple poles and cross arms, install two sets of temp inline links and replace transformer and structure T6/246. Worksite is between pole P44227 and ABS A78. Temp links 125 to be installed between poles P42448 & P42449. Temp links 126 to be installed between poles P42444 & P42445. | .
150 |  | JE25008804 | 1834 MORRINSVILLE-TAHUNA ROAD,TAHUNA,MORRINSVILLE | Eastern | TE PUNINGA | 2025-03-18 | 1:45 | 2025-03-18 | 7:20 | 0.048109 | 0.0010153 | 368 | 17437 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 3 Protection flags (nil where none): B & C ph O/C & E/F CAUSE: Lines down Location: 863402 & K0574 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: operational Weather (wind/rain): misty LFI (Y/N + Comments): Y Follow up Required (select advisory)? Additional fault restoration comments: Lines isolated at ABS 576 to repair lines down. Suspect due to bird strike. | .
151 |  | JE25008815 | 1334 OTARAOA ROAD,TIKORANGI,WAITARA | Western | MCKEE SOUTH 33KV | 2025-03-18 | 8:06 | 2025-03-18 | 8:16 | 0.040156 | 0.007165 | 2597 | 14555 | Unplanned | HUMAN ERROR - POTENTIAL SWITCHING ERROR | REGULATORY INFORMATION Voltage & Device ID: CB MCK191, MOT CB 210, ING CB I21 recloser 12690/2 Protection flags (nil where none): GrounDdFault, Ph-C OC, Back UP EF CAUSE: Operated LIVE ABS 211 instead of isolated 221 Location: ABS 211 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): None Circuit patrolled and type: N/A Weather (wind/rain): Rain LFI (Y/N + Comments): Yes at ABS 153 , Pole 760621 Follow up Required (select advisory)? No Additional fault restoration comments: Field switcher opened LIVE 33kV ABS 211 instead OF De-energised ABS 221 causing 33kV circuit breakers CBs 191 and 210 and 11kV Recloser 12690/2 at Inglewood to trip. All power restored after checking on Field Switcher to see if he was OK and procced with switching. and also after he confirmed with his manager that he could carry on. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): No Circuit that tripped: N/A DTF (KM): N/A | .
152 |  | JE25008881 | 4 KING EDWARD STREET,ELTHAM,ELTHAM | Western | MANGATOKI | 2025-03-18 | 11:02 | 2025-03-18 | 13:16 | 0.043147 | 0.00096564 | 350 | 15639 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: CB R51 Protection flags (nil where none): ABC Fault, HLT CAUSE: Unknown Location: Unknown Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): Nil Circuit patrolled and type: Yes, Cursory Weather (wind/rain): Rain LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Feeder patrolled, sectionalised, nothing found SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): N/A Circuit that tripped: N/A DTF (KM):N/A | .
153 |  | JE25008902 | 922 RAWHITIROA ROAD,RAWHITIROA,ELTHAM | Western | RAWHITIROA | 2025-03-18 | 14:21 | 2025-03-18 | 15:28 | 0.00037172 | 5.5179e-06 | 2 | 135 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | REGULATORY INFORMATION Voltage & Device ID: CB R31 (Fuses 7113) Protection flags (nil where none): None CAUSE: Deterioration Location: Pole 736476 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Rain LFI (Y/N + Comments): None Follow up Required (select advisory)? No Additional fault restoration comments: Isolated at Fuses 7113 and repaired jumper at Transformer 2151T (POLE 736476 and restored power. Power off - 14:20 Power on - 15:28 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): N/A Circuit that tripped: N/A DTF (KM): N/A | .
154 |  | JE25008917 | 1027 MANGAEHU ROAD,PUNIWHAKAU,STRATFORD | Western | STRATHMORE | 2025-03-18 | 12:36 | 2025-03-18 | 16:20 | 0.0067786 | 3.0349e-05 | 11 | 2457 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: Fuses 5453 No. Fuses: 2 Fuse Amp Size: 8A TIME CLOSED: 16:19 Cause: Wind Weather (wind/rain): Windy Follow up required (select advisory)? No | .
155 |  | JE25008927 | 184 3 LINE,WHANGANUI EAST,WANGANUI | Western | KIWI ST | 2025-03-18 | 13:09 | 2025-03-18 | 16:18 | 0.067519 | 0.0013353 | 484 | 24473 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 9 Protection flags (nil where none): E/F, O/C A & C CAUSE: Tree on lines Location: between Poles 790659 & 790660 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): wind, rain LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Tree fell over hit lines and blocked road Isolated at ABS 1108 & 039, unaffected network restored Tree cut away, lines repaired, hardware replaced, full power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): Cause: Chorus line low, not lines down @ 108 Talbot Street, Wanganui Actions Taken: Pulled lines back up, as high as possible Reported to Chorus: FM have reported this to them directly Chorus Ref: N/A Additional Info: Job sucked into this feeder fault, not related. | .
156 |  | JE25008959 | 2035 TARATA ROAD,TARATA,INGLEWOOD | Western | TARATA | 2025-03-18 | 15:08 | 2025-03-18 | 19:14 | 0.0061204 | 2.4831e-05 | 9 | 2218 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: 8600 No. Fuses: 2 Fuse Amp Size: 6 Amp TIME CLOSED: 19:14 hrs Cause: Possible Line Clash in strong winds Weather (wind/rain): Windy / Light Rain Follow up required (select advisory)? | .
157 |  | JE25008964 | recloser_F26 | Western | POHANGINA | 2025-03-18 | 15:20 | 2025-03-18 | 17:43 | 0.035352 | 0.0003697 | 134 | 12814 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: Rec F26 Trip, ABR F48 Trip Protection flags (nil where none): O/C A & B CAUSE: Bamboo on line Location: between Poles P14127 & P14128 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): wind, rain LFI (Y/N + Comments): n Follow up Required (select advisory)? Y - Powerco Tree person required to look at this site as there is a large bamboo plantation about 30m long and 10m high right next to the line, will need to be cut Additional fault restoration comments: Bamboo across the line found between Poles P14127 & P14128, bamboo removed with hotstick, full power restored. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
158 |  | JE25008971 | 414 NGATIRA ROAD,LICHFIELD,PUTARURU | Eastern | LICHFIELD | 2025-03-18 | 19:51 | 2025-03-18 | 21:41 | 0.00060642 | 5.5179e-06 | 2 | 220 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: Dueteration What was replaced? LV Crossarm and LV Fusing Where was it replaced (pole/TX/pillar box)? Transformer Pole Is 2R required? Y/N Yes 2R Y - What is the timeframe for repairs? Completed Additional Info: HV Isoalted at Fuses FCB12578/1 between 19:50 and 21:40 to carry out repairs | .
159 |  | JE25008975 | 1085 ALEXANDRA ROAD,MANAWARU,WAHAROA | Eastern | WAIRERE RD | 2025-03-18 | 16:01 | 2025-03-18 | 17:46 | 0.0014434 | 1.3795e-05 | 5 | 523 | Unplanned | UNKNOWN - DATA QUALITY | Fuses Location: TC2973 No. Fuses: 2 Fuse Amp Size: 3AMP TIME CLOSED: 17:45PM Cause: UNKNOWN Weather (wind/rain): CALM Follow up required (select advisory)?POWER RESTORED | .
160 |  | JE25008986 | 78 WAITOETOE ROAD, URENUI, 4377 | Western | MAIN RD MOTONUI | 2025-03-18 | 18:00 | 2025-03-19 | 10:57 | 0.028051 | 2.759e-05 | 10 | 10167 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faultman found broken cross arm at pole 762732, line was isolated at Fuses 5297. CUSTOMERS LEFT OFF OVER NIGHT DUE TO ROAD CLOSURE AT ONAERO, fm NEEDS TRUCK TO COMPLETE JOB, ROAD CLOSURE IS 4 - 8 HOURS TO OPEN . FM TRAVEL BACK VIA WANGA SH43 Faultman repaired broken cross arm supply restored. | .
161 |  | JE25005112 | MANGAWEKA | Western | MANGAWEKA | 2025-03-17 | 9:07 | 2025-03-17 | 14:55 | 0.019247 | 5.5179e-05 | 20 | 6976 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re-conductor 11KV between poles 810412 & 812118 | .
162 |  | JE25005150 | STRATHMORE | Western | STRATHMORE | 2025-03-17 | 10:16 | 2025-03-17 | 13:35 | 0.018714 | 9.3805e-05 | 34 | 6783 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove ABS 5230 from pole 708626 & install solid links 12804 on pole 708609 | .
163 |  | JE25005868 | MATAKANA RD | Eastern | MATAKANA RD | 2025-03-17 | 9:00 | 2025-03-17 | 14:41 | 0.023518 | 6.8974e-05 | 25 | 8524 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Reconductor HV from 202061 to 202075 (TC3-008) | .
164 |  | JE25005896 | KATERE 5 | Western | KATERE 5 | 2025-03-17 | 9:47 | 2025-03-17 | 10:58 | 0.0072529 | 0.00010208 | 37 | 2629 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Uncoil umbilical cable from around HV cross arm on Sectionaliser pole 12750/2 | .
165 |  | JE25006133 | CAMBRIDGE RD TAURANGA | Eastern | CAMBRIDGE RD TAURANGA | 2025-03-17 | 10:49 | 2025-03-17 | 11:24 | 0.0046573 | 0.00013519 | 49 | 1688 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install Eneida at TD4-588 | .
166 |  | JE25006333 | MANGATEPARU | Eastern | MANGATEPARU | 2025-03-17 | 8:30 | 2025-03-17 | 13:35 | 0.082474 | 0.00027038 | 98 | 29893 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To straighten poles K12658, K12657, 879057, 380916, replace arms on poles K12666, K12677, K1016, tighten stay wire on poles 879046, 480581 | .
167 |  | JE25008686 | 221 BROWN ROAD,TE PUKE,TE PUKE | Eastern | RANGIURU | 2025-03-17 | 3:20 | 2025-03-17 | 11:26 | 0.01712 | 7.4492e-05 | 14 | 6205 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faultman found 2 blown fuses at Fuses 14157, after a reload one fuse still blown Line will have to be patrolled in morning as goes across a gully and access is not good a night. Blown Transformer Found at TE6-235 - Isolated at Fuses 14157 Due to no Earthing Spiggots on Transformer TE6-235 11kV Fuses. Transformer Replaced and Power Restored All Operational. 1 x 10 Fuse Replaced at Fuses 14157. | .
168 |  | JE25008702 | 68 HACKETTS ROAD,ASHHURST,PALMERSTON NORTH | Western | ASHHURST | 2025-03-17 | 7:54 | 2025-03-17 | 11:19 | 0.00056524 | 2.759e-06 | 1 | 205 | Unplanned | WILDLIFE - BIRD | Fuses Location: 10778 No. Fuses: 2 Fuse Amp Size: 15A TIME CLOSED: 11:18 Cause: Bird strike Weather (wind/rain): calm Follow up required (select advisory)? | .
169 |  | JE25008717 | 36 DALEFIELD ROAD,CARTERTON,CARTERTON | Western | TAVERNER ST | 2025-03-17 | 8:54 | 2025-03-17 | 10:01 | 0.00018356 | 2.759e-06 | 1 | 67 | Unplanned | WILDLIFE - BIRD | Incorrect Job Location Fuses Location: 11047 No. Fuses: 2 Fuse Amp Size: 20 TIME CLOSED: 10:00 Cause: bird strike Weather (wind/rain): calm Follow up required (select advisory)?n | .
170 |  | JE25008755 | 54 KAIWHATA ROAD,TE WHARAU,MASTERTON | Western | WESTMERE GLADSTONE | 2025-03-17 | 13:21 | 2025-03-18 | 13:56 | 0.29766 | 0.00025934 | 94 | 107888 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 7417/2 Protection flags (nil where none): E/F, O/C A CAUSE: Tree on lines caused a fire Location: between poles 367782 & 365045 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): calm LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: 17/03/25 - Rec 7417/2 tripped, Fire reported, Isolated & Earthed at ABS S323, Rec 7417/2 closed Line stayed off over night so the fire brigade could put out the fire 18/03/25 - fire confirmed out, trees cut/cleared away from line, Full power restored Faultman confirmed rotten tree broke at its base, then fell across the lines causing the bush to catch fire SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): Fire comms advised ETA 15-20 mins ***Update 07:30 from Fire Comms Branches on lines - Tree cutters Required Hub updated *** | .
171 |  | JE25008759 | 2522 PIPIRIKI RAETIHI ROAD,PIPIRIKI,WANGANUI | Western | RAETIHI | 2025-03-17 | 14:24 | 2025-03-17 | 18:00 | 0.0053817 | 2.4831e-05 | 9 | 1951 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses 145 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 1800 Cause: POSSIBLE BIRD STRIKE Weather (wind/rain): Follow up required (select advisory)? RESTORED | .
172 |  | JE25008762 | unknown KOKIRI ROAD,Kapuni,Rural | Western | MATAPU | 2025-03-17 | 14:46 | 2025-03-17 | 15:40 | 0.0028482 | 5.242e-05 | 19 | 1032 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | REGULATORY INFORMATION Voltage & Device ID: CB 7 Protection flags (nil where none): No tripping CAUSE: Jumper failure Location: Pole720064 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Removed Jumpers at pole 720064 to an a redundant overhead line. Restored power to rest of feeder. Isolated at ABS KA763 and Links 12570/4 | .
173 |  | JE25008765 | 456A TE WHARAU ROAD,KOURARAU HILL,MASTERTON | Western | PUKETIRO | 2025-03-17 | 15:19 | 2025-03-17 | 17:56 | 0.006921 | 4.4143e-05 | 16 | 2509 | Unplanned | WILDLIFE - BIRD | Fuses Location: 7856 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 17:55 Cause: Bird strike Weather (wind/rain): windy Follow up required (select advisory)?n Line patrolled | .
174 |  | JE25008768 | WAITOTARA VALLEY ROAD, WAITOTARA, 4588 | Western | WAITOTARA | 2025-03-17 | 16:56 | 2025-03-18 | 11:26 | 0.26336 | 0.00023727 | 86 | 95457 | Unplanned | ADVERSE ENVIRONMENT - FIRE | ETA 40 MINS Bush Fire, between Poles 780189 - 780190, Fire requested Isolation of Lines at ABS 545 left 2 r open lines isolated overnight, no etr from fire , wanted lines isolated due to helicopters flying dumping water 18/03/25 Site Inspection - after vegetation fire Contact Clive Lennox - Incident Controller FENZ Call came via FENZ (Josh) DR 18/03/25 - Faultman has inspected affected network and found no damage from the fire, feeder restored at 11:25 | .
175 |  | JE25008774 | 364 WAITEIKA ROAD,OPUNAKE,OPUNAKE | Western | TE KIRI | 2025-03-17 | 18:44 | 2025-03-17 | 20:36 | 0.0070859 | 6.3456e-05 | 23 | 2568 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: Floating conductor burnt through cross arm. What was replaced? HV Cross Arm & 3x HV fuse holders Isolation: ABS TA995 Where was it replaced (pole/TX/pillar box)? Pole 715848 Is 2R required? Yes 2R Y - What is the timeframe for repairs? Complete Additional Info: | .
176 |  | JE25008794 | 36 MANGATANGI ROAD,WAVERLEY,WAVERLEY | Western | WAVERLEY | 2025-03-17 | 19:27 | 2025-03-17 | 22:37 | 0.22811 | 0.0017795 | 645 | 82681 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV, CB 262 Protection flags (nil where none): Nil CAUSE: Broken Glass Insulator Location: Pole 772106 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Yes / Operational Weather (wind/rain): Calm / Heavy Rain LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Section of WAV CB242 had to be isolated as both feeders on the same pole SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
177 |  | JE25008798 | 3 DUNLOP ROAD,WAHAROA,WAHAROA | Eastern | MOWBRAY RD | 2025-03-17 | 20:47 | 2025-03-18 | 0:57 | 0.10203 | 0.0016885 | 484 | 36983 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 1 Protection flags (nil where none): A ph E/F CAUSE: cracked glass insulator Location: pole H2175 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: operational Weather (wind/rain): calm LFI (Y/N + Comments): N Follow up Required (select advisory)? Additional fault restoration comments: line was isolated at ABS's 852 & IC1192 & Links 14999/4 to replace insulators on pole H2175 | .
178 |  | JE25008803 | 900 QUINE ROAD,TAHUNA,MORRINSVILLE | Eastern | HOE-O-TAINUI | 2025-03-17 | 22:50 | 2025-03-18 | 9:48 | 0.010892 | 1.6554e-05 | 6 | 3948 | Unplanned | WILDLIFE - BIRD | Fuses Location: FP1287 No. Fuses: 2 Fuse Amp Size: 10a TIME CLOSED: 0948 Cause: bird Weather (wind/rain): fine Follow up required (select advisory)? 2R for 2 x fuse barrels | .
179 |  | JE25005239 | PAHIATUA 1 | Western | PAHIATUA 1 | 2025-03-16 | 23:31 | 2025-03-17 | 1:27 | 0.044311 | 0.00038074 | 138 | 16061 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace 11kv DDOs and fly arm at TX T7/451 | .
180 |  | JE25008616 | 2794 OLD TAUPO ROAD, TOKOROA, 3491 | Eastern | OLD CAMBRIDGE RD | 2025-03-16 | 0:46 | 2025-03-16 | 3:31 | 0.012302 | 7.4492e-05 | 27 | 4459 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: Stub Pole # A12625 holding 33/11 Pole KINMAR062 hit by Car. Protection flags (nil where none): CAUSE: Stub Pole # A12625 holding Pole KINMAR062 hit by Car Location: Pole A12625 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Fine LFI (Y/N + Comments): Nil Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
181 |  | JE25008625 | 26 MOUNT STEWART HALCOMBE ROAD,SANSON,PALMERSTON NORTH | Western | MT STEWART | 2025-03-16 | 6:14 | 2025-03-16 | 14:52 | 0.076135 | 0.0014898 | 540 | 27595 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: REC 10368 Protection flags (nil where none): A & B Phase OC EF CAUSE: Car V Pole Location: P21114 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: N/A Weather (wind/rain): Calm / Light Rain LFI (Y/N + Comments): Pole 444464 indicated correctly, Pole P21781 has no comms Follow up Required (select advisory)? Additional fault restoration comments: Event # F4171100. Replaced Pole & Hardware. HV fuseholder complete & HV Insulator at TX 7309P. Replaced 3x Insulators at P21116, & repaired multiple lines down. | .
182 |  | JE25008629 | 815 2 ,OPAKI,MASTERTON | Western | OXFORD ST | 2025-03-16 | 7:36 | 2025-03-16 | 9:26 | 0.0041337 | 3.8625e-05 | 14 | 1498 | Unplanned | WILDLIFE - BIRD | Fuses Location: 11kV Fuses 11097 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 09:25 Cause: Birds Weather (wind/rain): Fine Follow up required (select advisory)? | .
183 |  | JE25008647 | 379A POREWA ROAD,MARTON,MARTON | Western | LEEDSTOWN 22KV | 2025-03-16 | 11:04 | 2025-03-16 | 12:41 | 0.00026611 | 2.759e-06 | 1 | 96 | Unplanned | WILDLIFE - BIRD | Fuses Location: 4922 No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 12:40 Cause: Birds nest Weather (wind/rain): Overcast Follow up required (select advisory)? Full power restored | .
184 |  | JE25008652 | 51 MOKI ROAD,URUTI,URENUI | Western | MAIN RD MOTONUI | 2025-03-16 | 9:16 | 2025-03-16 | 18:25 | 0.026642 | 0.0001683 | 61 | 9657 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV, Rec 12131 Protection flags (nil when none): Unknown CAUSE: tree through the lines. 2 Span of HV & LV Lines down Location: Pole 765149 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: Yes / Cursory Weather (wind/rain): Calm / Light Rain Follow up required (select advisory)? Additional fault restoration comments: No Comms to Rec 12131 so unknown what time it tripped | .
185 |  | JE25008660 | 183 MAXWELL STATION ROAD,MAXWELL,WANGANUI | Western | MAXWELL | 2025-03-16 | 15:34 | 2025-03-16 | 16:20 | 0.0030351 | 6.6215e-05 | 24 | 1100 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 825 No. Fuses: 2 Fuse Amp Size: 15 Amp TIME CLOSED: 16:19 hrs Cause: Unk Suspect Bird Weather (wind/rain): Calm Follow up required (select advisory)? | .
186 |  | JE25008577 | 1834 MORRINSVILLE-TAHUNA ROAD,TAHUNA,MORRINSVILLE | Eastern | TE PUNINGA | 2025-03-15 | 6:32 | 2025-03-15 | 10:32 | 0.0172 | 0.0010153 | 368 | 6234 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 3 Protection flags (nil where none): E/F, O/C A, B & C CAUSE: Bird strike / Lines down Location: between Poles K0580 & K058 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: n Weather (wind/rain): calm LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Line down remained live/Scrub fire reported under JE25008576 by fire comm's Boaz pulled of another job to go to this fault Job CB 3 Tripped before faultman could get to site and isolate fault Isolated at ABS 576 CB 3 Restored New crew organised to fix fault, Lines repaired & Full power restored | .
187 |  | JE25008590 | 51 ,, | Eastern | APATA | 2025-03-15 | 10:15 | 2025-03-15 | 12:50 | 0.013671 | 8.8287e-05 | 32 | 4955 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: SC2-126 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 12:50 Cause: Unknown Weather (wind/rain): calm Follow up required (select advisory)?n Line patrolled | .
188 |  | JE25008599 | FEEDER FAULT - FEATERSTON SUB - REVANS ST - SEC 11392 | Western | REVANS ST | 2025-03-15 | 11:44 | 2025-03-15 | 15:30 | 0.24437 | 0.0058987 | 1111 | 88574 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB C916 Protection flags (nil where none): E/F, O/C B & C CAUSE: Jumper failed Location: 814416 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: op Weather (wind/rain): calm LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: CB C916 & Sec 11392/2 tripped, CB C916 A/R Reports of lines down came in for Fox St, CB C916 Opened by NOC Back feed put in place for customer's between Rec C634 & Gas/Sw 11035 faultman confirmed faulted area Isolated between ABS S557 & Links 11385/4 CB C916 restored Part power jobs started coming in, line patrolled back towards the sub and a blown jumper found at Pole 814389 due to fault current ABS S575 opened and back feed put in place from Rec C634 (Power taken off as unable to parallel with missing phase) Isolated at ABS 8056, S587 & S575 Jumper repaired, power restored between ABS 8056, S587 & S575 Lines down at Pole 814416 repaired, full power restored Fault was caused by a jumper that has failed/broken and fallen down across another phase (mid span connection between 2 lines) SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
189 |  | JE25008617 | 1559C RANGIURU ROAD,TE RANGA,TE PUKE | Eastern | MANGOREWA | 2025-03-15 | 21:45 | 2025-03-15 | 23:43 | 0.0022814 | 1.9313e-05 | 7 | 827 | Unplanned | WILDLIFE - BIRD | Fuses Location: SF5-014 No. Fuses: 2 x fuses Fuse Amp Size: 15 TIME CLOSED: 23:43 Cause: Bird Strike Weather (wind/rain): fine Follow up required (select advisory)? | .
190 |  | JE25008618 | 3090A MOUNTAIN ROAD,MIDHIRST,STRATFORD | Western | CLOTON RD NORTH | 2025-03-15 | 22:57 | 2025-03-16 | 0:33 | 0.085501 | 0.0010263 | 372 | 30990 | Unplanned | WILDLIFE - POSSUM | REGULATORY INFORMATION Voltage & Device ID: REC 6616 Protection flags (nil where none): EF CAUSE: Possum on the lines Location: Pole 761206 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): Fine LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Removed with hot sticks | .
191 |  | JE25002121 | MANGATI RD | Western | MANGATI RD | 2025-03-14 | 9:06 | 2025-03-14 | 14:48 | 0.013842 | 4.4143e-05 | 16 | 5017 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Car vs pole damaged the 11kV cable between BBK CB1 to pole 743615. Work to joint new section of cable & re-install on new pole 949955. | .
192 |  | JE25002709 | BROOKLANDS 5 | Western | BROOKLANDS 5 | 2025-03-14 | 9:30 | 2025-03-14 | 14:22 | 0.023731 | 0.00024279 | 60 | 8602 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Outage to work at Mangorei Sub and 4 pole structure, doing multiple jobs. DRG R1666N maintenance, ABS maintenance. Replacing broken Lightning arrestors, replace broken cable blocks. | .
193 |  | JE25002825 | KAIHERE | Eastern | KAIHERE | 2025-03-14 | 9:01 | 2025-03-14 | 14:16 | 0.020845 | 6.6215e-05 | 24 | 7555 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replacing 11kV overhead equipment (poles and crossarms) between poles O336 and 496957/423433 | .
194 |  | JE25003174 | KAIMATA | Western | KAIMATA | 2025-03-14 | 8:31 | 2025-03-14 | 15:23 | 0.012513 | 3.0349e-05 | 11 | 4535 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace crossarms at poles 760555,760558,760559,840601,840602,760563. | .
195 |  | JE25004803 | MANGATOKI | Western | MANGATOKI | 2025-03-14 | 9:16 | 2025-03-14 | 16:05 | 0.021449 | 5.242e-05 | 19 | 7774 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Tx 2473T & pole 733411 | .
196 |  | JE25004825 | LONGBUSH | Western | LONGBUSH | 2025-03-14 | 9:00 | 2025-03-14 | 14:31 | 0.022802 | 6.8974e-05 | 25 | 8265 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV poles, hardware and conductor past ABS S67 | .
197 |  | JE25005102 | MANGAWEKA | Western | MANGAWEKA | 2025-03-14 | 9:08 | 2025-03-14 | 15:58 | 0.026001 | 6.3456e-05 | 23 | 9424 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re-conductor 11KV between poles 810412 & 812118 | .
198 |  | JE25005119 | COROGLEN | Eastern | COROGLEN | 2025-03-14 | 8:48 | 2025-03-14 | 15:18 | 0.0078353 | 0.00022623 | 41 | 2840 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Faulty 11kv Sectionaliser 13063 | .
199 |  | JE25005516 | TE ARAKURA | Western | TE ARAKURA | 2025-03-14 | 14:46 | 2025-03-14 | 15:51 | 0.019532 | 0.00029797 | 108 | 7079 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Connect new 11kV cable that comes from RMU 147 at pole P32371 and connect cable jumpers directly to the OH line to replace the decommissioned cable. This will put the Network back to original state prior to this project. Check 11kV phasing at RMU 147. | .
200 |  | JE25005704 | TE POI | Eastern | TE POI | 2025-03-14 | 8:48 | 2025-03-14 | 14:20 | 0.014634 | 4.4143e-05 | 16 | 5304 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace existing pole F1370 & install new TP4526 50kVA PMT. | .
201 |  | JE25008234 | MANGATEPARU | Eastern | MANGATEPARU | 2025-03-14 | 10:04 | 2025-03-14 | 11:50 | 0.000586 | 5.5179e-06 | 2 | 212 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | INSTALL A NEW DEADMAN BEHIND POLE K12741, PULL POLE BACK, AND RESTRAIN OVERHEAD hv TO GET UP TO LEGAL HEIGHT | .
202 |  | JE25008326 | KAIMATA | Western | KAIMATA | 2025-03-14 | 8:48 | 2025-03-14 | 15:13 | 0.025272 | 0.00010208 | 37 | 9160 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV crossarm at pole 760526 | .
203 |  | JE25008371 | 257 NGAIO ROAD, PALMERSTON NORTH, 4479 | Western | KAKARIKI | 2025-03-14 | 9:31 | 2025-03-14 | 11:32 | 0.0066758 | 5.5179e-05 | 20 | 2420 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole is not in danger, it has been this way for a long time. Will apply for an urgent NAPA Repaired under NAPA E00188 | .
204 |  | JE25008458 | 704R PEMBROKE ROAD,PEMBROKE,STRATFORD | Western | CARDIFF RD | 2025-03-14 | 4:37 | 2025-03-14 | 6:04 | 0.00048177 | 5.5179e-06 | 2 | 175 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 5661 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 06:04 Cause: Suspect Bird Strike Weather (wind/rain): calm Follow up required (select advisory)? | .
205 |  | JE25008459 | 213 PARK ROAD,PARKVALE,CARTERTON | Western | PARK RD | 2025-03-14 | 5:13 | 2025-03-14 | 6:21 | 0.00018671 | 2.759e-06 | 1 | 68 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses 7598 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 06:20 Cause: Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? No | .
206 |  | JE25008487 | COROGLEN | Eastern | COROGLEN | 2025-03-14 | 13:16 | 2025-03-14 | 17:06 | 0.0012678 | 5.5179e-06 | 2 | 460 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faulty TFR TC5281, Very high loop impedances on Phases at bushings I & E at TFR TC5281 Fuses TFR Replaced, Full power restored | .
207 |  | JE25008499 | recloser_9665:2 | Eastern | WAOTU | 2025-03-14 | 10:25 | 2025-03-14 | 13:36 | 0.062489 | 0.00052696 | 191 | 22650 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Recloser 9665 Protection flags (nil where none): B Phase O/C E/F CAUSE: Unknown Location: Unknown Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Fine LFI (Y/N + Comments): Yes and working Follow up Required (select advisory)? Yes Additional fault restoration comments: Recloser 9665 was out of scan at time so we did not get alarms patrolled Lines nothing Found Recloser 9665 is in and out of scan so may need to get it checked out Soon SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
208 |  | JE25008533 | 304 GORDON STREET, LANSDOWNE, MASTERTON | Western | GORDON ST | 2025-03-14 | 15:12 | 2025-03-14 | 15:43 | 0.0001705 | 5.5179e-06 | 2 | 62 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Resecure cross arm at Pole 848515 | .
209 |  | JE25008549 | 1367 CAMERONS LINE,AORANGI,FEILDING | Western | TE ARAKURA | 2025-03-14 | 16:05 | 2025-03-14 | 16:32 | 0.0078614 | 0.00029797 | 108 | 2849 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | . | .
210 |  | JE25008550 | 131 GUNN ROAD,MATAMATA,MATAMATA | Eastern | STATION RD | 2025-03-14 | 16:21 | 2025-03-14 | 17:31 | 0.00096636 | 1.3795e-05 | 5 | 350 | Unplanned | THIRD PARTY INTERFERENCE - OTHER | Fuses Location: TC3190 No. Fuses: 3 Fuse Amp Size: 3 TIME CLOSED: 17-31 Cause: water Blasting House Weather (wind/rain): Fine Follow up required (select advisory)? | .
211 |  | JE25008562 | MATUA SUB - WARATAH ST - MATUA/5 | Eastern | WARATAH ST | 2025-03-14 | 20:13 | 2025-03-14 | 21:09 | 0.059223 | 0.0022734 | 824 | 21466 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Cable Fault from Sw/Gear 13798/3 Protection flags (nil where none): O/C E/F CAUSE: Cable Fault Location: Sw/Gear 13798 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): DNO 2503011 Circuit patrolled and type: Unknown Weather (wind/rain): Fine LFI (Y/N + Comments): Yes 13798/3 Follow up Required (select advisory)? Additional fault restoration comments: Some Notes missing above, Cable Fault and Fault within sw gear motor Wiring on Sw/Gear 13798/3 This has been repaired and is now operational | .
212 |  | JE25008565 | KEREPEHI SUB - KAIHERE - KEREPEHI SUB/1 | Eastern | KAIHERE | 2025-03-14 | 21:56 | 2025-03-15 | 1:55 | 0.11147 | 0.0094467 | 3424 | 40403 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: Bird strike on CB 1 @ Pole 0134 dropped Squirrel Conductor ,The Fault was not cleared by CB 1 resulting in CB 17 & 19 opening . this is the 3rd time to my knowledge CB 1 has not cleared a fault and Caused this. CB 18 has been left open to save a total loss of supply till the protection has been sorted Protection flags (nil where none): CB 1 B, C Phase O/C, CB 17 & CB 19 E/F B Phase CAUSE: Bird strike on CB 1 @ Pole 0134 dropped Squirrel Conductor ,The Fault was not cleared by CB 1 resulting in CB 17 & 19 opening . this is the 3rd time to my knowledge CB 1 has not cleared a fault and Caused this. Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Fine LFI (Y/N + Comments): nil Follow up Required (select advisory)? Additional fault restoration comments: CB 1 & CB 17 & CB 19 need their protection actually checked , Discrimination Levels. High Low Contact also Houses inspected, 1 left off till morning , Inside metering. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Kerepehi Substation Circuit that tripped: CB 17 & CB 19 DTF (KM): lv re livened 0947 after inspector checked | .
213 |  | JE25001881 | TE ROTI | Western | TE ROTI | 2025-03-13 | 9:01 | 2025-03-13 | 14:34 | 0.0061698 | 8.2769e-05 | 30 | 2236 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | AP:01 - Replace fuses 5162 on pole 733604. AP:02 - Replace poles 733605, 733607 & 733608 & 11kV xarms at poles 733606 & 733609. | .
214 |  | JE25004913 | RAETIHI | Western | RAETIHI | 2025-03-13 | 8:30 | 2025-03-13 | 15:48 | 0.024127 | 5.5179e-05 | 20 | 8745 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles & cross arms from pole 777733,777734,777736,476943,777752,777753,777754,777756 | .
215 |  | JE25004917 | BEACH RD WAIHI BEACH | Eastern | BEACH RD WAIHI BEACH | 2025-03-13 | 9:00 | 2025-03-13 | 14:20 | 0.034468 | 0.0001076 | 39 | 12493 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 33kV Crossarms between poles 860944/860945 to CREWBH072 Waihi Beach Rd | .
216 |  | JE25005139 | COROGLEN | Eastern | COROGLEN | 2025-03-13 | 9:09 | 2025-03-13 | 14:44 | 0.043427 | 0.00012967 | 47 | 15740 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace crossarms etc at various sites and resag 11kV OH lines between TC1504 & TP3864 + cut trees main line and vicinity FC4120 | .
217 |  | JE25005165 | MOUNT | Eastern | MOUNT | 2025-03-13 | 10:05 | 2025-03-13 | 11:45 | 0.01327 | 0.00013243 | 48 | 4810 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Linkbox maintenance at TC5-020 | .
218 |  | JE25005330 | HUIROA | Western | HUIROA | 2025-03-13 | 9:46 | 2025-03-13 | 16:33 | 0.046043 | 0.00011312 | 41 | 16689 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | drop lines between poles 709290 & 709291. so over hanging pine trees can be dropped | .
219 |  | JE25005336 | PURANGI | Eastern | PURANGI | 2025-03-13 | 8:53 | 2025-03-13 | 15:43 | 0.71768 | 0.0017492 | 634 | 260126 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 1: W1456: Replace XArms 2: W1391, IC2125. Remove ABS IC2125. Replace pole. Install Sectionaliser 14470 and pole mount links on source side towards pole W1456 3: W13697, 2703. Remove ABS 2703 4: W1457: Replace pole. Install Sectionaliser 14467 and pole mount links on source side towards pole W1456 5: Commission new Sectionalisers 14470 & 14467 | .
220 |  | JE25005418 | KAIMATA | Western | KAIMATA | 2025-03-13 | 9:16 | 2025-03-13 | 14:08 | 0.0040338 | 1.3795e-05 | 5 | 1462 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace cracked 33kV/11kV pole 760610 found on the Inglewood re-arm project | .
221 |  | JE25005812 | OWERA RD | Eastern | OWERA RD | 2025-03-13 | 8:20 | 2025-03-13 | 15:55 | 0.002507 | 5.5179e-06 | 2 | 909 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Matarangi Generator Project Stage 2 Reroute existing 3 feeder cables connected to RMU 9457 into new Matarangi generator 11kV switchboard and remove RMU 9457. Commission new Matarangi 11kV generator switchboard and LST TP4446 into service. Generator to be left isolated & earthed, ready network connected testing on 18-19/3/25 . | .
222 |  | JE25006324 | 18TH AVE | Eastern | 18TH AVE | 2025-03-13 | 10:08 | 2025-03-13 | 14:12 | 0.033072 | 0.00013519 | 49 | 11987 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Reinstate cable break at pole# 386034 | .
223 |  | JE25008051 | PAPAMOA BEACH WEST | Eastern | PAPAMOA BEACH WEST | 2025-03-13 | 10:33 | 2025-03-13 | 13:31 | 0.061083 | 0.00034487 | 125 | 22140 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Connect new overlayed cable at SD5-085L1 & TD5-164 remove generation | .
224 |  | JE25008284 | 1250A TE WHITI ROAD,GLADSTONE,MASTERTON | Western | PUKETIRO | 2025-03-13 | 4:10 | 2025-03-13 | 5:53 | 0.0014246 | 1.3795e-05 | 5 | 516 | Unplanned | WILDLIFE - POSSUM | Fuses Location: Transformer T951 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 05:53 Cause: Possum Weather (wind/rain): Calm Follow up required (select advisory)?No | .
225 |  | JE25008286 | 149 25 ,WAITAKARURU,THAMES | Eastern | PUHUNGA ISLAND RD | 2025-03-13 | 7:11 | 2025-03-13 | 7:14 | 0.00033977 | 0.00012967 | 47 | 123 | Unplanned | WILDLIFE - BIRD | . | .
226 |  | JE25008447 | 307 INAHA ROAD,MANAIA,HAWERA | Western | OKAIAWA | 2025-03-13 | 19:35 | 2025-03-13 | 20:51 | 0.0037569 | 4.9661e-05 | 18 | 1362 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faultman found DDO's & jumpers on transformer 5199E were damaged due to age & deterioration, line was isolated at ABS's MA 415 & MA 579 to replace the DDO's & jumpers. | .
227 |  | JE25008453 | 51 ,, | Eastern | APATA | 2025-03-13 | 22:43 | 2025-03-14 | 0:26 | 0.0090237 | 8.8287e-05 | 32 | 3271 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses SC2-126 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 00:25 Cause: Swans Weather (wind/rain): Calm Follow up required (select advisory)? No | .
228 |  | JE25002798 | KAIHERE | Eastern | KAIHERE | 2025-03-12 | 8:46 | 2025-03-12 | 15:20 | 0.026122 | 6.6215e-05 | 24 | 9468 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replacing 11kV overhead equipment (poles and crossarms) between poles O336 and 496957/423433 | .
229 |  | JE25003141 | TE KIRI | Western | TE KIRI | 2025-03-12 | 9:35 | 2025-03-12 | 12:01 | 0.0024298 | 1.6554e-05 | 6 | 881 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | DRG 12307/2 maintenance and testing. | .
230 |  | JE25004817 | LONGBUSH | Western | LONGBUSH | 2025-03-12 | 8:45 | 2025-03-12 | 15:23 | 0.027455 | 6.8974e-05 | 25 | 9951 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV poles, hardware and conductor past ABS S67 | .
231 |  | JE25004872 | MATAKANA RD | Eastern | MATAKANA RD | 2025-03-12 | 9:16 | 2025-03-12 | 11:30 | 0.0092793 | 6.8974e-05 | 25 | 3363 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace LV Pole 202065. Reconductor LV 202065 to 202061. HV Outage required for Safety | .
232 |  | JE25004900 | RAETIHI | Western | RAETIHI | 2025-03-12 | 8:45 | 2025-03-12 | 15:44 | 0.023111 | 5.5179e-05 | 20 | 8377 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles & cross arms form pole 777721,777723,777725,777728,477351,419101,777732 | .
233 |  | JE25005163 | KAIMATA | Western | KAIMATA | 2025-03-12 | 9:00 | 2025-03-12 | 14:24 | 0.0071509 | 2.2072e-05 | 8 | 2592 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 760618 and hardware. Replace crossarms on poles 760620, 759685, 758993, 758994, 758995. | .
234 |  | JE25005332 | BENNETT ST | Eastern | BENNETT ST | 2025-03-12 | 9:45 | 2025-03-12 | 15:48 | 0.024995 | 6.8974e-05 | 25 | 9060 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv & 400v Xarms at poles S0356,S12845,877767,S12825,877493,S12851 | .
235 |  | JE25006523 | LOCKINGTON ROAD | Eastern | LOCKINGTON ROAD | 2025-03-12 | 10:15 | 2025-03-12 | 13:57 | 0.14504 | 0.00065387 | 237 | 52571 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace DNO sectionaliser 9865/2 with Entec. Remove Bypass ABS 9865/1 and load side links 9865/6 . Install Source side swing links 9865/4. This will remove DNO 2410015. | .
236 |  | JE25008125 | 53 MANUTAHI ROAD,TARURUTANGI,NEW PLYMOUTH | Western | KATERE 5 | 2025-03-12 | 0:40 | 2025-03-12 | 3:11 | 0.020626 | 0.00019865 | 72 | 7476 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 12251/2, Sec 12745/2 Protection flags (nil where none): E/F, O/C C CAUSE: unknown Location: na Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): rain LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Line patrolled, no fault found, full power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
237 |  | JE25008131 | 66 NORFOLK ROAD,WAINGAWA,CARTERTON | Western | WAINGAWA RD | 2025-03-12 | 4:11 | 2025-03-12 | 5:43 | 0.021798 | 0.00040833 | 148 | 7901 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: CB C881 Protection flags (nil where none): B Phase EF CAUSE: No Fault Found Location: High St Masterton Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): Fine LFI (Y/N + Comments): Yes Indicated Past Sw/Gear 11374/1 Follow up Required (select advisory)? Additional fault restoration comments: No Fault Found | .
238 |  | JE25008135 | 53 MANUTAHI ROAD,TARURUTANGI,NEW PLYMOUTH | Western | KATERE 5 | 2025-03-12 | 10:02 | 2025-03-12 | 12:38 | 0.0077472 | 4.9661e-05 | 18 | 2808 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Brent (0272206950) is sorting out the thermal camera and some one to patrol the line. At pole 746589 failed surge arrestor was found. Lines were isolated and three surge arrestors and insulators were replaced. Voltage & Device ID: 11kV Rec 12251/2 Protection flags (nil where none): E/F, O/C C Weather (wind/rain): rain Follow up required (select advisory): Line patrol with thermal camera LFI Activation: N | .
239 |  | JE25008140 | 15 OLD DEVON ROAD, NEW PLYMOUTH, 4373 | Western | DEVON RD | 2025-03-12 | 7:18 | 2025-03-12 | 10:30 | 0.010579 | 5.5179e-05 | 20 | 3834 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 3 Protection flags (nil where none): Nil CAUSE: Insulator failure Location: 742055 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Not patrolled Weather (wind/rain): Rain LFI (Y/N + Comments): no Follow up Required (select advisory)? no Additional fault restoration comments: Fire on pole due to insulator failure. Replaced HV double pin arm complete assembly SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
240 |  | JE25008158 | 1065 RONGOTEA ROAD,RONGOTEA,PALMERSTON NORTH | Western | KOPANE | 2025-03-12 | 9:14 | 2025-03-12 | 13:15 | 0.040618 | 0.0005849 | 212 | 14722 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: Nil Protection flags (nil where none): Nil CAUSE: Car vs Pole Location: P36983 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: operation Weather (wind/rain): calm LFI (Y/N + Comments): Nil Follow up Required (select advisory)? N Additional fault restoration comments: Faultman advised no lines down at car vs pole, line was isolated at ABS 10182/1, Links 10182/4, ABS 10416/1, Links 10416/6 & Links C21/4 to replace pole and hardware. | .
241 |  | JE25008193 | unknown SH 2 ,Waihi,Waihi | Eastern | WAIHI BEACH RD | 2025-03-12 | 12:02 | 2025-03-14 | 13:39 | 0.048636 | 0.00048558 | 66 | 17629 | Unplanned | THIRD PARTY INTERFERENCE - TREES | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 9713 & Sec 13200 Protection flags (nil where none): O/C A & B CAUSE: Tree hit lines and broke Pole Location: P0353 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: cur Weather (wind/rain): unknown LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Forestry workers felling trees have had a tree hit the lines and broke a pole 14/03/25 - Isolated at ABS 217, pole replaced, full power restored | .
242 |  | JE25008206 | 1641 HOMEWOOD ROAD,HOMEWOOD,MASTERTON | Western | BLAIRLOGIE | 2025-03-12 | 10:18 | 2025-03-12 | 13:01 | 0.00044976 | 2.759e-06 | 1 | 163 | Unplanned | WILDLIFE - BIRD | Fuses Location: 8164 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 13:00 Cause: Birdstrike Weather (wind/rain): NA Follow up required (select advisory)? An issue with Emap sucked original job into JE25008117 unknown reason Remake request as downer were happy with this . N2R rrequired | .
243 |  | JE25008247 | 173 COLOMBO ROAD,MASTERTON,MASTERTON | Western | COLOMBO RD | 2025-03-12 | 19:48 | 2025-03-12 | 20:59 | 0.063026 | 0.0015174 | 550 | 22844 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | CHECK JE25008248 ON CLOSURE CHECK JE25008251 ON CLOSURE CHECK JE25008252 ON CLOSURE REGULATORY INFORMATION Voltage & Device ID: Recloser 11259/2 Protection flags (nil where none): None CAUSE: Broken jumper at Pole 833045 Location: Pole 833045 Temp generation (state details when used): None PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Windy LFI (Y/N + Comments): None Follow up Required (select advisory)? No Additional fault restoration comments: Back fed upto S81/2, ISOLATEED AT Links 81/4, Links 83/4 and Recloser 11259.Repaired jumper under access permit power restored at 20:58 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
244 |  | JE25008273 | JE25008263 | Western | WAITE ST | 2025-03-12 | 21:13 | 2025-03-12 | 21:44 | 0.0057735 | 0.00018485 | 67 | 2093 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | REGULATORY INFORMATION Voltage & Device ID: ABS S549 Protection flags (nil where none): No Tripping CAUSE: Broken jumper Location: Pole 818857 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Windy LFI (Y/N + Comments): None Follow up Required (select advisory)? No Additional fault restoration comments: Isolated at ABS S549and Links S570. Repaired jumper at Pole 818857 under ACCESS permit. Isolated at 21:13. Restored at 21:44 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): No Circuit that tripped: No DTF (KM):N/A | .
245 |  | JE25003135 | JUNCTION RD | Western | JUNCTION RD | 2025-03-11 | 9:11 | 2025-03-11 | 11:56 | 0.02778 | 0.0001683 | 61 | 10069 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | DRG 12171/2 maintenance and testing. | .
246 |  | JE25004643 | TOTMANS RD | Eastern | TOTMANS RD | 2025-03-11 | 9:16 | 2025-03-11 | 9:48 | 0.00026003 | 8.2769e-06 | 3 | 94 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Restrain heavy duty HV stay wire at TC2281 | .
247 |  | JE25004645 | PLEASANT POINT | Eastern | PLEASANT POINT | 2025-03-11 | 9:30 | 2025-03-11 | 15:13 | 0.18438 | 0.00055455 | 201 | 66828 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace faulty RMU 9782 with new automated CCC. Commission SCADA controls. | .
248 |  | JE25004668 | KOPANE | Western | KOPANE | 2025-03-11 | 9:15 | 2025-03-11 | 15:12 | 0.019672 | 5.5179e-05 | 20 | 7130 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11KV conductor to neon from P45028 to P29591 | .
249 |  | JE25004768 | HUNTERVILLE 22KV | Western | HUNTERVILLE 22KV | 2025-03-11 | 10:01 | 2025-03-11 | 10:30 | 0.00016416 | 5.5179e-06 | 2 | 60 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV Binders on pole 806862 raised by Helicopter Topography | .
250 |  | JE25004773 | FORDELL | Western | FORDELL | 2025-03-11 | 10:01 | 2025-03-11 | 11:09 | 0.010839 | 0.00016002 | 58 | 3929 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV Binders on pole 791150 raised by Helicopter Topography | .
251 |  | JE25004819 | NO 3 ROAD | Eastern | NO 3 ROAD | 2025-03-11 | 10:03 | 2025-03-11 | 14:34 | 0.0052457 | 1.9313e-05 | 7 | 1901 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Reconductor OH HV From 223556 to 382033 | .
252 |  | JE25004916 | COROGLEN | Eastern | COROGLEN | 2025-03-11 | 9:46 | 2025-03-11 | 16:05 | 0.12018 | 0.00031728 | 115 | 43558 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole W12475. Remove Sectionaliser 13199/2 and replace with Recloser with Pole Mount links and ABS. Recloser to retain same number as Sectionaliser i.e. 13199. New recloser site to be left by-passed (ABS 13199/1 Closed) until future SCADA commissioning. | .
253 |  | JE25005441 | KAIMAI DRIVE | Eastern | KAIMAI DRIVE | 2025-03-11 | 8:46 | 2025-03-11 | 13:44 | 0.00082383 | 2.759e-06 | 1 | 299 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove redundant 11kv overhead conductors between poles 390298 & 211622 from Manawa Energy assets on Wairoa 33kv CB372-Ruahihi 2 | .
254 |  | JE25005684 | WATERWORKS RD | Western | WATERWORKS RD | 2025-03-11 | 9:00 | 2025-03-11 | 16:02 | 0.046568 | 0.00011036 | 40 | 16879 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Cut trees between poles 468625 & 784220 | .
255 |  | JE25007518 | WHARAWHARA ROAD | Eastern | WHARAWHARA ROAD | 2025-03-11 | 9:45 | 2025-03-11 | 12:46 | 0.0074761 | 4.1384e-05 | 15 | 2710 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Connect new 11kv overlayed cable at IP652 & TB1-094 and remove generation. New cable tested before connection, no TP required . Remove DNO 2502018 | .
256 |  | JE25007993 | 940 CARRINGTON ROAD,HURWORTH,NEW PLYMOUTH | Western | BROOKLANDS 7 | 2025-03-11 | 1:27 | 2025-03-11 | 11:15 | 0.031201 | 0.00029245 | 106 | 11309 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV, Rec 12353/2 Protection flags (nil where none): E/F, B phase CAUSE: Duck Strike Location: Pole 702133 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Yes / Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Possible HV/LV clash. Tx 1320 left off for testing by inspector before livening LV installations checked by inspected no fault found. 1320 transformer Fuses 1 x 2A Lines repaired 10m x 16mm² HD Cu SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
257 |  | JE25007997 | 663 MAIN DRAIN ROAD,RANGIOTU,PALMERSTON NORTH | Western | TAIKOREA | 2025-03-11 | 3:38 | 2025-03-11 | 6:06 | 0.015486 | 0.00010484 | 38 | 5613 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: B12 No. Fuses: 2 Fuse Amp Size: 15 Amp TIME CLOSED: 06:05 hrs Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)? | .
258 |  | JE25008012 | 270 FAIRFIELD ROAD,HAWERA,HAWERA | Western | MANAWAPOU RD | 2025-03-11 | 8:03 | 2025-03-11 | 10:35 | 0.00041975 | 2.759e-06 | 1 | 152 | Unplanned | WILDLIFE - BIRD | Fuses Location: WH822 No. Fuses: 2 Fuse Amp Size: 8A TIME CLOSED:10:35 Cause: Bird Weather (wind/rain): Sunny Follow up required (select advisory)? N2R Did not create verified job on Emaps when opening fuses | .
259 |  | JE25008039 | 213 PARK ROAD,PARKVALE,CARTERTON | Western | PARK RD | 2025-03-11 | 9:53 | 2025-03-11 | 10:17 | 6.5433e-05 | 2.759e-06 | 1 | 24 | Unplanned | WILDLIFE - BIRD | Fuses Location: 7598 No. Fuses: 3 Fuse Amp Size: 6AMP Outage Time 09:53 AM TIME CLOSED: 10:16AM Cause: BIRDSTRIKE Weather (wind/rain): CALM Follow up required (select advisory)?NO FOLLOW UP 2R IS BEING USED FOR FUSE REPLACEMENT | .
260 |  | JE25008105 | 267 GLUE POT ROAD,OROPI,TAURANGA | Eastern | WAIMAPU | 2025-03-11 | 20:00 | 2025-03-11 | 23:43 | 0.0049275 | 2.2072e-05 | 8 | 1786 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Transformer TF4-007 Faulty Transformer Replaced all voltage and readings correct | .
261 |  | JE25008117 | 7 MANGAPURUPURU ROAD,BIDEFORD,MASTERTON | Western | BIDEFORD | 2025-03-11 | 20:07 | 2025-03-12 | 14:09 | 0.021058 | 0.00013795 | 50 | 7632 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: SEC C218/2 Protection flags (nil where none): A B C GROUND CAUSE: NOT FOUND Location: PAST FUSES 7771 Temp generation (state details when used): NIK PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: CURSOARY Weather (wind/rain): FINE LFI (Y/N + Comments): NIL Follow up Required (select advisory)? Additional fault restoration comments: Operational Control past Sectionliser C218/2 due to poor coms, Sectionlised Line Closed Sectionliser C218/2 at 20:39 livened to ABS S148 - ABS S148 Closed at 21:41 to ABS S150 - ABS S150 Livened to end of line at 21:51 Spur Line isolated at Fuses 7771, Goes through Forestry, Requires ATV and daylight to safetly navigated - to be patrolled in daylight Line patrolled in first day and found lines down due tree through lines at poles 839345 & 845684, line was already isolated at Fuses 7771, operational control was issued to Stu Coulson, lines were repaired supply restored. | .
262 |  | JE25008118 | 95 PAPAITI ROAD,PAPAITI,WANGANUI | Western | MAKIRIKIRI | 2025-03-11 | 20:08 | 2025-03-11 | 21:06 | 0.0024019 | 4.1384e-05 | 15 | 871 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: 2829 No. Fuses: 2 Fuse Amp Size: 15A TIME CLOSED: 21:05 Cause: Wind Weather (wind/rain): Windy Follow up required (select advisory)? Full power restored | .
263 |  | JE25002012 | KAIHERE | Eastern | KAIHERE | 2025-03-10 | 8:46 | 2025-03-10 | 14:20 | 0.011976 | 3.5867e-05 | 13 | 4341 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace cross arms on pole O316, O317, O14183, O14184,O318, O319, O320, O12404, O321, O322, O324, 859221, O329, O331. | .
264 |  | JE25004502 | MANAIA COROMANDEL | Eastern | MANAIA COROMANDEL | 2025-03-10 | 9:30 | 2025-03-10 | 14:24 | 0.076949 | 0.0002621 | 95 | 27890 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Access permit for Franklyn Trees to cut at two sites COR CB5 vicinity poles V0404 and V0433 | .
265 |  | JE25004594 | MANGATEPARU | Eastern | MANGATEPARU | 2025-03-10 | 8:26 | 2025-03-10 | 15:05 | 0.083596 | 0.00020968 | 76 | 30300 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace HV arms on poles I0471, I0470, I13807, I0203, I13799, I0190, I13804, I0455 | .
266 |  | JE25004678 | MATAKANA RD | Eastern | MATAKANA RD | 2025-03-10 | 9:00 | 2025-03-10 | 13:51 | 0.020016 | 6.8974e-05 | 25 | 7255 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace LV Pole 202074. Reconductor LV 202074 to 202072 and from 202072 to 202069. HV Outage required for Safety | .
267 |  | JE25004810 | LONGBUSH | Western | LONGBUSH | 2025-03-10 | 9:01 | 2025-03-10 | 15:15 | 0.025838 | 6.8974e-05 | 25 | 9365 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV poles, hardware and conductor past ABS S67 | .
268 |  | JE25005125 | PASCAL ST 6 | Western | PASCAL ST 6 | 2025-03-10 | 9:31 | 2025-03-17 | 13:17 | 0.053976 | 0.00039177 | 71 | 19564 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | STAGE 2 - INSTALL NEW SW/GEAR 10935 AND CARRY OUT NECESSARY 11KV JOINTING. INSTALL & CONNECT NEW 11KV CABLE BETWEEN 10927/3 & 10935/1 | .
269 |  | JE25007848 | 282 RUAKERE ROAD,WAREA,NEW PLYMOUTH | Western | WAREA | 2025-03-10 | 3:41 | 2025-03-10 | 5:01 | 0.00066339 | 8.2769e-06 | 3 | 240 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: P1245 No. Fuses: 2 Fuse Amp Size: 3 Amp TIME CLOSED: 05:01hrs Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)? | .
270 |  | JE25007850 | 3 PARAPARA ROAD, RAETIHI | Western | RAETIHI | 2025-03-10 | 4:58 | 2025-03-10 | 13:00 | 0.028193 | 0.00049937 | 145 | 10219 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 284 Protection flags (nil where none): O/C A - B Ø CAUSE: Car V pole Location: 376434 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: F5, not patrolled. Weather (wind/rain): Calm LFI (Y/N + Comments): No none installed. Follow up Required (select advisory)? NDR to follow Additional fault restoration comments: Event # F4166232 Pole 376434 damaged by vehicle, driver did a runner, 1 x Pole replaced with 11m 1 x HV pin cross arm complete assembly SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
271 |  | JE25007854 | 149 25 ,WAITAKARURU,THAMES | Eastern | MANGATARATA | 2025-03-10 | 6:38 | 2025-03-10 | 6:42 | 0.00044788 | 0.00012967 | 47 | 162 | Unplanned | WILDLIFE - BIRD | . | .
272 |  | JE25007869 | 130 CANAL WEST ROAD,WAITAKARURU,THAMES | Eastern | PUHUNGA ISLAND RD | 2025-03-10 | 8:41 | 2025-03-10 | 12:14 | 0.039826 | 0.00057111 | 207 | 14435 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: Recloser 9969 Protection flags (nil where none): None CAUSE: Broken cross arms-deterioration Location: Pole O3694 Temp generation (state details when used): NO PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Opened Recloser 9969 as EMERGENCY as 11kV was 100mm from LV. Isolated at ABS IC465, Gas/Sw 13233/4 and Sectionaliser 14729/4.Replaced 2 x Termination arms and restored power at 12:13 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): N/A Circuit that tripped: N/A DTF (KM):N/A | .
273 |  | JE25007894 | 1543 LONGBUSH ROAD,LONGBUSH,MASTERTON | Western | LONGBUSH | 2025-03-10 | 10:17 | 2025-03-10 | 12:08 | 0.0009247 | 8.2769e-06 | 3 | 335 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | Fuses Location: 8189 No. Fuses: 2 Fuse Amp Size: 8a TIME CLOSED: 1208 Cause: vegetation on pole 823622 Weather (wind/rain): Follow up required (select advisory)? main switch was off on arrival left main switch off . | .
274 |  | JE25007923 | recloser_RC05 | Eastern | RANGITANUKU RD | 2025-03-10 | 12:29 | 2025-03-10 | 19:18 | 0.13978 | 0.0015505 | 352 | 50662 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec RC05 Protection flags (nil where none): E/F CAUSE: Broken HV jumper Location: TC3233 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: F4, Cursory patrolled. Weather (wind/rain): Calm LFI (Y/N + Comments): Installed but fault before LFI Follow up Required (select advisory)? No Additional fault restoration comments: HV jumper broke at transformer TC3233 which caused a localized scrub fire which the fire brigade extinguished. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
275 |  | JE25007956 | 536 HIMATANGI BLOCK ROAD,FOXTON,FOXTON | Western | BAINESSE | 2025-03-10 | 17:05 | 2025-03-10 | 18:56 | 0.00030612 | 2.759e-06 | 1 | 111 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: 10462 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 18:55 hrs Cause: Unknown Weather (wind/rain): Windy Follow up required (select advisory)? | .
276 |  | JE25007958 | 626 2 LINE,FORDELL,WANGANUI | Western | UNION LINE | 2025-03-10 | 17:49 | 2025-03-10 | 19:00 | 0.0084352 | 0.00011864 | 43 | 3057 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: 2792 No. Fuses: 2 Fuse Amp Size: 30a TIME CLOSED: 1900 Cause: unknown Weather (wind/rain): good lite wind Follow up required (select advisory)? full power restored | .
277 |  | JE25007982 | 298 BEDFORD ROAD NORTH,KAIMIRO,INGLEWOOD | Western | MOUNTAIN RD | 2025-03-10 | 20:34 | 2025-03-10 | 21:28 | 0.001954 | 3.5867e-05 | 13 | 708 | Unplanned | WILDLIFE - BIRD | Fuses Location: 5547 No. Fuses: 2 Fuse Amp Size: 8 TIME CLOSED: 2128 Cause: bird Weather (wind/rain): fine Follow up required (select advisory)? | .
278 |  | JE25007983 | 211 SHARP ROAD,AONGATETE,KATIKATI | Eastern | WILLS RD | 2025-03-10 | 20:38 | 2025-03-10 | 21:29 | 0.0016674 | 3.3108e-05 | 12 | 604 | Unplanned | WILDLIFE - BIRD | Fuses Location: SB2 069 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 21:28 Cause: BIRD STRIKE Weather (wind/rain): FINE Follow up required (select advisory)? | .
279 |  | JE25007984 | WAIHI SUB - WAIHI NORTH - 9604/2 | Eastern | WAIHI NORTH | 2025-03-10 | 20:45 | 2025-03-11 | 4:43 | 0.077663 | 0.00045799 | 166 | 28149 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV Recloser 9604 Protection flags (nil where none): EF CAUSE: Trees on Lines at Pole 876769 Location: 700 Waihi Whangamata Road Temp generation (state details when used): NIL PERFORMANCE DETAIL DNO (number or state No): NIL Circuit patrolled and type: Cursory Weather (wind/rain): Fine LFI (Y/N + Comments): NIL No indications Follow up Required (select advisory)? NIL Additional fault restoration comments: NIL Trees through line - brought conductors down and broke crossarms, was on a tight blind corner required bucket and additional resources all repairs complete | .
280 |  | JE25004612 | WORKS | Western | WORKS | 2025-03-09 | 8:00 | 2025-03-12 | 7:02 | 0.00072092 | 5.5179e-06 | 1 | 261 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Move LV from existing panel at TX T3/310 into new RDL cabinet next to T3/310. Connect the generator to the Genport in the RDL cabinet to supply the LV distribution for 3 days while TX T3/310 & RMU 146,147,FS60 are getting upgraded into the same location. Complete HV joint across the road to join in new section of cable back to RMU 146. Terminate HV cables at TX T3/310 & RMU 146,147,FS60. Remove generator once all work is complete and liven through to RMU 146,FS60 & TX T3/310. | .
281 |  | JE25007811 | 1557 WOODLANDS ROAD,MORRINSVILLE,MORRINSVILLE | Eastern | MANGATEPARU | 2025-03-09 | 2:00 | 2025-03-09 | 4:59 | 0.0049427 | 2.759e-05 | 10 | 1792 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Car V Pole Found at Pole K0998 Isolated at Fuses FC2147 Reported to Police event number P061855097 Pole Replaced | .
282 |  | JE25007813 | 13 STATION ROAD,WAVERLEY,WAVERLEY | Western | WAVERLEY | 2025-03-09 | 1:00 | 2025-03-09 | 3:52 | 0.046672 | 0.00033659 | 122 | 16917 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: REC 2680 Protection flags (nil where none): A phase EF CAUSE: 1 x line down. Corroded off at the insulator Location: Pole 771842 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: cursory Weather (wind/rain): Calm LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
283 |  | JE25007816 | 9110 PAEROA KOPU ROAD,MATATOKI,THAMES | Eastern | PURIRI | 2025-03-09 | 7:48 | 2025-03-09 | 9:26 | 0.0029632 | 3.0349e-05 | 11 | 1074 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: FP1332 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 09:25 Cause: Unknown Weather (wind/rain): Fine Follow up required (select advisory)? NIL | .
284 |  | JE25007833 | 276 TE WHITI SETTLEMENT ROAD,TE WHITI,MASTERTON | Western | PUKETIRO | 2025-03-09 | 13:01 | 2025-03-09 | 14:19 | 0.00021607 | 2.759e-06 | 1 | 78 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses 11125 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 14:19 Cause: Bird on transformer Weather (wind/rain): Fine Follow up required (select advisory)? NIL | .
285 |  | JE25007845 | unknown SH 3 ,Waverley,Waverley | Western | RANGIKURA | 2025-03-09 | 22:58 | 2025-03-10 | 0:57 | 0.0052641 | 4.4143e-05 | 16 | 1908 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV, Rec 1112 Protection flags (nil where none): A/R, E/F, O/C B-C phase CAUSE: Lines Down due to suspect Bird Strike Location: Pole 470507 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Yes / Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Lines down repaired & relivened SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
286 |  | JE25007764 | 3090A MOUNTAIN ROAD,MIDHIRST,STRATFORD | Western | CLOTON RD NORTH | 2025-03-08 | 6:37 | 2025-03-08 | 9:59 | 0.13502 | 0.0010263 | 372 | 48938 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: Recloser 6616/2 Protection flags (nil where none): OC - B & C Phase CAUSE: Trees on lines Location: Pole Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): None Follow up Required (select advisory)? No Additional fault restoration comments: Lines patrolled. Found tree on lines at Pole. Removed trees under Access Permit, isolations at ABS 12654 and 5536. Restored power at 09:58,. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): N/A Circuit that tripped: N/A DTF (KM):N/A | .
287 |  | JE25007794 | 87 AHU AHU ROAD,KAITAKE,NEW PLYMOUTH | Western | SEAWARD COAST | 2025-03-08 | 15:19 | 2025-03-08 | 16:26 | 0.010194 | 0.00015174 | 55 | 3695 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: Fuses 6564 No. Fuses: 2 Fuse Amp Size: 15A TIME CLOSED: 16:25 Cause: Deterioration Weather (wind/rain): Calm Follow up required (select advisory)? No | .
288 |  | JE25000865 | POHANGINA | Western | POHANGINA | 2025-03-07 | 9:18 | 2025-03-07 | 10:19 | 0.0089027 | 0.00014623 | 53 | 3227 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV crossarm at pole P13073 | .
289 |  | JE25003612 | BUNNYTHORPE | Western | BUNNYTHORPE | 2025-03-07 | 10:00 | 2025-03-07 | 15:10 | 0.080504 | 0.00025934 | 94 | 29179 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace HV xarms at pole P38730 (T2/238) & LV xarms at pole P38729 | .
290 |  | JE25004345 | ATHENREE | Eastern | ATHENREE | 2025-03-07 | 8:31 | 2025-03-07 | 13:05 | 0.050554 | 0.00018485 | 67 | 18323 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To clean out and replace HV cable termination at SA2-016 | .
291 |  | JE25004360 | CLOTON RD WEST | Western | CLOTON RD WEST | 2025-03-07 | 9:02 | 2025-03-07 | 14:52 | 0.040508 | 0.00011588 | 42 | 14683 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | ELE021493 Automated OH Tie Point FY25. Removing ABS's to install automated Safelink 12769 tie points. Work done in 2 outages. This NAPA is for shut 2 of 2. Shut 1 to be completed first on NAPA 118720. | .
292 |  | JE25004439 | LONGBUSH | Western | LONGBUSH | 2025-03-07 | 9:00 | 2025-03-07 | 14:36 | 0.023189 | 6.8974e-05 | 25 | 8405 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles , hardware and conductors past ABS 67 | .
293 |  | JE25004480 | SANDHURST | Eastern | SANDHURST | 2025-03-07 | 23:31 | 2025-03-08 | 2:29 | 0.01229 | 6.8974e-05 | 25 | 4455 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9569/1/2/3 | .
294 |  | JE25004588 | WAIHI NORTH | Eastern | WAIHI NORTH | 2025-03-07 | 9:17 | 2025-03-07 | 15:01 | 0.0047339 | 1.3795e-05 | 5 | 1716 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV Insulator arm and 11kV fuse arm on Pole P13370 using LLP GB-T07 and GB-T17. | .
295 |  | JE25004781 | MANGAWEKA | Western | MANGAWEKA | 2025-03-07 | 9:24 | 2025-03-07 | 12:53 | 0.0063616 | 3.0349e-05 | 11 | 2306 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Multiple poles & X-Arms between poles 812176 & 812118 | .
296 |  | JE25004838 | PUHUNGA ISLAND RD | Eastern | PUHUNGA ISLAND RD | 2025-03-07 | 9:00 | 2025-03-07 | 19:50 | 0.082772 | 0.00012967 | 47 | 30001 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles and remove 11kV lines on CB5 and connecting CB5 & CB 7 together. Install temp links TEMP055 | .
297 |  | JE25005375 | KEENAN RD | Eastern | KEENAN RD | 2025-03-07 | 8:47 | 2025-03-07 | 14:14 | 0.045627 | 0.00014623 | 53 | 16538 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv overhead conductors between poles 211666 & 211670 | .
298 |  | JE25005575 | UPPER MANAIA RD | Western | UPPER MANAIA RD | 2025-03-07 | 8:42 | 2025-03-07 | 12:54 | 0.039554 | 0.00015726 | 57 | 14336 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Isolate 33kV & 11kV to relocate sheath earths on pole 456232/484921 and pole 470675/471284 | .
299 |  | JE25007316 | PILLANS POINT | Eastern | PILLANS POINT | 2025-03-07 | 10:16 | 2025-03-07 | 14:54 | 0.030821 | 0.00022072 | 80 | 11171 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | connect new overlayed cable at pole 206774 and remove generation | .
300 |  | JE25007470 | CITY 6 | Western | CITY 6 | 2025-03-07 | 8:48 | 2025-03-07 | 15:19 | 0.69324 | 0.0017713 | 642 | 251268 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 753328 and remove ABS 223. Install new manual Entec switch 12789/2 with solid links (12789/4) replace DNO ABS 246. | .
301 |  | JE25007579 | 359 MORETON ROAD,PARKVALE,CARTERTON | Western | PARK RD | 2025-03-07 | 7:13 | 2025-03-07 | 8:58 | 0.012092 | 0.00011588 | 42 | 4383 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 7600 No. Fuses: 2 Fuse Amp Size: 20 AMP TIME CLOSED: 8:57 Cause: UNKNOWN Weather (wind/rain): CALM Follow up required (select advisory)?N/A | .
302 |  | JE25007612 | 295 FOREST ROAD,PAREWANUI,BULLS | Western | PAREWANUI | 2025-03-07 | 7:11 | 2025-03-07 | 8:58 | 0.0005923 | 5.5179e-06 | 2 | 215 | Unplanned | WILDLIFE - BIRD | Fuses Location: 4146 No. Fuses: 2 Fuse Amp Size: 10 AMP TIME CLOSED: 8:58 Cause: BIRDSTRIKE Weather (wind/rain): CALM Follow up required (select advisory)?N/A | .
303 |  | JE25007666 | KAI IWI SUB - WATERWORKS RD - 1026/2 | Western | WATERWORKS RD | 2025-03-07 | 12:14 | 2025-03-07 | 12:29 | 0.0015882 | 0.00011036 | 40 | 576 | Unplanned | HUMAN ERROR - POTENTIAL WORKMANSHIP | REGULATORY INFORMATION Voltage & Device ID: 11kV Recloser 1026 Protection flags (nil where none): A, C Ph Fault CAUSE: Branch contacted lines will tree trimming under NAPA 119555-05 Location: between Poles 468625 & 784220 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Windy LFI (Y/N + Comments): N Follow up Required (select advisory)? N Additional fault restoration comments: Power restored after tree trimmers confirmed they cause branch to contact lines. FM to Check for damage to lines. Tree trimmer remaining on site until FM on site. All work stopped FM checked site . All ok SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
304 |  | JE25001472 | MAKIRIKIRI | Western | MAKIRIKIRI | 2025-03-06 | 9:24 | 2025-03-06 | 13:31 | 0.0040841 | 1.6554e-05 | 6 | 1480 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace defected pole 790651 raised by Helicopter Topography | .
305 |  | JE25003798 | KAIMAI DRIVE | Eastern | KAIMAI DRIVE | 2025-03-06 | 8:37 | 2025-03-06 | 10:38 | 0.001001 | 8.2769e-06 | 3 | 363 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Liven 3c 185 mm HV cable from CFCF 15001/2 to existing transformer TE3-191. Cap redundant cable Unable to close job until Transformer is transferred on Emap | .
306 |  | JE25003981 | MANAIA | Western | MANAIA | 2025-03-06 | 9:16 | 2025-03-06 | 15:17 | 0.0039898 | 1.1036e-05 | 4 | 1446 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace HV poles 719605, 719606, 719607 & 719608 & LV pole 719604 | .
307 |  | JE25004110 | NEWTON ST | Eastern | NEWTON ST | 2025-03-06 | 17:02 | 2025-03-06 | 18:15 | 0.010886 | 0.00014898 | 54 | 3946 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To carry out PD tests and clean cables and HV terminations on SC4-323 | .
308 |  | JE25004130 | LINDERMANN RD | Eastern | LINDERMANN RD | 2025-03-06 | 8:45 | 2025-03-06 | 14:22 | 0.061383 | 0.00018209 | 66 | 22249 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv/400vt cross arms @852923, 259939,204635,259940. Replace 11kv poles, 204631 & 204632. Isolation point @ SB1-002. | .
309 |  | JE25004138 | MATAKANA RD | Eastern | MATAKANA RD | 2025-03-06 | 9:01 | 2025-03-06 | 15:05 | 0.025139 | 6.8974e-05 | 25 | 9112 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 202071 and 202075 TC3-008 incl LV poles 202081 to 202083. Replace LV OH Line from 383952 to 202083 | .
310 |  | JE25004346 | CLOTON RD SOUTH | Western | CLOTON RD SOUTH | 2025-03-06 | 9:42 | 2025-03-06 | 14:27 | 0.073139 | 0.00025658 | 93 | 26510 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | ELE021493 Automated OH Tie Point FY25. Removing ABS's to install automated Safelink 12769 tie points. Work done in 2 outages. This NAPA is for shut 1 of 2. Shut 2 to follow on NAPA 118721 Switching did not go smoothly: 1) Back feed of CB's - loading issue with CLO 7 the donor feeder going into alarm limit 2 197A, 2) An additional back feed installed to reduce load of CLO 7 via CLO 5 3) ABS 5917 failed to open which was required for an isolation point for CLO 8, possibly welded contacts. | .
311 |  | JE25004477 | RAETIHI | Western | RAETIHI | 2025-03-06 | 8:46 | 2025-03-06 | 15:46 | 0.023162 | 5.5179e-05 | 20 | 8395 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles & cross-arms form pole 777713,777714,777715,777716,777718,777717,777719,777720 | .
312 |  | JE25004512 | WAIHI NORTH | Eastern | WAIHI NORTH | 2025-03-06 | 9:30 | 2025-03-06 | 12:24 | 0.00047771 | 2.759e-06 | 1 | 173 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Disconnect Fuses 13322 so 11kv service to TP3780 be isolated to carry out work. Replace 11kv arm on Pole WHIWGM061 using LLP GB-01. Request reclose block on 33kv OH line. | .
313 |  | JE25004811 | COROGLEN | Eastern | COROGLEN | 2025-03-06 | 9:15 | 2025-03-06 | 12:10 | 0.0033636 | 1.9313e-05 | 7 | 1219 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Isolate 66kV and 11kV line to replace insulators at pole CGNTAI 156/157 | .
314 |  | JE25004918 | CAMERON RD | Eastern | CAMERON RD | 2025-03-06 | 23:36 | 2025-03-07 | 2:28 | 0.021367 | 0.00012415 | 45 | 7745 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9395-1/2/3/4/5/6 | .
315 |  | JE25007421 | unknown unknown ,Kinleith,Rural | Eastern | KINLEITH 2752 | 2025-03-06 | 0:51 | 2025-03-06 | 3:03 | 0.00036267 | 2.759e-06 | 1 | 131 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: KIN CB 2752 Protection flags (nil where none): OC, Neutral Time, Earth Fault CAUSE: Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Downer Faultman delayed to be let in by Kinleith Staff (Awaiting keys to unlock gate and start line patrol from 01:24.-02:)). Line patrolled, Lightning arrestor at Fuses FP257 broken. pieces on the ground. Can't tell whether recent or have been like that for a long time. FRM to organise planned shut to replace. Besides that sectionalised and nothing else found. Full power restored | .
316 |  | JE25007456 | MANAWA ENERGY HYDRO RD ,BURGESS PARK RURAL , 4386 | Western | KAIPI RD | 2025-03-06 | 9:24 | 2025-03-06 | 11:11 | 0.0002942 | 2.759e-06 | 1 | 107 | Unplanned | WILDLIFE - BIRD | Fuses Location: 12117 No. Fuses: 2 Fuse Amp Size: 6 AMP TIME CLOSED: 11:10AM Cause: BIRD STRIKE Weather (wind/rain): CALM Follow up required (select advisory)?N/A | .
317 |  | JE25007494 | PAENGAROA SUB - MAUNGARANGI RD - PAENGAROA/6 | Eastern | MAUNGARANGI RD | 2025-03-06 | 12:01 | 2025-03-06 | 15:29 | 0.019246 | 0.00032004 | 116 | 6976 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 6 & Sec 9834 Protection flags (nil where none): A, B, C Ph, E/F CAUSE: Tree brought Lines down Location: Pole 230122 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Yes Follow up Required (select advisory)? Additional fault restoration comments: CB 6 Tripped A/R, Sectionaliser 9834 Tripped LFI active at Pole 221847 Isolated at Fuses SF6-008 Tree cleared from Lines, Lines repaired SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
318 |  | JE25007498 | 92 HAHEI BEACH ROAD, WHITIANGA | Eastern | COROGLEN | 2025-03-06 | 14:06 | 2025-03-06 | 15:46 | 0.0011014 | 1.1036e-05 | 4 | 399 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Transformer TC1090 found to be faulty Isolated at Fuses for Transformer Transformer replaced | .
319 |  | JE25007504 | 46 MANGAMAHU ROAD,FORDELL,WANGANUI | Western | FORDELL | 2025-03-06 | 11:45 | 2025-03-06 | 13:35 | 0.00090821 | 8.2769e-06 | 3 | 329 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 940 No. Fuses: 2 Fuse Amp Size: 15 AMP TIME CLOSED: 13:35 Cause: WIND Weather (wind/rain): CALM Follow up required (select advisory)?N/A | .
320 |  | JE25007517 | 770 MANAIA ROAD,KAPUNI,HAWERA | Western | AUROA | 2025-03-06 | 14:09 | 2025-03-06 | 14:42 | 0.0050664 | 0.00015726 | 57 | 1836 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | At pole 719158 a twisted cross arm was repaired. The section of line was isolated and earthed, repaired the twisted cross arm by replacing the bracing strap bolts. | .
321 |  | JE25007531 | switch_12594 | Western | CAMBRIA LS | 2025-03-06 | 15:33 | 2025-03-06 | 17:03 | 0.0009947 | 1.1036e-05 | 4 | 361 | Unplanned | THIRD PARTY INTERFERENCE - DIG IN | HV Cable fed off Links 12594 hit during SO JE25006965, this job is to complete repairs ***Safety Manager on closure*** REGULATORY INFORMATION Voltage & Device ID: 11kV Links 12594 Protection flags (nil where none): Nil CAUSE: Digger damaged HV cable Location: Links 12594 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: N/A Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? NDR to follow Additional fault restoration comments: During a standover an U/G cable was damaged by a digger. The cable was isolated and a repair zip sleeve installed. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
322 |  | JE25007557 | unknown RADNOR ROAD,Midhirst,Rural | Western | CLOTON RD NORTH | 2025-03-06 | 12:22 | 2025-03-06 | 19:37 | 0.0086596 | 0.00012691 | 44 | 3139 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faultman found after replacing transformer 2638T that there was a problem with the voltages after transformer was restored to service. Faultman found that the fuses supplying the transformer were of the old type. Line was isolated at FusedABS 5454 and the full set of DDO's were replaced and after re-livening transformer 2638T the voltages were tested and found all in order. | .
323 |  | JE25009388 | BOWENTOWN | Eastern | BOWENTOWN | 2025-03-06 | 10:02 | 2025-03-06 | 11:05 | 0.00069471 | 1.1036e-05 | 4 | 252 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace broken transformer support arm at TA2-076 - 06/03/2025 10:00-14:00 | .
324 |  | JE25001273 | RANGITANUKU RD | Eastern | RANGITANUKU RD | 2025-03-05 | 9:15 | 2025-03-05 | 13:57 | 0.066035 | 0.00023451 | 85 | 23935 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE POLES ; 878905/E0050/E0051/E0056 & XARM E0023 | .
325 |  | JE25003698 | PASCAL ST 9 | Western | PASCAL ST 9 | 2025-03-05 | 9:00 | 2025-03-05 | 15:59 | 0.10629 | 0.00025382 | 92 | 38527 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | STAGE 1 - REPLACE 11KV CABLE BETWEEN PAS CB9 & G318.INSTALL NEW SW/GEAR 10927.DISCONNECT CABLE BETWEEN G183/A & G318. | .
326 |  | JE25003773 | PAREWANUI | Western | PAREWANUI | 2025-03-05 | 9:22 | 2025-03-05 | 15:30 | 0.0030437 | 8.2769e-06 | 3 | 1103 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install line break at pole 809539, replace pole 809541, X arms on poles 809540, and 809542 (X2166) remove line break 809539 | .
327 |  | JE25003814 | AUROA | Western | AUROA | 2025-03-05 | 9:31 | 2025-03-05 | 11:25 | 0.022107 | 0.00019313 | 70 | 8013 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV ABS insulator for 12139/1 | .
328 |  | JE25003932 | MAIN RD MOTONUI | Western | MAIN RD MOTONUI | 2025-03-05 | 9:46 | 2025-03-05 | 14:53 | 0.0059274 | 1.9313e-05 | 7 | 2148 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Change 11kV poles 764901, 764902 & 764903 with digger | .
329 |  | JE25003939 | PUHUNGA ISLAND RD | Eastern | PUHUNGA ISLAND RD | 2025-03-05 | 9:15 | 2025-03-05 | 15:06 | 0.022289 | 6.3456e-05 | 23 | 8079 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv conductor between Pole sites 427148/427102 and 426181/425988 | .
330 |  | JE25004288 | WAIPUNA | Eastern | WAIPUNA | 2025-03-05 | 8:30 | 2025-03-05 | 16:18 | 0.018063 | 3.8625e-05 | 14 | 6547 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace HV and LV arms on Poles 213136, 213135, 213143 and 213142 | .
331 |  | JE25004316 | CAMBRIA LS | Western | CAMBRIA LS | 2025-03-05 | 10:00 | 2025-03-05 | 16:13 | 0.026945 | 0.00015174 | 55 | 9767 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Pole 856591, 11kV cable termination failure. Outage to remove cable from pole and joint new section cable up pole. Due to Links both sides, Isolate transformers to do livening and phasing. Proposed switching methodology attached. | .
332 |  | JE25004341 | DAIRYFACT | Western | DAIRYFACT | 2025-03-05 | 9:30 | 2025-03-05 | 12:39 | 0.0010422 | 5.5179e-06 | 2 | 378 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace transformer Xarm T6/12 Reconductor LV conductor | .
333 |  | JE25004364 | MOFFAT RD | Eastern | MOFFAT RD | 2025-03-05 | 23:31 | 2025-03-06 | 3:17 | 0.23483 | 0.0010374 | 376 | 85117 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance 9135/1/2/3/4 | .
334 |  | JE25005098 | TURAKINA | Western | TURAKINA | 2025-03-05 | 8:30 | 2025-03-05 | 12:41 | 0.015894 | 6.3456e-05 | 23 | 5761 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Correcting defects on poles from and including pole 851027 and 794726 | .
335 |  | JE25006514 | KAIMAI DRIVE | Eastern | KAIMAI DRIVE | 2025-03-05 | 10:40 | 2025-03-05 | 13:07 | 0.0032324 | 2.2072e-05 | 8 | 1172 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove redundant 11kv lines from pole 498408 - 211714 and broken X arm 211710 | .
336 |  | JE25007252 | unknown OHURA ROAD,Tahora,Rural | Western | STRATHMORE | 2025-03-05 | 10:20 | 2025-03-06 | 15:57 | 0.024514 | 1.3795e-05 | 5 | 8885 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: 4103T CAUSE: Lightning Temp generation (stage details when used): No TX BLOWN, REPLACING TONIGHT 05/03/25 PERFORMANCE DETAIL DNO (number or state no): N/A Circuit patrolled & type: No Weather (wind/rain): Lightning Follow up required (select advisory)? No Additional fault restoration comments: 1 x 30kVA 3 Ø 11kV / 400V transformer 3 x Surge arrestors 1 x 3m steel LV cross arm 3 x 3A HV fuses | .
337 |  | JE25007253 | 3124 POHANGINA ROAD,POHANGINA,ASHHURST | Western | POHANGINA | 2025-03-05 | 7:22 | 2025-03-05 | 8:44 | 0.00022467 | 2.759e-06 | 1 | 81 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T4/192 No. Fuses: 2 Fuse Amp Size: 3AMP CLOSED: 08:43 Cause: LIGHTNING Weather (wind/rain): CALM Follow up required (select advisory)?NOT NEEDED JOB LINK JE25007264 HAS THE CORRECT DETAILS | .
338 |  | JE25007278 | CLAREVILLE SUB - WYNDHAM ST - C841 | Western | WYNDHAM ST | 2025-03-05 | 9:12 | 2025-03-05 | 14:40 | 0.52094 | 0.0086714 | 3143 | 188817 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: CB C838 / CB C841 Protection flags (nil where none): EF CAUSE: Car V Pole Location: Pole 853771 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: N Weather (wind/rain): Windy LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: NDR to follow | .
339 |  | JE25007282 | 7468 26 ,KOMATA,PAEROA | Eastern | BENNETT ST | 2025-03-05 | 7:08 | 2025-03-05 | 11:16 | 0.01244 | 9.6564e-05 | 35 | 4509 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV DTX TC2174 Broken D/Out Replaced x 3 & Crossarm Protection flags (nil where none): CAUSE: DTX TC2174 Broken D/Out Replaced x 3 & Crossarm Location: DTX TC2174 Broken D/Out Replaced x 3 & Crossarm Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: DTX TC2174 Broken D/Out Replaced x 3 & Crossarm SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
340 |  | JE25007293 | CAMBRIA SUB - KETEMARAE RD - 8800/2 | Western | KETEMARAE RD | 2025-03-05 | 9:48 | 2025-03-05 | 10:35 | 0.1003 | 0.0022044 | 799 | 36355 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | REGULATORY INFORMATION Voltage & Device ID: 11kV CB12 Protection flags (nil where none): O/C INVT A - B Ø CAUSE: Palm frong on lines Location: Pole 703556 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: F3 / F4 cursory patrolled Weather (wind/rain): Windy LFI (Y/N + Comments): No none installed Follow up Required (select advisory)? No Additional fault restoration comments: Palm frong fell onto lines then fell off, no damage to assets. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
341 |  | JE25007304 | KAI IWI SUB - WATERWORKS RD - 1026/2 | Western | WATERWORKS RD | 2025-03-05 | 10:25 | 2025-03-06 | 12:11 | 0.17054 | 0.00011036 | 40 | 61812 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: REC 1026 Protection flags (nil where none): C Phase EF CAUSE: Tree through the lines - tree was not part of the CAC site and was outside the zone, crew witnessed the tree fall from their worksite. Location: Pole 454485 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): windy LFI (Y/N + Comments): N Follow up Required (select advisory)? Additional fault restoration comments: Work was underway on CAC 119555-03 when Recloser tripped. Crew advised before tripping that a tree had split and fallen near their worksite and that they are standing clear to make sure it was safe to continue. They then watched the tree come over and bring down all three lines. CAC cancelled and waiting for Field Switcher to arrive in case they need help removing the trees. NDR to follow Trees are still falling and the forestry manager has said the site is unsafe to work at. Crews will return on the 2r when the wind dies down. Lines repaired and power restored | .
342 |  | JE25007315 | TP BRUNSWICK - PEAT ST 33KV - 1092 | Western | PEAT ST 33KV | 2025-03-05 | 11:14 | 2025-03-05 | 16:48 | 0.40686 | 0.018675 | 6769 | 147470 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: CB 1092 Protection flags (nil where none): C Phase EF CAUSE: broken 33kV crossarm on Pole with 11kV PST7 Location: Pole 706814 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: cursory Weather (wind/rain): windy LFI (Y/N + Comments): N/A Follow up Required (select advisory)? N Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): PST, KAI, CAC (ABR Restored) Circuit that tripped: BRK 1092 DTF (KM): N/A | .
343 |  | JE25007324 | 241 BAYLY ROAD, OKATO | Western | WAREA | 2025-03-05 | 13:20 | 2025-03-05 | 18:43 | 0.00089183 | 2.759e-06 | 1 | 323 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Cause: Lines Down Wind What was replaced? Where was it replaced (pole/TX/pillar box)? Is 2R required? Y 2R Y - What is the timeframe for repairs? Today Additional Info: Lines had part power when FM arrived on site as one line had flicked across insulator to the other side. FM has now de energized lines. Waiting on bucket truck. Line was isolated at Fuses 6475 to repair the lines down. | .
344 |  | JE25007337 | 42 TOKOMARU EAST ROAD,BRUNSWICK,WANGANUI | Western | BRUNSWICK | 2025-03-05 | 12:59 | 2025-03-05 | 15:05 | 0.0041717 | 3.3108e-05 | 12 | 1512 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: 986 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 15:04 Cause: WIND Weather (wind/rain): WIND Follow up required (select advisory)? | .
345 |  | JE25007339 | 22 RIMUTOTO BRANCH ROAD,OHANGAI,HAWERA | Western | WHAKAMARA | 2025-03-05 | 14:47 | 2025-03-05 | 16:15 | 0.00097686 | 1.1036e-05 | 4 | 354 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: WH289 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 16:15 Cause: DETERIORATION Weather (wind/rain): Follow up required (select advisory)? Fuses WH289 I&E due to insulator replacement at Pole 725742 | .
346 |  | JE25007342 | 484 LANDSDOWNE ROAD, WAHAROA | Eastern | PIAKOITI RD | 2025-03-05 | 14:10 | 2025-03-05 | 14:21 | 0.00011532 | 1.1036e-05 | 4 | 42 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: DTX TC4868 set on 10,750, 246, 248, 249V Loop tests completed: Test results: Voltage at TX: Voltage at house: Now on 11kV 242, 242, 241V Have all connections been checked? yes PQI Ref #: Additional Info: | .
347 |  | JE25007346 | 81 NORTH RANGE ROAD, AOKAUTERE, PALMERSTON NORTH, 4471 | Western | SUMMERHILL | 2025-03-05 | 15:20 | 2025-03-05 | 18:25 | 0.0020411 | 1.1036e-05 | 4 | 740 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolate DTX T2/695 for safety due to broken cross arm touching jumper Crew coming today to repair, Tom Childs leaving site Temp repairs made to restore customer but crew will defect the structure for a planned shutdown due to customer impact. | .
348 |  | JE25007370 | 2105 WIREMU ROAD,NEWALL,NEW PLYMOUTH | Western | PARIHAKA | 2025-03-05 | 15:08 | 2025-03-05 | 19:30 | 0.10558 | 0.00062077 | 225 | 38269 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV 12270/2 Protection flags (nil where none): A ph, E/F CAUSE: Broken Binder Location: 740398 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: operational Weather (wind/rain): Very windy LFI (Y/N + Comments): N Follow up Required (select advisory)? N Additional fault restoration comments: Feeder was sectionalised and Line was isolated at Links 12553/4 & ABS 6430 to replace the broken binder . | .
349 |  | JE25007373 | 657 WANGANUI ROAD,TURAKINA,MARTON | Western | TURAKINA | 2025-03-05 | 15:14 | 2025-03-05 | 16:47 | 0.016048 | 0.00017106 | 62 | 5817 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Broken HV Pin xarm which was rotten Pole 802408, replaced complete xarm | .
350 |  | JE25007374 | 351 WAITAO ROAD,WAITAO,TAURANGA | Eastern | BRUCE RD | 2025-03-05 | 15:09 | 2025-03-05 | 15:38 | 0.0010427 | 3.5867e-05 | 13 | 378 | Unplanned | WILDLIFE - BIRD | Fuses Location: SD5-066 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 15:38 Cause: BIRD Weather (wind/rain): FINE Follow up required (select advisory)? No lines down customer thought TX should have 3 wires and not two, but FM confirmed on 2 phase TX, No Issue | .
351 |  | JE25007378 | 1566 OLD COACH ROAD,PUKEHINA,TE PUKE | Eastern | ROTOEHU | 2025-03-05 | 15:33 | 2025-03-05 | 17:21 | 0.00029705 | 2.759e-06 | 1 | 108 | Unplanned | ADVERSE WEATHER - WIND-BLOWN DEBRIS (NOT TREES) | Fuses Location: SF7-060 No. Fuses: 3 Fuse Amp Size: 3A PLUS BARRELLS TIME CLOSED: 17:20 Cause: TREE BRANCH Weather (wind/rain): WIND Follow up required (select advisory)? CUSTOMER ADVISED ABOUT TREES | .
352 |  | JE25007397 | 140 PILOT STATION ROAD,PATEA,PATEA | Western | OTAUTU | 2025-03-05 | 18:11 | 2025-03-05 | 19:49 | 0.0051547 | 5.242e-05 | 19 | 1868 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faultman found lines down at pole 727032 due to deuteriation and wind, line was isolated at Fuses LI182 to repair the lines. 1 x 20 amp hv fuses was replaced at Fuses LI182. | .
353 |  | JE25007398 | 122 FENWICKS LINE,MORRISONS BUSH,GREYTOWN | Western | MOROA | 2025-03-05 | 17:27 | 2025-03-05 | 18:29 | 0.00051242 | 8.2769e-06 | 3 | 186 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: TX T959 No. Fuses: 3 Fuse Amp Size: 6A TIME CLOSED: 18:28 Cause: UNKNOWN Weather (wind/rain): RAIN Follow up required (select advisory)? | .
354 |  | JE25003024 | LINDERMANN RD | Eastern | LINDERMANN RD | 2025-03-04 | 8:56 | 2025-03-04 | 14:46 | 0.027991 | 8.001e-05 | 29 | 10146 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv/400vt cross arms @ 268253, 204532,204536,204539. Replace pole 11kv 204537. Isolation point @ SB1-047. | .
355 |  | JE25003033 | MATAKANA RD | Eastern | MATAKANA RD | 2025-03-04 | 9:00 | 2025-03-04 | 15:06 | 0.025225 | 6.8974e-05 | 25 | 9143 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace XArms 202067 & poles 202069, 202072, 202073, 202076 Self issue permit, no comms on Matakana island | .
356 |  | JE25003177 | EVERSHAM RD | Eastern | EVERSHAM RD | 2025-03-04 | 9:45 | 2025-03-04 | 15:50 | 0.13955 | 0.00039177 | 142 | 50580 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install new fully Automated CFC 15079 and new CFC 15069. Install new cable from SC5-174 to 15069-1 and from 15069-3 to 15079-1. Remove 185mm cable from TD5-218 feeding to SC5-180, cut and join to cable from new CFC 15079-3. Install new cable between 15079-2 to transformer TD5-218 and from 15069-2 to transformer TD5-217. | .
357 |  | JE25003768 | CLOTON RD NORTH | Western | CLOTON RD NORTH | 2025-03-04 | 9:06 | 2025-03-04 | 14:36 | 0.13204 | 0.00040005 | 145 | 47860 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace fuses 6320 & ABS 5558 with new fused ABS 5558 & replace HV pin arm. | .
358 |  | JE25003794 | RAETIHI | Western | RAETIHI | 2025-03-04 | 8:50 | 2025-03-04 | 15:46 | 0.022933 | 5.5179e-05 | 20 | 8312 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles & cross arms form pole 477585 ,777702, 477752, 777704,777705,851455,777708, 777709,777710,777711,777712 | .
359 |  | JE25003975 | VICTORY STREET | Eastern | VICTORY STREET | 2025-03-04 | 9:16 | 2025-03-04 | 11:54 | 0.057769 | 0.00036694 | 133 | 20939 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9324/1/2/3 | .
360 |  | JE25004275 | BENNETT ST | Eastern | BENNETT ST | 2025-03-04 | 9:31 | 2025-03-04 | 13:38 | 0.023895 | 9.6564e-05 | 35 | 8661 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Pole N0484 | .
361 |  | JE25004808 | COROGLEN | Eastern | COROGLEN | 2025-03-04 | 8:46 | 2025-03-04 | 15:30 | 0.0078143 | 1.9313e-05 | 7 | 2832 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace pole CGNTAI 201/202 | .
362 |  | JE25005106 | KAIMAI DRIVE | Eastern | KAIMAI DRIVE | 2025-03-04 | 8:31 | 2025-03-04 | 13:37 | 0.010997 | 3.5867e-05 | 13 | 3986 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Liven 3c 300mm HV cable from CFCF 15001/3 to CFC 15014/1. commission new new transformer TP4483: New RMU 15014 Liven new 4 c 185mm LV cable to pillars DP1, DP2, DP3, Remove HV leads from redundant Transformers TE3-195, TE3-194 & TE3-091 | .
363 |  | JE25005731 | PURIRI ST | Western | PURIRI ST | 2025-03-04 | 8:15 | 2025-03-04 | 12:30 | 0.32695 | 0.0012857 | 466 | 118505 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace/relocate Pole 765528 closer to customer boundary. Remove poles 452110, 453199, 453372 | .
364 |  | JE25006644 | JELLICOE ST | Eastern | JELLICOE ST | 2025-03-04 | 13:39 | 2025-03-04 | 15:37 | 0.043098 | 0.0003835 | 139 | 15621 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install replaced cable and reinstate cable breaks at poles 409508 & 222425. | .
365 |  | JE25007090 | unknown KUPARA ROAD,Ratapiko,Rural | Western | RATAPIKO | 2025-03-04 | 10:50 | 2025-03-04 | 11:46 | 0.00030395 | 5.5179e-06 | 2 | 110 | Unplanned | WILDLIFE - POSSUM | Fuses Location: 5337 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 11:45 Cause: Possum on transformer pole 4696T Weather (wind/rain): Calm Follow up required (select advisory)? Possum removed with hot stick, the pole had no possum guard. Line was patrolled and new guard installed. | .
366 |  | JE25007093 | TE PUKE SUB - MAONEKA ROAD - TE PUKE/4 | Eastern | MANOEKA RD | 2025-03-04 | 7:07 | 2025-03-04 | 8:47 | 0.11566 | 0.0022679 | 822 | 41923 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 4 Protection flags (nil where none): E/F C Phase CAUSE: Bird Standing on Lightning Arrestor Caused Flashover Location: Pole 223579 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: curse Weather (wind/rain): fine LFI (Y/N + Comments): yes ground mounted operated Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
367 |  | JE25007166 | 155 WHAKATOMOTOMO ROAD,PIRINOA,FEATHERSTON | Western | BURNSIDE | 2025-03-04 | 12:38 | 2025-03-04 | 14:39 | 0.0019958 | 1.6554e-05 | 6 | 723 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 7445 No. Fuses: 2 Fuse Amp Size: 10 AMP TIME CLOSED: 14:38 Cause: LIGHTNING Weather (wind/rain): RAIN Follow up required (select advisory)?N/A | .
368 |  | JE25007180 | unknown KAIPIKARI ROAD,Urenui,Rural | Western | MAIN RD MOTONUI | 2025-03-04 | 13:46 | 2025-03-04 | 14:59 | 0.00020149 | 2.759e-06 | 1 | 73 | Unplanned | WILDLIFE - BIRD | Fuses Location: TX 4830T No. Fuses: 2A Fuse Amp Size: 2 TIME CLOSED: 14:58 Cause: BIRD Weather (wind/rain): RAIN Follow up required (select advisory)? | .
369 |  | JE25007187 | 580 KAHUTARA ROAD,KAHUTARA,FEATHERSTON | Western | DAIRY FACTORY | 2025-03-04 | 15:38 | 2025-03-04 | 18:15 | 0.00043371 | 2.759e-06 | 1 | 157 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: Tfr T4549 CAUSE: Lightning Strike Temp generation (stage details when used): N PERFORMANCE DETAIL DNO (number or state no): N Circuit patrolled & type: operational Weather (wind/rain): Rain & lightning Follow up required (select advisory)? Additional fault restoration comments: Replace Tfr T4549 | .
370 |  | JE25007190 | 181 BACKWATER ROAD,MARTINBOROUGH,MARTINBOROUGH | Western | TAWAHA | 2025-03-04 | 14:19 | 2025-03-04 | 17:23 | 0.0010127 | 5.5179e-06 | 2 | 367 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: TX T975 No. Fuses: 3 Fuse Amp Size: 3A TIME CLOSED: 17:22 Cause: LIGHTNING Weather (wind/rain): RAIN Follow up required (select advisory)? | .
371 |  | JE25007192 | 180 LAKE FERRY ROAD,MARTINBOROUGH,MARTINBOROUGH | Western | DYERVILLE | 2025-03-04 | 14:24 | 2025-03-04 | 15:46 | 0.0013581 | 1.6554e-05 | 6 | 492 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 7334 No. Fuses: 2 Fuse Amp Size:10a TIME CLOSED: 15:45 Cause: Lightning Weather (wind/rain): rain Follow up required (select advisory)? Also TX T2434 REPLACED 2 2A fuses at 15:40 | .
372 |  | JE25007193 | 941 STATE HIGHWAY 53,TAUHERENIKAU,FEATHERSTON | Western | MOROA | 2025-03-04 | 14:24 | 2025-03-04 | 18:00 | 0.0023839 | 1.1036e-05 | 4 | 864 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: TX T960 No. Fuses: 2 Fuse Amp Size: 2A PLUS BARRELL TIME CLOSED: 18:00 Cause: LIGHTNING Weather (wind/rain): RAIN Follow up required (select advisory)? parent of JE25007671 correct tx linked through TX 960 | .
373 |  | JE25007212 | 543 KELLY ROAD, NEW PLYMOUTH, 4373 | Western | WAITARA RD | 2025-03-04 | 16:39 | 2025-03-04 | 21:13 | 0.032444 | 0.0003697 | 134 | 11759 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Line down found at pole 744961 Isolated at Fuses 8454 Line broke at the insulator on pole 744961, 2 span down & broken insulator Insulator & conductor replaced, full power restored | .
374 |  | JE25007218 | 4 KING EDWARD STREET,ELTHAM,ELTHAM | Western | ELTHAM EAST 33KV | 2025-03-04 | 17:09 | 2025-03-04 | 17:59 | 0.092896 | 0.0056255 | 2039 | 33671 | Unplanned | LIGHTNING - LIGHTNING STRIKE | REGULATORY INFORMATION Voltage & Device ID: 33kV CB 2782 Protection flags (nil where none): O/C INST CAUSE: Lightning Strike on or close to 33kV Lines Location: na Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op, Line patrolled, no fault found Weather (wind/rain): lightning LFI (Y/N + Comments): na Follow up Required (select advisory)? n Additional fault restoration comments: Lightning strike, CB 2782 tripped open, Cloton Rd Sub CB 392, 19, Eltham CB 403, 402, R08 & R09 also tripped open, TPWR restored feeder, full power restored to Cloton & Eltham Sub SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Eltham Circuit that tripped: 33kV CB 402 & 403 DTF (KM):na | .
375 |  | JE25007235 | 32 LEES PAKARAKA ROAD,TE ORE ORE,MASTERTON | Western | WERAITI | 2025-03-04 | 20:46 | 2025-03-04 | 21:22 | 0.0055007 | 0.00015174 | 55 | 1994 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | REGULATORY INFORMATION Voltage & Device ID: CB C830 Protection flags (nil where none): None CAUSE: Deterioration Location: Pole 827321 Temp generation (state details when used): None PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Rain LFI (Y/N + Comments): None Follow up Required (select advisory)? No Additional fault restoration comments: Broken jumper at Pole 827321. Isolated at ABS S101, REPAIRED JUMPER UNDER ACCESS PERMIT. Power off @ 20:45.Power restored at 21:21Hrs | .
376 |  | JE25007244 | unknown RAUPO ROAD,Rangiotu,Rural | Western | TAIKOREA | 2025-03-04 | 22:29 | 2025-03-05 | 4:06 | 0.19211 | 0.0018733 | 364 | 69632 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: Rec 10715/2 Protection flags (nil where none): E/F, O/C A CAUSE: Broken Insulator Location: Pole P16467 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): rain LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: line patrolled, Broken Insulator found at pole P16467, Isolated at ABS B13 & 10194, Broken insulator replaced, full power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
377 |  | JE25002102 | KAITEMAKO RD | Eastern | KAITEMAKO RD | 2025-03-03 | 8:45 | 2025-03-03 | 12:37 | 0.23877 | 0.0010291 | 373 | 86542 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - IP382/FP466/IP388/9309 | .
378 |  | JE25002988 | PUHUNGA ISLAND RD | Eastern | PUHUNGA ISLAND RD | 2025-03-03 | 9:03 | 2025-03-03 | 14:32 | 0.02088 | 6.3456e-05 | 23 | 7568 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles O742.O743. O744, O746, O747, O748, & O749. Replace crossarms on Pole 347499. | .
379 |  | JE25003017 | RANGITANUKU RD | Eastern | RANGITANUKU RD | 2025-03-03 | 9:15 | 2025-03-03 | 13:56 | 0.041019 | 0.00014623 | 53 | 14867 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv and 400v Xarms at Pole E1201 | .
380 |  | JE25003346 | MANGAMAIRE | Western | MANGAMAIRE | 2025-03-03 | 9:30 | 2025-03-03 | 15:14 | 0.036991 | 0.0001076 | 39 | 13408 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Change 11kV arms & poles between R47 & 10296 | .
381 |  | JE25003905 | HAU NUI 33KV | Western | HAU NUI 33KV | 2025-03-03 | 10:32 | 2025-03-03 | 11:18 | 0.00012857 | 2.759e-06 | 1 | 47 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Scada Test C971 SEL651R Relay | .
382 |  | JE25004664 | MANGAWEKA | Western | MANGAWEKA | 2025-03-03 | 9:18 | 2025-03-03 | 15:39 | 0.020985 | 5.5179e-05 | 20 | 7606 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Multiple poles & X-Arms between poles 810412 & 812162 install new links at pole 812176 | .
383 |  | JE25004888 | BRUCE RD | Eastern | BRUCE RD | 2025-03-03 | 9:46 | 2025-03-03 | 17:22 | 0.041603 | 9.1046e-05 | 33 | 15079 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Lower Lines between poles 393822 and 220184 for tree cutters Due to X arm failure while pulling lines back up, these have to be replaced new ETR 20:00 | .
384 |  | JE25006642 | MAIN ST 15 | Western | MAIN ST 15 | 2025-03-03 | 11:54 | 2025-03-03 | 12:12 | 5.1087e-05 | 2.759e-06 | 1 | 19 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 50A fuses with 80A fuses at RMU 10600/4 | .
385 |  | JE25006935 | 8766 SH 1,TAIHAPE,TAIHAPE | Western | MOAWHANGO | 2025-03-03 | 1:23 | 2025-03-03 | 3:12 | 0.0003007 | 2.759e-06 | 1 | 109 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Darren Morris - 0276599212 Replaced 2 x 50A HV Fuses Cause unknown Restored 03:11 | .
386 |  | JE25006982 | 601 HAOWHENUA PLACE,HAWERA,HAWERA | Western | CAMBRIA LS | 2025-03-03 | 9:33 | 2025-03-03 | 12:51 | 0.01307 | 6.6215e-05 | 24 | 4737 | Unplanned | OTHER | The contractor was concerned stringing 400V line past the live transformer C6033. Full isolation and earthing was done, work completed on the NAPA 119463 was completed. | .
387 |  | JE25007014 | 499 WAIHAKEKE ROAD,TAUMATA ISLAND,CARTERTON | Western | TAVERNER ST | 2025-03-03 | 12:39 | 2025-03-03 | 13:39 | 0.00016439 | 2.759e-06 | 1 | 60 | Unplanned | VEGETATION - OUTSIDE ZONE | Faultman reported that there is a branch that had fallen onto the lines, the line was isolated at Fuses 7550 to remove the branch. Job was between Fuses 7550 & Tfr T3073. | .
388 |  | JE25007047 | unknown CAMPBELL ROAD,Maata,Rural | Western | TE ROTI | 2025-03-03 | 15:01 | 2025-03-03 | 16:41 | 0.0099931 | 9.9323e-05 | 36 | 3622 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 6082 No. Fuses: 2 Fuse Amp Size: 20A TIME CLOSED: 16:41 Cause: Unknown lines patrolled Weather (wind/rain): Calm Follow up required (select advisory)? No | .
389 |  | JE25003355 | PONATAHI | Western | PONATAHI | 2025-03-02 | 9:01 | 2025-03-02 | 12:25 | 0.002816 | 1.3795e-05 | 5 | 1021 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles and hardware past fuses 7562 (poles 819147 and 819151 are red tagged) | .
390 |  | JE25004633 | WORKS | Western | WORKS | 2025-03-02 | 5:00 | 2025-03-02 | 16:13 | 0.090529 | 0.00037798 | 136 | 32813 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove 11kV Cable jumpers that come from RMU147 from the line at Pole P32371 and remove cable from the pole. Cut cable below termination at RMU 147 and cap off to decommission the cable between RMU 147 and Pole 32371. Connect new RMU140/141/FS59 at 10 Mahinui Street and remove old RMU140/141/FS59. Connect new 11kV Cable from new RMUFS59 to existing TX T3/254. Completed 2x 11kv Through Joints/transition Joints. extra outage on TFR T3/310 to correct rotation | .
391 |  | JE25006890 | 424 MOTUKAWA ROAD,TARATA,INGLEWOOD | Western | TARATA | 2025-03-02 | 6:38 | 2025-03-02 | 9:51 | 0.082324 | 0.00042764 | 155 | 29839 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | faultman was attending a part power fault, patrolling the line back, faultman found a line burning on the ground around Pole 762050, CB H41 had not tripped NOC Tripped CB H41 Isolated at ABS H43 & Links H42 No back feed points bad section of conductor removed, 30meters of conductor replaced Full power restored faultman inspected the broken ends of the conductor and could only find an old burn/clash mark at break point | .
392 |  | JE25006904 | 162B BANKS ROAD,MATAMATA,MATAMATA | Eastern | FIRTH ST | 2025-03-02 | 11:37 | 2025-03-02 | 11:49 | 6.41e-05 | 5.5179e-06 | 2 | 23 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Transformer TP1127 Overvoltage TAP 3 (before tapping) R-W 421V - 250V R-B 422V - 249V W-B 421V - 248V TAP 2 (after tapping down) R-W-408V- 240V R-B -407V - 231V W-B 407V - 230V | .
393 |  | JE25006916 | 1349 CAMERON ROAD,GATE PA,TAURANGA | Eastern | HYNDS RD | 2025-03-02 | 17:56 | 2025-03-04 | 11:26 | 0.54349 | 0.0051924 | 1383 | 196990 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 12, 14 18 Protection flags (nil where none): A B C OC CAUSE: Unknown Location: ABS SD4-572 Temp generation (state details when used): Transformer TD4 291 - 22:35 Transformer TD4 - 046 - 23:04 Transformer TP4182 - 23:43 PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): Fine LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Trapnspower Requested CB 18 Open as their relay was faulted and required a power cycle, CB 18 was open at 23:03 and closed at 23:14, as per request of transpower. Address Between 35 - 69 Hynds St Remain without power overnight as a electrical inpsector is required for relivening. ABS SD4-572 HV jumpers blown off and one Cable End blown Off. Line Break Created at Pole 858590 FRM Paul Cooper is aware of address's that need inspection Network Restored 05/03/25 Josh Reid | .
394 |  | JE25006928 | 30 TOPAZ DRIVE,PAPAMOA BEACH,TAURANGA | Eastern | PAPAMOA BEACH WEST | 2025-03-02 | 20:35 | 2025-03-03 | 0:47 | 0.051994 | 0.0005242 | 190 | 18846 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Faulted Cable Between Fuses SD5 - 085 and Transformer TD5 164 Permission Granted to install Generator Test Results Red Phase 2.15Gohms White Phase 10kohms Blue Phase 2.1 Gohms Fuses SD5 085 Left Open Removed and Tagged Generator Installed at 00:47 Sw/Gear 13098 lost its marbles on restoration. DNO Number 2503004 Dc to Dc convertor faulty - Parts to be orderd, End of the week Fix Generation will be on at this address for the next 2 x 3 weeks . Work will start in this area this week. Rodney has replaced dc to dc convertor, All Working Correctly | .
395 |  | JE25003764 | DAIRYFACT | Western | DAIRYFACT | 2025-03-01 | 17:04 | 2025-03-01 | 21:07 | 0.0070685 | 3.0349e-05 | 11 | 2562 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11KV ABS A88 & Xarms P43741 & take oil samples of all Goodman fielders Private equipment | .
396 |  | JE25005499 | POOLES RD | Eastern | POOLES RD | 2025-03-01 | 9:02 | 2025-03-01 | 11:16 | 0.0081021 | 6.0697e-05 | 22 | 2937 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace broken 11kv cable support x-arm at pole 215873 | .
397 |  | JE25006824 | 229A PAHIATUA MANGAHAO ROAD,MANGAMUTU,PAHIATUA | Western | MANGATAINOKA | 2025-03-01 | 8:15 | 2025-03-01 | 10:56 | 0.010615 | 6.6215e-05 | 24 | 3848 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Line down between Pole P18227 & P18228, faulty fargo sleeves Isolated at Fuses R15 Faulty fargo joint found, 50+ meters of conductor replaced, Re-loaded fuses R15, full power restored | .
398 |  | JE25006840 | 309 ALBERT ROAD,KORITO,NEW PLYMOUTH | Western | JUNCTION RD | 2025-03-01 | 9:37 | 2025-03-01 | 13:29 | 0.0063962 | 2.759e-05 | 10 | 2318 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Car V pole 752042, Broken pole, pole on its side at ground level and still live as no live conductor - ground contact Isolated at Fuses 8296 Pole replaced, Full power restored | .
399 |  | JE25006846 | sub_ELT | Western | TE ROTI | 2025-03-01 | 9:52 | 2025-03-01 | 12:16 | 0.092049 | 0.00092701 | 336 | 33363 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV CB R61 Protection flags (nil where none): E/F CAUSE: Unknown Location: na Temp generation (state details when used): na PERFORMANCE DETAIL DNO (number or state No): na Circuit patrolled and type: op Weather (wind/rain): calm LFI (Y/N + Comments): y LFI at Pole 733919 indicated Follow up Required (select advisory)? n Additional fault restoration comments: Line patrolled, no fault found, unable to put remote back feed in place as Sec 12281/2 is not commissioned SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
400 |  | JE25006850 | 267 CAMERON ROAD, MANGATEPARU, MORRINSVILLE, 3375 | Eastern | MVILLE NORTH | 2025-03-01 | 13:47 | 2025-03-01 | 15:04 | 0.015921 | 0.00023727 | 86 | 5771 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faultman Required - Recloser 9320 Faulty needs to be jumperd Across Contact Control Before Attending. Recloser 9320/2 Bypassed, Links 9320/6 Open removed and tagged. DNO 2503003 | .
401 |  | JE25006851 | 206 Mill Road, Rongotea | Western | KOPANE | 2025-03-01 | 12:30 | 2025-03-01 | 12:51 | 0.00034046 | 1.6554e-05 | 6 | 123 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Broken LV insulators on TFR T1/65 Structure (Pole P20838) due to bad design of structure HV was required to be de-energised De-energised TFR T1/65 LV insulators where replaced Full power restored | .
402 |  | JE25006853 | SCHOOL ROAD, MATAKANA ISLAND | Eastern | MATAKANA RD | 2025-03-01 | 13:47 | 2025-03-01 | 14:41 | 0.0037005 | 6.8974e-05 | 25 | 1341 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faulty DDO Lead at Transformer TC3008 - Has Been Repaired 2 R for the fairy and materials | .
403 |  | JE25000774 | DYERVILLE | Western | DYERVILLE | 2025-02-28 | 9:06 | 2025-02-28 | 12:52 | 0.058603 | 0.00025934 | 94 | 21241 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove ABS S507, install new automated Entec Switch S507/2 configured as a sectionaliser & links S507/4 on pole 810643. | .
404 |  | JE25001230 | MANGAWEKA | Western | MANGAWEKA | 2025-02-28 | 9:15 | 2025-02-28 | 15:41 | 0.021278 | 5.5179e-05 | 20 | 7712 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace multiple poles & x-arms between poles 810412 & 812118 | .
405 |  | JE25001363 | CLOTON RD CENTRAL | Western | CLOTON RD CENTRAL | 2025-02-28 | 9:00 | 2025-02-28 | 13:50 | 0.069201 | 0.00024831 | 90 | 25082 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | DNO 2412016 at switchgear 12170 with low SF6. Outage to replace unit. | .
406 |  | JE25002247 | MANGATOKI | Western | MANGATOKI | 2025-02-28 | 8:30 | 2025-02-28 | 14:23 | 0.013575 | 3.8625e-05 | 14 | 4920 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Entec 12281/2 Remove 12281 /6 links Sectionaliser installed, still to be comissioned | .
407 |  | JE25002298 | KAIMAI DRIVE | Eastern | KAIMAI DRIVE | 2025-02-28 | 8:56 | 2025-02-28 | 13:43 | 0.029269 | 0.00010208 | 37 | 10609 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv overhead conductors between poles 211660 &211666 with AAAC Iodine | .
408 |  | JE25006424 | COROGLEN | Eastern | COROGLEN | 2025-02-28 | 10:00 | 2025-02-28 | 11:37 | 0.00053165 | 5.5179e-06 | 2 | 193 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Access Permit to change Transformer TC2589 | .
409 |  | JE25006797 | 405 RONGOTEA ROAD,RONGOTEA,PALMERSTON NORTH | Western | RONGOTEA | 2025-02-28 | 15:19 | 2025-02-28 | 16:45 | 0.00023605 | 2.759e-06 | 1 | 86 | Unplanned | WILDLIFE - BIRD | Fuses Location: 047 No. Fuses: 2 Fuse Amp Size: 3Amp TIME CLOSED: 16:45 Pm Cause: Possible Bird strike Weather (wind/rain): Calm Follow up required (select advisory)? Power restored | .
410 |  | JE25000879 | BOWENTOWN | Eastern | BOWENTOWN | 2025-02-27 | 9:21 | 2025-02-27 | 15:08 | 0.021071 | 6.0697e-05 | 22 | 7637 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace hardware at various locations past Fuses SA2-011 | .
411 |  | JE25001101 | MATAKANA RD | Eastern | MATAKANA RD | 2025-02-27 | 9:00 | 2025-02-27 | 14:45 | 0.023783 | 6.8974e-05 | 25 | 8620 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 202059 to 202063, 202066, 202068 | .
412 |  | JE25001148 | LOMOND AVE | Eastern | LOMOND AVE | 2025-02-27 | 23:31 | 2025-02-28 | 2:30 | 0.044023 | 0.00024555 | 89 | 15956 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - IC1577/SW5025/IC1583 | .
413 |  | JE25001200 | WEST ST | Western | WEST ST | 2025-02-27 | 8:31 | 2025-02-27 | 13:00 | 0.058671 | 0.00021796 | 79 | 21265 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles and hardware past T2042 | .
414 |  | JE25001371 | RAETIHI | Western | RAETIHI | 2025-02-27 | 8:45 | 2025-02-27 | 13:55 | 0.017118 | 5.5179e-05 | 20 | 6205 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles & cross arms from pole 777682,851454,777686,942982, 777688, 777689,777691, 777692,777693,777694 | .
415 |  | JE25002004 | TREMAINE AVE | Western | TREMAINE AVE | 2025-02-27 | 9:00 | 2025-02-27 | 16:42 | 5.8398e-06 | 5.5179e-06 | 1 | 2 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 33KV pole install new recloser 10950 remove ABS A21 | .
416 |  | JE25002905 | KAIMAI DRIVE | Eastern | KAIMAI DRIVE | 2025-02-27 | 8:36 | 2025-02-27 | 12:59 | 0.00072791 | 2.759e-06 | 1 | 264 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Liven 3c 300mm HV cable from CFCF 15028 to CFC 15014. Liven new 3 c 185mm HV cable to new 11/100/3 G/M transformer TP4490: Liven new 4 c 185mm LV cable to pillars DP7, DP6, DP5, DP4. Relocate G/M transformer TE3-150 HV cable end from fuses SE3-045 to CFCF 15028/4. Commission RMUs | .
417 |  | JE25003604 | PARAPARA | Western | PARAPARA | 2025-02-27 | 9:18 | 2025-02-27 | 14:43 | 0.014352 | 4.4143e-05 | 16 | 5202 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace red tag pole 785225 using digger. | .
418 |  | JE25004317 | HIKUAI | Eastern | HIKUAI | 2025-02-27 | 9:30 | 2025-02-27 | 15:01 | 0.02006 | 6.0697e-05 | 22 | 7271 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT to replace xarms hardware and reconfigure at structures: 323181/323408 and 383178/383179 | .
419 |  | JE25006337 | 177 JOHNSON ROAD, TE PUKE | Eastern | ROTOEHU | 2025-02-27 | 10:36 | 2025-02-27 | 12:17 | 0.00083541 | 8.2769e-06 | 3 | 303 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FM advised he was unable to gain access due to locked gates and pole is further into a Forestry Block that has a sign saying a permit is required to gain entry. Will look to do work under 2R. 27/02/25 Fault repaired , Dead Ends Replaced , line resagged, Old Short Dead Ends the cause. | .
420 |  | JE25006563 | TP MASTERTON - GLADSTONE 33kV - GLADSTONE/3267 | Western | GLADSTONE 33KV | 2025-02-27 | 6:48 | 2025-02-27 | 8:01 | 0.13129 | 0.0019423 | 704 | 47585 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: CB 3267 Protection flags (nil where none): C phase INST OC CAUSE: magpie on transformer bushing Location: T1 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): fine LFI (Y/N + Comments): N Follow up Required (select advisory)? Additional fault restoration comments: Gas sample sent for testing as a precaution SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): GLA Sub Circuit that tripped: CB 3267 DTF (KM): | .
421 |  | JE25006567 | 15 HENRY ROAD,KATIKATI,KATIKATI | Eastern | WHARAWHARA ROAD | 2025-02-27 | 10:40 | 2025-02-27 | 21:41 | 0.027359 | 4.1384e-05 | 15 | 9916 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 11kV Cable Fault Between FABS IP652 & TD4-094. Awaiting for Generator to be Connected. 11kV generation connected at 21:40 27/02/25 DNO 2502018 | .
422 |  | JE25006692 | 89 BREAKWATER ROAD,MOTUROA,NEW PLYMOUTH | Western | OMATA RD | 2025-02-27 | 16:57 | 2025-02-27 | 19:04 | 0.10407 | 0.004453 | 1614 | 37720 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 8 Protection flags (nil where none): C Ph E/F CAUSE: Bird Strike Location: Pole 750479 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Y active at Sw/Gear 12620 Follow up Required (select advisory)? Additional fault restoration comments: Sw/Gear 12620/1 Opened, Power restored up to Sw/Gear Lines down reported, Isolated at Fuses 8242 Livened up to Fuses 8242 Cause Bird strike, lines caused grass fire Lines repaired SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
423 |  | JE25000561 | REVANS ST | Western | REVANS ST | 2025-02-26 | 9:01 | 2025-02-26 | 15:15 | 0.066014 | 0.00017657 | 64 | 23927 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV arms between poles 798600 & 798399 | .
424 |  | JE25006418 | unknown unknown ,Mangaweka,Rural | Western | MANGAWEKA | 2025-02-26 | 4:49 | 2025-02-26 | 16:05 | 0.15927 | 0.00066767 | 242 | 57729 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV Recloser Tripped Protection flags (nil where none): a Ph E/F CAUSE: Truck V Pole Location: 808384 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Isolated at Links 950 & ABS 964 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
425 |  | JE25006482 | 162 HINUERA ROAD,MATAMATA,MATAMATA | Eastern | SMITH ST | 2025-02-26 | 11:45 | 2025-02-26 | 14:18 | 0.00084351 | 5.5179e-06 | 2 | 306 | Unplanned | VEGETATION - INSIDE ZONE | FENZ Advised attending due to lines down causing vegetation fire, ETA required #F4157710 - Called SMC and advised eta given of 10mins HV Lines down brought down by branch falling on lines Lines Live on ground (Fuses didn't blow) Isolated at Fuses FC4091 Branch cleared, Cross arm replaced Lines repaired | .
426 |  | JE25006534 | unknown MCINTOSH ROAD,Pongakawa,Rural | Eastern | TAINUI | 2025-02-26 | 16:58 | 2025-02-26 | 19:27 | 0.0024578 | 1.6554e-05 | 6 | 891 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: SE7-053 No. Fuses: 2 Fuse Amp Size: 15AMP TIME CLOSED: 19:26 Cause: Unknown Cause suspect bird strike Weather (wind/rain): Calm Follow up required (select advisory)? N/A Power Restored | .
427 |  | JE25000857 | LINDERMANN RD | Eastern | LINDERMANN RD | 2025-02-25 | 8:53 | 2025-02-25 | 14:50 | 0.0649 | 0.00018209 | 66 | 23524 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv/400vt cross arms @204626,204630 Replace pole 204629 & 204631. Isolation point @ SB1-002 | .
428 |  | JE25000858 | MCCABE ROAD | Eastern | MCCABE ROAD | 2025-02-25 | 9:31 | 2025-02-25 | 14:55 | 0.0206 | 6.3456e-05 | 23 | 7467 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Poles and arms at various sites | .
429 |  | JE25000880 | MATAKANA RD | Eastern | MATAKANA RD | 2025-02-25 | 9:01 | 2025-02-25 | 15:00 | 0.038716 | 0.0001076 | 39 | 14033 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 202042, 202044 ( TC3-077); 202047, 202050, 202053, 202054, 202056 | .
430 |  | JE25001098 | STANLEY AVE | Eastern | STANLEY AVE | 2025-02-25 | 23:30 | 2025-02-26 | 1:52 | 0.046202 | 0.00032556 | 118 | 16746 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - IC1415-IC1403-FC712 | .
431 |  | JE25001199 | WEST ST | Western | WEST ST | 2025-02-25 | 8:30 | 2025-02-25 | 13:12 | 0.061406 | 0.00021796 | 79 | 22257 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles and hardware past T2042 | .
432 |  | JE25001276 | RAETIHI | Western | RAETIHI | 2025-02-25 | 8:58 | 2025-02-25 | 15:50 | 0.022732 | 5.5179e-05 | 20 | 8239 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles & cross-arms from pole 941422 , 777669, 777670, 777671,777672,777673,851453,777677,777681 | .
433 |  | JE25002460 | NGAERE | Western | NGAERE | 2025-02-25 | 9:16 | 2025-02-25 | 14:09 | 0.0016188 | 5.5179e-06 | 2 | 587 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | ELE020871. Eltham Sub 4 pole structure systematic undergrounding. This NAPA is to do R31. Remove conductors from ABS 12547 back to ABS 6105. Install & connect new 11kV cable from CB R31 to ABS 12547 via new switchgear 12829. Feeders to be done one at a time in following sequence. Shut 1. R11 completed first on NAPA 117483. Shut 2. R61 completed next on NAPA 117485. Shut 3. R31 on this NAPA (117486). Shut 4. R51 last on NAPA 117487. | .
434 |  | JE25003967 | BALMORAL DR | Eastern | BALMORAL DR | 2025-02-25 | 9:53 | 2025-02-25 | 14:59 | 0.021126 | 6.8974e-05 | 25 | 7657 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Red Defect - Replace TC563 with new 100kva Pad Mount | .
435 |  | JE25005425 | BURETA RD | Eastern | BURETA RD | 2025-02-25 | 9:19 | 2025-02-25 | 14:28 | 0.026495 | 8.5528e-05 | 31 | 9603 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace damaged TX TC4-019, 200KVA | .
436 |  | JE25006257 | 450 WANGANUI ROAD,MARTON,MARTON | Western | TURAKINA | 2025-02-25 | 6:52 | 2025-02-25 | 10:46 | 0.003231 | 1.3795e-05 | 5 | 1171 | Unplanned | WILDLIFE - BIRD | Fuses Location: 1362 No. Fuses: 3 Fuse Amp Size: 3A TIME CLOSED: 10:45 Cause: Bird strike Weather (wind/rain): Fine Follow up required (select advisory)? Full power restored | .
437 |  | JE25006389 | sub_ATU | Eastern | TE PUKE NORTH | 2025-02-25 | 15:55 | 2025-02-26 | 17:50 | 0.025529 | 0.00051869 | 101 | 9253 | Unplanned | THIRD PARTY INTERFERENCE - DIG IN | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 4 Protection flags (nil where none): Neut O/C E/F B - C Ø CAUSE: Digger dug up Cable from Sw/G 15020/3 East Pack Location: Sw/G 15020/3 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F1 /F3 cursory patrolled Weather (wind/rain): Calm LFI (Y/N + Comments): Yes 14296 /1 /3 Follow up Required (select advisory)? Additional fault restoration comments: Cable repaired by Northpower Nothing found wrong with DTX TP4477 relivened all o.k NDR to follow SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
438 |  | JE25006402 | Check if related JE25006399 , JE25006401 1551 PACK SPUR ROAD,MATAIKONA,MASTERTON | Western | CASTLEPOINT | 2025-02-25 | 17:16 | 2025-02-25 | 18:58 | 0.019101 | 0.00018761 | 68 | 6923 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: Fuses 7366 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 18:57 Cause: Line Clash Weather (wind/rain): Windy Follow up required (select advisory)? No | .
439 |  | JE25006409 | recloser_9464:2 | Eastern | AWAITI | 2025-02-25 | 20:56 | 2025-02-25 | 23:17 | 0.028765 | 0.0002759 | 100 | 10426 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: Recloser 9464 Protection flags (nil where none): Phase B OC CAUSE: Unknown Location: Unknown Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Line patrolled, sectionalised, Restored, Nothing Found SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): N/A Circuit that tripped: N/A DTF (KM):N/A | .
440 |  | JE25000757 | PYES PA | Eastern | PYES PA | 2025-02-24 | 9:00 | 2025-02-24 | 11:46 | 0.00091303 | 5.5179e-06 | 2 | 331 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace TX TE3-145 | .
441 |  | JE25000807 | MOWBRAY RD | Eastern | MOWBRAY RD | 2025-02-24 | 23:31 | 2025-02-25 | 3:01 | 0.060922 | 0.00028969 | 105 | 22082 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9355-1/2/3 | .
442 |  | JE25001130 | MANGAWEKA | Western | MANGAWEKA | 2025-02-24 | 9:09 | 2025-02-24 | 15:05 | 0.019659 | 5.5179e-05 | 20 | 7126 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace multiple poles & x-arms between poles 810412 & 812162 | .
443 |  | JE25002689 | WERAITI | Western | WERAITI | 2025-02-24 | 9:46 | 2025-02-24 | 14:13 | 0.010313 | 3.8625e-05 | 14 | 3738 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re sag 11kv lines between Gladstone sub and S369 | .
444 |  | JE25005752 | DUKE ST | Eastern | DUKE ST | 2025-02-24 | 17:31 | 2025-02-24 | 17:39 | 0.00086245 | 9.9323e-05 | 36 | 313 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To repair HV cable fault between 9547/2 and TC3223 | .
445 |  | JE25005861 | OPOUTERE | Eastern | OPOUTERE | 2025-02-24 | 9:48 | 2025-02-24 | 11:14 | 0.00094669 | 1.1036e-05 | 4 | 343 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove fishing line from overhead 11kv span near R0942 by dropping then reinstating 11kv conductor | .
446 |  | JE25006083 | 413B BUSBY ROAD,TAHAWAI,unknown | Eastern | LINDERMANN RD | 2025-02-24 | 2:17 | 2025-02-24 | 3:32 | 0.020235 | 0.00027314 | 99 | 7334 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: SB1 - 072 Fuses where faulty and required to be replaced, isolated furhter out and replace all 3 fuse carriers | .
447 |  | JE25006171 | unknown SH 3 ,Waverley,Waverley | Western | WAITOTARA | 2025-02-24 | 12:51 | 2025-02-24 | 14:48 | 0.00097167 | 8.2769e-06 | 3 | 352 | Unplanned | WILDLIFE - BIRD | Fuses Location: 4105 No. Fuses: 2 Fuse Amp Size: 8 TIME CLOSED: 14:48 Cause: Bird strike ( Goose) Weather (wind/rain): calm Follow up required (select advisory)? | .
448 |  | JE25006178 | 172 OMANAWA ROAD,OMANAWA,TAURANGA | Eastern | KAIMAI DRIVE | 2025-02-24 | 12:53 | 2025-02-24 | 13:50 | 0.0012368 | 2.2072e-05 | 8 | 448 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Broken cross arm on pole 211710, this is under the trustpower 33kV CB 3242 a Temp line break was made at pole 211705 as there are no connected transformers and ICPs past 211705. Complete under a planned job | .
449 |  | JE25006237 | 26 COBHAM CRESCENT,TOKOROA,TOKOROA | Eastern | DUKE ST | 2025-02-24 | 17:50 | 2025-02-24 | 19:06 | 0.0075187 | 9.9323e-05 | 36 | 2725 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Blown fuse at Fuse/Sw 9547/2 replaced | .
450 |  | JE25006240 | 3 RIVERBANK ROAD, WANGANUI EAST, WANGANUI, 4573 | Western | KIWI ST | 2025-02-24 | 19:16 | 2025-02-24 | 20:52 | 0.01614 | 0.0001683 | 61 | 5850 | Unplanned | VEGETATION - OUTSIDE ZONE | Reports of Trees on the lines, CB 9 did not trip or display and flags Faultman found trees on lines around Pole 790661 Isolated at ABS 039 & 1108 Trees cut away from lines, no damage to lines, full power restored | .
451 |  | JE25006037 | 53 ROTOKOHU ROAD,PAEROA,PAEROA | Eastern | TIROHIA-KARANGAHAKE | 2025-02-23 | 5:26 | 2025-02-23 | 11:50 | 0.068385 | 0.00037798 | 137 | 24787 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: CB 3 Protection flags (nil where none): OC B & C Phase CAUSE: Car vs Pole Location: Pole 416211 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): Yes, Pole 876695 Follow up Required (select advisory)? No Additional fault restoration comments: Auto backfeed system worked okay keeping more than half the circuit back fed. Isolated at ABSs IC505 & 547. Pole replaced under ACCESS PERMIT. Power restored @ 11:50Hrs Some LV circuits deleyed to be restored until tested by inspectors due to a possible HV/LV line clashi SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): No Circuit that tripped: N/A DTF (KM):N/A | .
452 |  | JE25006043 | 5 TUNA ROAD,MIDHIRST,STRATFORD | Western | CLOTON RD SOUTH | 2025-02-23 | 7:15 | 2025-02-23 | 8:29 | 0.0026421 | 3.5867e-05 | 13 | 958 | Unplanned | WILDLIFE - BIRD | Fuses Location: 5552 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 08:28 Cause: Bird strike Weather (wind/rain): calm Follow up required (select advisory)? | .
453 |  | JE25006062 | FEEDER FAULT 33KV HUIRANGI - MOTUKAWA ABS 153 | Western | MAMAKU RD NO 1 33KV | 2025-02-23 | 12:54 | 2025-02-23 | 14:24 | 0.045923 | 0.0030983 | 1123 | 16645 | Unplanned | THIRD PARTY INTERFERENCE - OTHER | REGULATORY INFORMATION Voltage & Device ID: 33kV CB 1292 Protection flags (nil where none): Intertrip CAUSE: Balloons in 33kV lines Location: pole 760791 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: Operational Weather (wind/rain): calm LFI (Y/N + Comments): Y - poles 754726, 760783,760621 & 760322 Follow up Required (select advisory)? N Additional fault restoration comments: Faultman removed balloons from lines with hot line sticks, supply restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): McKee & Mangahewa & Motukawa Gen. Circuit that tripped: 33kV Mamaku Rd No.1 DTF (KM):n/a | .
454 |  | JE25006068 | FEEDER FAULT - BAIRD ROAD - PAPANAI - REC 13024 | Eastern | PAPANUI ST | 2025-02-23 | 14:11 | 2025-02-23 | 19:39 | 0.028007 | 0.00038901 | 141 | 10151 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: Recloser 13024/2 Protection flags (nil where none): OC Phase B & C CAUSE: Tractor Versus Pole Location: Pole Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Permit area isolated at ABSs 2634 & 2621. Pole and replaced and full power restored @ SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): No Circuit that tripped: N/A DTF (KM):N/A | .
455 |  | JE25006070 | 48 HOLLIS ROAD,WAIKINO,WAIHI | Eastern | OLD TAURANGA RD | 2025-02-23 | 14:40 | 2025-02-23 | 16:15 | 0.0028856 | 3.0349e-05 | 11 | 1046 | Unplanned | THIRD PARTY INTERFERENCE - TREES | Fuses Location: Transformer TC4394 No. Fuses: 2 Fuses Carrier Fuse Amp Size: TIME CLOSED: 16:15 Cause: Tree cutters, branches in the lines Weather (wind/rain): Calm Follow up required (select advisory)?No | .
456 |  | JE25006081 | 56 GORDON STREET,LANSDOWNE,MASTERTON | Western | GORDON ST | 2025-02-23 | 21:09 | 2025-02-24 | 1:41 | 0.10348 | 0.00038074 | 138 | 37508 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Car took pole out cleanily, and it resit, was safe and did not pose a risk to public line isolated and pole replaced, No Trippings on feeder. Pole 850532 Isolated at ABS S136 | .
457 |  | JE25006085 | 2980 TAUPO ROAD,TOKOROA,TOKOROA | Eastern | OLD CAMBRIDGE RD | 2025-02-23 | 23:38 | 2025-02-24 | 1:52 | 0.016183 | 0.00012139 | 44 | 5866 | Unplanned | WILDLIFE - POSSUM | REGULATORY INFORMATION Voltage & Device ID: 11kV Recloser 14843 Protection flags (nil where none): EF CAUSE: Possum at Pole A0204 Location: Pole A0204 Temp generation (state details when used): NIL PERFORMANCE DETAIL DNO (number or state No): NIL Circuit patrolled and type: Cursoary Weather (wind/rain): Fine LFI (Y/N + Comments): NIL Follow up Required (select advisory)? NIL Additional fault restoration comments: Possum Centre Phase | .
458 |  | JE25002077 | FACTORY RD | Eastern | FACTORY RD | 2025-02-22 | 8:31 | 2025-02-22 | 11:46 | 0.0010784 | 5.5179e-06 | 2 | 391 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - FC907-FC914 | .
459 |  | JE25005967 | 130 CANAL WEST ROAD,WAITAKARURU,THAMES | Eastern | MANGATARATA | 2025-02-22 | 3:57 | 2025-02-22 | 6:05 | 0.04014 | 0.00035039 | 127 | 14549 | Unplanned | WILDLIFE - POSSUM | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 13066 Protection flags (nil where none): E/F CAUSE: Oppossum Pole 02748 Location: Oppossum Pole 02748 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Curse Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
460 |  | JE25006003 | 8140 STATE HIGHWAY 27,MATAMATA,MATAMATA | Eastern | BUCKLAND RD | 2025-02-22 | 10:42 | 2025-02-22 | 15:33 | 0.0003523 | 5.5179e-06 | 1 | 128 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuse blown at Fuses FP1067 and two Lightning arrestors blown Work to be done under JE25005999 (Charlie Sahota) Reload re liven done. Lightning arrestors by by-passed. To be replaced later in the day once delivered to site Fuses Location: Fuses FP1067 No. Fuses: 1 Fuse Amp Size: 6A TIME CLOSED: 11:09 Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)? Yes - To isolate again and replace Lightning arrestors Isolated at Fuses FP1067 again at 13:53 for AP. Replaced 3 X lightning arrestors. Power restored 15:33 | .
461 |  | JE25006014 | unknown MOUNTAIN ROAD,Midhirst,Rural | Western | CLOTON RD NORTH | 2025-02-22 | 14:41 | 2025-02-22 | 16:31 | 0.00030358 | 2.759e-06 | 1 | 110 | Unplanned | WILDLIFE - BIRD | Fuses Location: 6225 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 16:30 Cause: bird strike Weather (wind/rain): calm Follow up required (select advisory)?n | .
462 |  | JE25006020 | 405 NEAVESVILLE ROAD, PURIRI, THAMES, 3578 | Eastern | BENNETT ST | 2025-02-22 | 17:15 | 2025-02-22 | 19:16 | 0.0063184 | 5.242e-05 | 19 | 2290 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Spragged Conductor at pole 481862- Repairs Made | .
463 |  | JE25000410 | LEPPERTON | Western | LEPPERTON | 2025-02-21 | 9:36 | 2025-02-21 | 14:56 | 0.01326 | 4.1384e-05 | 15 | 4806 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To Replace multiple x- arms in between poles 746712 - 746723 | .
464 |  | JE25000762 | KAIMAI DRIVE | Eastern | KAIMAI DRIVE | 2025-02-21 | 8:46 | 2025-02-21 | 13:37 | 0.029738 | 0.00010208 | 37 | 10779 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles 211666 &, 211669 | .
465 |  | JE25001113 | MANGAWEKA | Western | MANGAWEKA | 2025-02-21 | 9:03 | 2025-02-21 | 15:40 | 0.021929 | 5.5179e-05 | 20 | 7948 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace multiple poles & x-arms between poles 810412 & 812162 | .
466 |  | JE25001567 | CASTLEPOINT | Western | CASTLEPOINT | 2025-02-21 | 9:05 | 2025-02-21 | 14:38 | 0.042239 | 0.00012691 | 46 | 15310 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace defected 11kv cross arms at pole 838741 | .
467 |  | JE25001896 | PUHUNGA ISLAND RD | Eastern | PUHUNGA ISLAND RD | 2025-02-21 | 9:00 | 2025-02-21 | 14:19 | 0.052825 | 0.00016554 | 60 | 19147 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Pole 0303. Replace crossarms and hardware O13808, O300, O301, O302, O304, O305, O306, O307, O310, O12401, O312, O14185, O314 and O315. | .
468 |  | JE25004447 | STONEY CREEK | Western | STONEY CREEK | 2025-02-21 | 10:01 | 2025-02-21 | 13:35 | 0.023114 | 0.0001076 | 39 | 8378 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE FAULTY 11KV CABLE BETWEEN POLES P39337 & P39336 (DNO 2410004) | .
469 |  | JE25005839 | 279 KAHUTARA ROAD,KAHUTARA,FEATHERSTON | Western | DAIRY FACTORY | 2025-02-21 | 5:11 | 2025-02-21 | 7:35 | 0.00039846 | 2.759e-06 | 1 | 144 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 7245 No. Fuses: 2 Fuse Amp Size: 10Amp TIME CLOSED: 07:35 Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)?N/A | .
470 |  | JE25005946 | 3 KAWAKAWA STREET,MANGAWEKA,MANGAWEKA | Western | MANGAWEKA | 2025-02-21 | 17:21 | 2025-02-21 | 19:45 | 0.004784 | 3.3108e-05 | 12 | 1734 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | . | .
471 |  | JE25005964 | 814 KAUANGAROA ROAD,FORDELL,WANGANUI | Western | FORDELL | 2025-02-21 | 23:21 | 2025-02-22 | 12:39 | 0.037466 | 4.6902e-05 | 17 | 13580 | Unplanned | VEGETATION - OUTSIDE ZONE | Fuses Location: 544 No. Fuses: 3 Fuse Amp Size: TIME CLOSED: Cause: Large tree branch as broken and bought down LV & HV lines Weather (wind/rain): Windy / Light Rain Follow up required (select advisory)? Additional Info: Isolated overnight via Fuses 544. Crew to return tomorrow morning to make repairs 22/02/25 - Tree cleared and lines repaired, full power restored, HV / LV clash, affected customers off TFR X581 have had there meters inspected Customer requested service fuses at Pole 791645 to old farm shed at 814 Kauangaroa Rd be left removed with Tag (Tag No A43388) as Private LV line and hardware are in bad shape and customer is going to have the meter removed. | .
472 |  | JE25000420 | HUIROA | Western | HUIROA | 2025-02-20 | 8:15 | 2025-02-20 | 16:19 | 0.054715 | 0.00011312 | 41 | 19832 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Asplundh to cut trees between poles 709351 to 709355 | .
473 |  | JE25000469 | TUTAENUI | Western | TUTAENUI | 2025-02-20 | 9:15 | 2025-02-20 | 15:26 | 0.012268 | 3.3108e-05 | 12 | 4447 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace three poles 794575, 794569, 794571, replace X arms on pole 794572 | .
474 |  | JE25000734 | MURAL TOWN | Eastern | MURAL TOWN | 2025-02-20 | 23:30 | 2025-02-21 | 3:25 | 0.13149 | 0.00056007 | 203 | 47658 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - SB2-130/SB2-132/SB2-136/SB2-134 | .
475 |  | JE25000925 | STONEY CREEK | Western | STONEY CREEK | 2025-02-20 | 9:04 | 2025-02-20 | 13:53 | 0.13305 | 0.00046075 | 167 | 48224 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Combined works. Northpower work. Pole P42843 Replacing Xarms & ABS E63 Downer work. Replace 11kV ABS E15 & replace 11kV TX pole P41791 and install old Tx T2/875 | .
476 |  | JE25001042 | WEST ST | Western | WEST ST | 2025-02-20 | 8:45 | 2025-02-20 | 13:37 | 0.041037 | 0.00014071 | 51 | 14874 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re conductor 11kv line between pole 818222 and Transformer T4040 | .
477 |  | JE25001581 | MAIN RD MOTONUI | Western | MAIN RD MOTONUI | 2025-02-20 | 8:45 | 2025-02-20 | 13:42 | 0.11789 | 0.00039729 | 144 | 42730 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 11kv wire upgrade from pole 743062 to 370836 & pole 743063 to 743069 | .
478 |  | JE25001678 | HIKUAI | Eastern | HIKUAI | 2025-02-20 | 8:55 | 2025-02-20 | 14:26 | 0.013667 | 4.1384e-05 | 15 | 4954 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | PQI - Install new 50kVA transformer TP4486 on new intermediate pole between poles R0741 & R0740. Replace 11kV pole R0741 & LV poles 877148 & 267375. Remove temporary inline links TEMP054 on pole R12936. | .
479 |  | JE25003976 | SANSONW40-OHAKEA3132 33KV | Western | SANSONW40-OHAKEA3132 33KV | 2025-02-20 | 23:01 | 2025-02-20 | 23:05 | 0.031556 | 0.0094246 | 3416 | 11438 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Stage 0.5 Shift Sanson and Ohakea Substation from Bunnythorpe GXP to Marton GXP. Sanson ripple plant to be put into service and checked working prior to further outages proceeding. Phase rotation MUST be taken at VT secondary fuses W10 and recorded prior to outage | .
480 |  | JE25004815 | MANGOREWA | Eastern | MANGOREWA | 2025-02-20 | 9:00 | 2025-02-20 | 12:16 | 0.010492 | 5.7938e-05 | 21 | 3803 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | connect new cable and remove generation | .
481 |  | JE25005677 | 736 MID KAHUI ROAD,RAHOTU,OPUNAKE | Western | NGARIKI RD | 2025-02-20 | 5:33 | 2025-02-20 | 7:00 | 0.00024045 | 2.759e-06 | 1 | 87 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: NG405 No. Fuses: 2 Fuse Amp Size: 2 amp TIME CLOSED:7am Cause: possible strike Weather (wind/rain): calm Follow up required (select advisory)?N/A | .
482 |  | JE25005682 | 1112 KAHUTARA ROAD,KAHUTARA,FEATHERSTON | Western | KUMENGA | 2025-02-20 | 10:33 | 2025-02-20 | 13:18 | 0.0013676 | 8.2769e-06 | 3 | 496 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: Line Down due to mechanical damage Isolation: Fuses 7312 What was replaced? Conductor, conductor joints, and1x 10A HV fuse Where was it replaced (pole/TX/pillar box)? Pole 799096 Is 2R required? Y/N Additional Info: | .
483 |  | JE25005706 | 503 WARDS LINE,MORRISONS BUSH,GREYTOWN | Western | MOROA | 2025-02-20 | 7:33 | 2025-02-20 | 8:56 | 0.0011505 | 1.3795e-05 | 5 | 417 | Unplanned | WILDLIFE - BIRD | Fuses Location: 7495 No. Fuses: 2 Fuse Amp Size:6A TIME CLOSED: 08:56 Cause: Bird Weather (wind/rain) : Calm Follow up required (select advisory)?n | .
484 |  | JE25005711 | 173 CORNWALL ROAD,EAST TARATAHI,MASTERTON | Western | CHESTER RD | 2025-02-20 | 9:06 | 2025-02-20 | 10:48 | 0.00028287 | 2.759e-06 | 1 | 103 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: T3191 No. Fuses: 2 Fuse Amp Size:3 TIME CLOSED: 10:48 Cause: unknown Weather (wind/rain): Sunny Follow up required (select advisory)? N | .
485 |  | JE25005712 | 1175 LAKE FERRY ROAD,DYERVILLE,MARTINBOROUGH | Western | OTARAIA | 2025-02-20 | 9:10 | 2025-02-20 | 14:13 | 0.0016732 | 5.5179e-06 | 2 | 606 | Unplanned | WILDLIFE - POSSUM | Fuses Location: T2507 No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 14:12 Cause: Opossum Weather (wind/rain): Sunny Follow up required (select advisory)? N | .
486 |  | JE25005744 | 1187 TAIRUA WHITIANGA ROAD, WHENUAKITE, WHITIANGA | Eastern | COROGLEN | 2025-02-20 | 14:11 | 2025-02-20 | 16:11 | 0.00033066 | 2.759e-06 | 1 | 120 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faulty Transformer TC1171 - Replaced and loop reading is now within regulation. | .
487 |  | JE25005755 | 1835 27 ,PATETONGA,MORRINSVILLE | Eastern | PATETONGA | 2025-02-20 | 14:26 | 2025-02-20 | 16:15 | 0.00060055 | 5.5179e-06 | 2 | 218 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: FC4221 No. Fuses: 2 Fuse Amp Size: 15A TIME CLOSED: 16:15 Cause: Unknown - Possible Birds Weather (wind/rain): Clear Skys Follow up required (select advisory)? | .
488 |  | JE25005771 | WAVERLY GXP - CB 242 - RECLOSER 1406 | Western | WAITOTARA | 2025-02-20 | 15:22 | 2025-02-20 | 19:57 | 0.047751 | 0.00019037 | 69 | 17307 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11KV Rec 1406 Protection flags (nil where none): E/F CAUSE: Lines down Tree Location: Pole 841726 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): no Circuit patrolled and type: Weather (wind/rain): Fine LFI (Y/N + Comments): no Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
489 |  | JE25005824 | 19 GRANGE ROAD,OTUMOETAI,TAURANGA | Eastern | PILLANS POINT | 2025-02-20 | 21:15 | 2025-02-20 | 22:25 | 0.010204 | 0.00014623 | 53 | 3699 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Fuses SC4-413 Protection flags (nil where none): CAUSE: Faulty Cable Location: Temp generation (state details when used): Gen installed for Transformer TC4-091 Started 22:25 PERFORMANCE DETAIL DNO (number or state No): 2502015 Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): DNO 2502015 | .
490 |  | JE25005829 | 510 NORFOLK ROAD UPPER,NORFOLK,INGLEWOOD | Western | MOUNTAIN RD | 2025-02-20 | 22:32 | 2025-02-21 | 2:50 | 0.0021346 | 8.2769e-06 | 3 | 774 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Replaced Transformer 2434T Found 2 Blown Fuses at 5440 JE25005830 | .
491 |  | JE25005830 | JE25005829 | Western | MOUNTAIN RD | 2025-02-20 | 21:44 | 2025-02-21 | 2:46 | 0.0091552 | 3.0349e-05 | 11 | 3318 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 5440 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 02-45 Cause: Unknown Weather (wind/rain): Fine Follow up required (select advisory)? | .
492 |  | JE25000677 | MIDDLEBROOK | Eastern | MIDDLEBROOK | 2025-02-19 | 23:30 | 2025-02-20 | 3:50 | 0.24533 | 0.00094357 | 342 | 88920 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9154/1/2/3 & 9154/4 | .
493 |  | JE25000741 | KEENAN RD | Eastern | KEENAN RD | 2025-02-19 | 8:49 | 2025-02-19 | 15:22 | 0.10078 | 0.00025658 | 93 | 36529 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 211598. Install new Pole 1. Replace 11kv conductors between poles 211598 & 390298 with AAAC Iodine. Commission new 3c 300mm 11kv cable from new pole 1 @ Links 14981 to new CFC RMU 15001. Commission new 3c 300mm 11kv cable from new pole 2 @ Links 14962 to new CFCF RMU 15028. Commission new CFC RMU 15001 & New .CFCF RMU 15028. | .
494 |  | JE25001568 | WESTMERE GLADSTONE | Western | WESTMERE GLADSTONE | 2025-02-19 | 8:45 | 2025-02-19 | 11:32 | 0.015664 | 9.3805e-05 | 34 | 5677 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re-sag 11kV lines between ABS S156 & ABS S194 | .
495 |  | JE25002219 | OLD TAURANGA RD | Eastern | OLD TAURANGA RD | 2025-02-19 | 9:43 | 2025-02-19 | 14:09 | 0.021324 | 8.001e-05 | 29 | 7729 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 33kV Crossarms Pukekauri Rd between WKOCRE041 to WKOCRE044 & LV Pole P12412 | .
496 |  | JE25003801 | WAIONE | Western | WAIONE | 2025-02-19 | 9:21 | 2025-02-19 | 13:53 | 0.0022516 | 8.2769e-06 | 3 | 816 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Change red tagged pole P04767 , change HV arm P04927 | .
497 |  | JE25004365 | DAIRYFACT | Western | DAIRYFACT | 2025-02-19 | 9:15 | 2025-02-19 | 16:02 | 0.02271 | 0.00012139 | 44 | 8231 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Accucal doing metering testing to certify the units. | .
498 |  | JE25004607 | PUNGAREHU | Western | PUNGAREHU | 2025-02-19 | 10:00 | 2025-02-19 | 11:50 | 0.0018242 | 1.6554e-05 | 6 | 661 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace badly burnt xarm at pole 711016 | .
499 |  | JE25004766 | TE MATAI RD | Eastern | TE MATAI RD | 2025-02-19 | 9:46 | 2025-02-19 | 16:04 | 0.0020868 | 5.5179e-06 | 2 | 756 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace pole 221105 with a new 12.5m concrete busck, replace DDO Fuse with anew Fused ABS SE6-191. Planner note - 11kV Fuses on pole are currently earthed - these can be removed as part of the switching as they are NOC applied due to the cable fault. Downers are replacing the 11kV Cable on pole 221105 the following day. Northpower are aware of this and will not re connect the old 11kV cable. | .
500 |  | JE25005412 | RANGITANUKU RD | Eastern | RANGITANUKU RD | 2025-02-19 | 8:33 | 2025-02-19 | 10:43 | 0.00036004 | 2.759e-06 | 1 | 131 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Earth test on TC2966 required for maintenance | .
501 |  | JE25005493 | unknown LAKE FERRY ROAD,Dyerville,Rural | Western | DYERVILLE | 2025-02-19 | 8:56 | 2025-02-19 | 10:03 | 0.00018352 | 2.759e-06 | 1 | 67 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: Bolt came adrift on operating handle of Fused ABS 7891 What was replaced? Bolt replaced & birds nest removed Where was it replaced (pole/TX/pillar box)? Pole 845960 Is 2R required? Yes 2R Y - What is the timeframe for repairs? Completed Additional Info: | .
502 |  | JE25005537 | recloser_6497 | Western | MANGATOKI | 2025-02-19 | 10:00 | 2025-02-19 | 12:02 | 0.054151 | 0.00061525 | 223 | 19627 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Recloser 6497 Protection flags (nil where none): A, B Ph O/C CAUSE: No Fault Found Location: ??? Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Tree Trimmers working on Feeder Contacted to check if safe & if they had had a contact with line. No contact with line. team stood down. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
503 |  | JE25005597 | 257 ROYDON DOWNS ROAD,PAENGAROA,TE PUKE | Eastern | OLD COACH RD | 2025-02-19 | 11:22 | 2025-02-19 | 13:53 | 0.00041614 | 2.759e-06 | 1 | 151 | Unplanned | WILDLIFE - BIRD | Fuses Location: FP939 No. Fuses: 2 Fuse Amp Size:15 TIME CLOSED: 13:52 Cause: Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? N | .
504 |  | JE25005599 | 2208 POHANGINA ROAD,POHANGINA,ASHHURST | Western | POHANGINA | 2025-02-19 | 13:40 | 2025-02-21 | 15:50 | 0.0096033 | 8.2769e-06 | 2 | 3481 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Cause: Aged What was replaced? Where was it replaced (pole/TX/pillar box)? Is 2R required? Y/N 2R Y - What is the timeframe for repairs? Additional Info: 2R left open for repair of cable termination. 19/02/25 - Faulty Cable Identified, Isolated at Fuses F60, Line break made at Pole P14010, Line restored, TFR T4/65 left off 21/02/25 - Isolated at Fuses F60, Cable repaired, line break removed and power restored under Switching E00185 | .
505 |  | JE25005607 | KELVIN GROVE SUB - POHANGINA - REC 10303/2 | Western | POHANGINA | 2025-02-19 | 14:20 | 2025-02-19 | 19:51 | 0.16894 | 0.0028086 | 613 | 61234 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV, Rec 10303/2 Protection flags (nil where none): O/C A-C phase CAUSE: Line Down due to broken insulator Location: Pole P45547 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Operated at Pole P14294 Follow up Required (select advisory)? Additional fault restoration comments: Lines have been clashing by the looks SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
506 |  | JE25005616 | 133 UPPER STUART ROAD,ELTHAM,HAWERA | Western | MANGATOKI | 2025-02-19 | 14:36 | 2025-02-19 | 16:56 | 0.00038679 | 2.759e-06 | 1 | 140 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: 6350 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 16:55 Cause: Unknown Weather (wind/rain): Overcast Follow up required (select advisory)? | .
507 |  | JE25005635 | 400 BEAMISH ROAD,SANTOFT,BULLS | Western | LAKE ALICE | 2025-02-19 | 16:01 | 2025-02-19 | 17:06 | 0.0012563 | 1.9313e-05 | 7 | 455 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Blown Jumper found at Fuses 4248 Isolated at Fuses 4248 Jumper repaired | .
508 |  | JE25005673 | unknown PAHIATUA PONGAROA ROAD,Pahiatua,Pahiatua | Western | COONOOR | 2025-02-19 | 23:25 | 2025-02-20 | 1:41 | 0.023731 | 0.00029245 | 106 | 8601 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kv rec T42 Protection flags (nil where none): B & C phase Trip Flags CAUSE: Twisted Wires Location: Pole P46488 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Weather (wind/rain): Light Rain & Wind LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: These wire need to be defected Andrew Is going to do this T7/381 | .
509 |  | JE24045680 | HUIROA | Western | HUIROA | 2025-02-18 | 8:15 | 2025-02-18 | 16:12 | 0.053927 | 0.00011312 | 41 | 19546 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Clear trees between poles 709351 to 709355 | .
510 |  | JE25000574 | MAIN RD MOTONUI | Western | MAIN RD MOTONUI | 2025-02-18 | 8:46 | 2025-02-18 | 15:42 | 0.78298 | 0.0019175 | 695 | 283795 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles & cross arms From poles 743003 to pole 743073 run one span of 11kv lines from pole 743003 to 743062 & through joint 11kv cable at pole 370836. | .
511 |  | JE25000594 | LINDERMANN RD | Eastern | LINDERMANN RD | 2025-02-18 | 8:57 | 2025-02-18 | 15:12 | 0.030004 | 8.001e-05 | 29 | 10875 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv/400vt cross arms @ 204559,204560,204561,204562,204564. Replace LV pole 204563. Isolation point @ SB1-047 | .
512 |  | JE25000641 | LINDERMANN RD | Eastern | LINDERMANN RD | 2025-02-18 | 8:51 | 2025-02-18 | 12:23 | 0.0067009 | 3.3108e-05 | 12 | 2429 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9387/1/2/3 | .
513 |  | JE25000669 | SANDHURST | Eastern | SANDHURST | 2025-02-18 | 9:45 | 2025-02-18 | 11:18 | 0.023546 | 0.00025382 | 92 | 8535 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To isolate and level RMU 13168 | .
514 |  | JE25000671 | MATAKANA RD | Eastern | MATAKANA RD | 2025-02-18 | 9:16 | 2025-02-18 | 15:30 | 0.040321 | 0.0001076 | 39 | 14615 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 202051 (TC3-007); 202055 (T4760) , 202049, 202048, 202046 (TE3-136) | .
515 |  | JE25000692 | SOUTH RD NGARIKI | Western | SOUTH RD NGARIKI | 2025-02-18 | 9:00 | 2025-02-18 | 11:15 | 0.023829 | 0.00017657 | 64 | 8637 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | remove temp ABS TEMP049 at pole 713077 | .
516 |  | JE25001195 | WEST ST | Western | WEST ST | 2025-02-18 | 8:45 | 2025-02-18 | 14:30 | 0.075239 | 0.00021796 | 79 | 27271 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles and hardware between isolation points | .
517 |  | JE25001866 | KAIHERE | Eastern | KAIHERE | 2025-02-18 | 9:30 | 2025-02-18 | 14:53 | 0.053416 | 0.00016554 | 60 | 19361 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Pole O420 and install ABS TEMP053. Install ABS TEMP050 on Pole O335. Install ABS TEMP051 on Pole O386. Replace crossarms and hardware as per additional information. DNO raised for Sec SC08 DNO2502013 | .
518 |  | JE25003931 | RANGITANUKU RD | Eastern | RANGITANUKU RD | 2025-02-18 | 6:42 | 2025-02-18 | 9:46 | 0.00050724 | 2.759e-06 | 1 | 184 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | earth test on TC2966 required for maintenance Unable to get to transformer Jump cancelled | .
519 |  | JE25005303 | 407 MANUTAHI ROAD,LEPPERTON,NEW PLYMOUTH | Western | LEPPERTON | 2025-02-18 | 2:38 | 2025-02-18 | 4:37 | 0.027715 | 0.00065663 | 238 | 10045 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 12368/2 Protection flags (nil where none): A ph O/C & E/F CAUSE: Unknown Location: ? Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: operational Weather (wind/rain): rain LFI (Y/N + Comments): N Follow up Required (select advisory)? N Additional fault restoration comments: Lines patrolled No fault found | .
520 |  | JE25005309 | 5 ARAPUNI ROAD,LICHFIELD,PUTARURU | Eastern | LICHFIELD | 2025-02-18 | 5:39 | 2025-02-18 | 12:11 | 0.079622 | 0.0014043 | 357 | 28859 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 7 Protection flags (nil where none): B Ph O/C, E/F CAUSE: Broken Insulator Location: Pole 878946 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Fault found to be between ABS's 2520 & 2527 Back feds installed via Recloser RP03 & Sectionaliser 9595 Insulator Replaced SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
521 |  | JE25005312 | 209 RUANUI ROAD,TAIHAPE,TAIHAPE | Western | MATAROA A | 2025-02-18 | 13:16 | 2025-02-18 | 17:23 | 0.0013639 | 5.5179e-06 | 2 | 494 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: X1031 No. Fuses: 2 Fuse Amp Size: TIME CLOSED: Failed Cause: Transformer faulty Weather (wind/rain): Follow up required (select advisory)? Isolated at Transformer fuses Transformer replaced. Power restored 17:23 | .
522 |  | JE25005324 | sub_CLO | Western | CLOTON RD NORTH EAST | 2025-02-18 | 8:07 | 2025-02-18 | 11:44 | 0.24113 | 0.0040722 | 738 | 87400 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 4 Protection flags (nil where none): B Ph , E/F CAUSE: Cracked Insulator Location: 734357 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Raining LFI (Y/N + Comments): No Comms to LFI's on feeder Follow up Required (select advisory)? N Additional fault restoration comments: Isolated at ABS's 5800 & 5673 plus Links 5681/4 Back Feed installed via ABS 5713, Insulator Replaced SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
523 |  | JE25005365 | sub_KEG | Western | POHANGINA | 2025-02-18 | 9:58 | 2025-02-18 | 11:35 | 0.40028 | 0.005242 | 1900 | 145085 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11KV CB 8 Protection flags (nil where none): A & B Phase trip Flags CAUSE: Unknown Location: Unknown Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Fine LFI (Y/N + Comments): No Follow up Required (select advisory)? Additional fault restoration comments: This was back feeding into Fielding CB 13 & Kimbolton 5 patrolled and nothing Found SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
524 |  | JE25005390 | 26 COBHAM CRESCENT,TOKOROA,TOKOROA | Eastern | DUKE ST | 2025-02-18 | 11:53 | 2025-02-20 | 10:05 | 0.047425 | 0.00019865 | 36 | 17189 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Fault past Fuse /Sw 9547/2 Isolated at Fuse/Sw 9547/2 Generator to be installed - Sourcing generator currently and will install - No ETA Gen connected and all customers power restored at 19:45 On Emap Gen installed at TC3223 Repairs to be completed under planned work | .
525 |  | JE25005393 | sub_TUR | Western | SUMMERHILL | 2025-02-18 | 12:08 | 2025-02-18 | 15:38 | 0.38684 | 0.0066188 | 1749 | 140212 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kv Cb 5 Protection flags (nil where none): E/F Trip Flag CAUSE: Blown Insulator Location: Pole P46306 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Fine LFI (Y/N + Comments): No Follow up Required (select advisory)? Additional fault restoration comments: This was Back feeding some of CB 4 as well SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
526 |  | JE25005410 | 387A GALPINS ROAD,MARTON,MARTON | Western | TUTAENUI | 2025-02-18 | 13:42 | 2025-02-18 | 15:50 | 0.0010608 | 8.2769e-06 | 3 | 385 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: X4269 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 15:50 Cause: Wind Weather (wind/rain): Windy Follow up required (select advisory)? Full power restored Completed 2R on accident - 2R was not used | .
527 |  | JE25005431 | recloser_12368:2 | Western | LEPPERTON | 2025-02-18 | 14:46 | 2025-02-18 | 18:09 | 0.036682 | 0.00065663 | 238 | 13296 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | ETA 10mins. Firecoms advised Recloser 12368/2 Tripped A Ph E/F Back feed installed via SEc 12247 up to Sec 12194 Blown Insulator found at Pole 745376 Isolated at Fuses 8448 Insulator replaced | .
528 |  | JE25005443 | 33 BACK MIRANDA ROAD,WAITAKARURU,THAMES | Eastern | MANGATARATA | 2025-02-18 | 15:54 | 2025-02-18 | 16:59 | 0.018762 | 0.00028969 | 105 | 6800 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV DTX TC467 Lead off top D/Outs Protection flags (nil where none): Nil CAUSE: Lead off Deterioration Location: DTX TC467 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
529 |  | JE25005461 | 32 WARAHOE ROAD,MATATOKI,THAMES | Eastern | NGATI MARU | 2025-02-18 | 16:27 | 2025-02-18 | 21:00 | 0.0077257 | 6.0697e-05 | 11 | 2800 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Fuses Location: Fused/Sw 9447/4 No. Fuses: 3 Fuse Amp Size: 20A HRC fuses TIME CLOSED: 21:00 Cause: Blown cable termination Weather (wind/rain): Rain Follow up required (select advisory)? More info required on cable termination repairs Cable termination repaired HV fuses replaced | .
530 |  | JE25005473 | 362 TE KOPI ROAD,TE WHITI,MASTERTON | Western | PUKETIRO | 2025-02-18 | 17:27 | 2025-02-18 | 18:38 | 0.00019574 | 2.759e-06 | 1 | 71 | Unplanned | WILDLIFE - BIRD | Fuses Location: T3956 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 18:38 Cause: Bird strike Weather (wind/rain): Overcast Follow up required (select advisory)? | .
531 |  | JE25005481 | ATUAROA SUB - TE PUKE NORTH - ATUAROA AVE/4 | Eastern | TE PUKE NORTH | 2025-02-18 | 21:24 | 2025-02-19 | 2:42 | 0.017843 | 0.00027866 | 101 | 6467 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 4 Protection flags (nil where none): O/C, E/F, C Ø. CAUSE: Transformer failure Location: TE5-184 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: F1/F3, cursory patrolled. Weather (wind/rain): Calm LFI (Y/N + Comments): Yes, Sw/Gear 14269/1 and 2 Follow up Required (select advisory)? No Additional fault restoration comments: TE5-184 failed internally and was replaced. 1 x 30kVA 11kV/400V 3 Ø transformer 3 x 3A HV fuses SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
532 |  | JE25000659 | OKOROIRE | Eastern | OKOROIRE | 2025-02-17 | 8:31 | 2025-02-17 | 15:08 | 0.054816 | 0.00013795 | 50 | 19868 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Shut 8 Maintenance Pole sites Cross-arm Replacement: E12345; D13016; D13015;D13011; D13010; TIRPUT128; TIRPUT111 | .
533 |  | JE25000881 | TIKORANGI | Western | TIKORANGI | 2025-02-17 | 10:00 | 2025-02-17 | 11:39 | 0.00027314 | 2.759e-06 | 1 | 99 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To put in new 11kV 10m pole across Rd from fuses 6982 to get legal clearance across Rd | .
534 |  | JE25001111 | MANGAWEKA | Western | MANGAWEKA | 2025-02-17 | 9:05 | 2025-02-17 | 14:45 | 0.021568 | 6.3456e-05 | 23 | 7817 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace multiple poles & xarms between poles 810412 & 812162 and install new 11kV links 16191 at pole 810412. | .
535 |  | JE25005089 | 12800 ROUTE 52,TIRAUMEA,EKETAHUNA | Western | TIRAUMEA | 2025-02-17 | 7:34 | 2025-02-17 | 9:52 | 0.0064555 | 4.6902e-05 | 17 | 2340 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: V83 No. Fuses: 2 Fuse Amp Size: 8AMP TIME CLOSED: 9:52AM Cause: UNKNOWN Weather (wind/rain): CALM Follow up required (select advisory)?UNKNOWN | .
536 |  | JE25005100 | 265 NGATITANGATA ROAD,WAIHI,WAIHI | Eastern | WAIHI NORTH | 2025-02-17 | 11:48 | 2025-02-17 | 15:11 | 0.0039099 | 1.9313e-05 | 7 | 1417 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: TC1681 Fuses CAUSE: Internal fault Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: No Weather (wind/rain): Rain Follow up required (select advisory)? No Additional fault restoration comments: 1 x 30kVA 1 Ø transformer repalced 2 x 3A HV fuses 2 x 63A HRC fuses | .
537 |  | JE25005110 | REC_9373/2 | Eastern | CAMBRIDGE RD TIRAU | 2025-02-17 | 9:03 | 2025-02-17 | 11:22 | 0.062314 | 0.00075596 | 274 | 22586 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Recloser 9773/2 Protection flags (nil where none): E/F CAUSE: Unknown, No Fault Found Location: ??? Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Non Active Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
538 |  | JE25005126 | recloser_RC31 | Eastern | MOUNTAIN | 2025-02-17 | 10:13 | 2025-02-17 | 18:45 | 0.0098975 | 1.9313e-05 | 7 | 3587 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec RC31 Protection flags (nil where none): E/F CAUSE: Deterioration Location: Pole C1490 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Rain LFI (Y/N + Comments): Follow up Required (select advisory)? No Additional fault restoration comments: Cross arm replaced under Access Permit. Isolations at Recloser RC31 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): N/A Circuit that tripped: N/A DTF (KM):N/A | .
539 |  | JE25005127 | 752 WELCOME BAY ROAD,WAITAO,TAURANGA | Eastern | REID RD | 2025-02-17 | 12:10 | 2025-02-17 | 13:30 | 0.00066919 | 8.2769e-06 | 3 | 243 | Unplanned | VEGETATION - INSIDE ZONE | Fuses Location: Fuses SD5-162 No. Fuses: 3 Fuse Amp Size: 10A TIME CLOSED: 13:30 Cause: Branch in Lines Weather (wind/rain): Windy Follow up required (select advisory)? No | .
540 |  | JE25005128 | sub_AON | Eastern | WILLS RD | 2025-02-17 | 10:24 | 2025-02-17 | 11:39 | 0.0312 | 0.0011312 | 410 | 11309 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV CB4 Protection flags (nil where none): O/C A - C Ø CAUSE: Unknown Location: Unknown Temp generation (state details when used): N/A PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F3/4, cursory patrolled Weather (wind/rain): Raining LFI (Y/N + Comments): Only at pole 209808 Follow up Required (select advisory)? No Additional fault restoration comments: No fault found, lines patrolled. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
541 |  | JE25005158 | 20 GRABELLA PLACE,PAPAMOA BEACH,TAURANGA | Eastern | SANDHURST | 2025-02-17 | 10:35 | 2025-02-17 | 11:55 | 0.0010981 | 1.3795e-05 | 5 | 398 | Unplanned | WILDLIFE - BIRD | Fuses Location: SD5-005 No. Fuses: 2 Fuse Amp Size: 15A TIME CLOSED: 11:54 Cause: Bird Strike Weather (wind/rain): Wind an Rain Follow up required (select advisory)? | .
542 |  | JE25005168 | recloser_9275:2 | Eastern | KAIMAI DRIVE | 2025-02-17 | 12:46 | 2025-02-17 | 14:43 | 0.11811 | 0.0013353 | 484 | 42811 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 9275/2 Protection flags (nil where none): O/C A - B - C Ø CAUSE: Bark on lines Location: Pole 390961 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: F4, cursory patrolled. Weather (wind/rain): Rain LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Gumtree bark removed from lines at pole 390961 with hot stick. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
543 |  | JE25005179 | check if related too JE25005175 1160 WELCOME BAY ROAD,PAPAMOA,TE PUKE | Eastern | REID RD | 2025-02-17 | 13:51 | 2025-02-17 | 15:43 | 0.018277 | 0.00016278 | 59 | 6625 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Lines down between poles 219867 and 753043 5m Namu conductor replaced 2 x Full tension joints 2 x 30A HV fuses Lines broke due to wind causing a clash. | .
544 |  | JE25005182 | check if JE25005187 34 SHADY LANE,WELCOME BAY,TAURANGA | Eastern | KAITEMAKO RD | 2025-02-17 | 13:30 | 2025-02-17 | 17:24 | 0.0096623 | 4.4143e-05 | 16 | 3502 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: SD4-444 No. Fuses: 2 X 10A Fuse Amp Size: 10A TIME CLOSED: 17:23 Cause: Wind Weather (wind/rain): Windy Follow up required (select advisory)? Full power restored | .
545 |  | JE25005191 | recloser_9560:2 | Eastern | WHAKAMARAMA | 2025-02-17 | 13:47 | 2025-02-17 | 15:57 | 0.092611 | 0.00088839 | 322 | 33567 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 9560/2 Protection flags (nil where none): O/C CAUSE: Tree branch in road reserve broke an fell onto lines. // Tangled lines Location: 210178 - 210179 // 263346 - 210111 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: F4, cursory patrolled. Weather (wind/rain): High wind / heavy rain LFI (Y/N + Comments): Yes at Pole 210117 Follow up Required (select advisory)? No Additional fault restoration comments: Lines tangled due to fault current Branch touching lines cut off with hot stick SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
546 |  | JE25005195 | sub_KEG | Western | POHANGINA | 2025-02-17 | 14:08 | 2025-02-17 | 15:47 | 0.48045 | 0.0052448 | 1901 | 174140 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kv CB 8 Protection flags (nil where none): B & C Phase Trip flags CAUSE: Tree falling pass lines Location: Transformer T4/163 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Weather (wind/rain): Fine LFI (Y/N + Comments): Yes and working on SCADA, but no Alarm in View Point. Follow up Required (select advisory)? Additional fault restoration comments: Back Feeding in Kimbolton CB 5 and Fielding CB 13 as Kimbolton Sub Offload for SIS 119210 | .
547 |  | JE25005218 | 517 FRASER STREET,PARKVALE,TAURANGA | Eastern | OROPI RD | 2025-02-17 | 17:00 | 2025-02-17 | 19:59 | 0.066409 | 0.00058214 | 211 | 24070 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Replaced damaged 3 x HV fuse bases at SD4-369 | .
548 |  | JE25005264 | 311 1 LINE LONGBURN,LONGBURN,PALMERSTON NORTH | Western | TREMAINE AVE | 2025-02-17 | 16:53 | 2025-02-17 | 19:13 | 0.0011545 | 8.2769e-06 | 3 | 418 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | Fuses Location: 10336 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 19:12 Cause: Branch hitting lines Weather (wind/rain): calm Follow up required (select advisory)? | .
549 |  | JE25005271 | 12800 ROUTE 52,TIRAUMEA,EKETAHUNA | Western | TIRAUMEA | 2025-02-17 | 17:19 | 2025-02-26 | 12:21 | 0.011966 | 8.8287e-05 | 16 | 4337 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: V83 No. Fuses: 1 Fuse Amp Size: 8 TIME CLOSED: 19:09 Cause: Suspect the trees in lines at 3 places. Weather (wind/rain): light rain Follow up required (select advisory)? Y- Faultman will leave 2R open and will try and get tree contractors out to cut trees in morning. | .
550 |  | JE25005284 | 129 MATAI ROAD,MATAMATA,MATAMATA | Eastern | STATION RD | 2025-02-17 | 19:51 | 2025-02-18 | 14:25 | 0.02458 | 2.2072e-05 | 8 | 8909 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: Fuses FC2160 Protection flags (nil where none): No Tripping CAUSE: Tree on Lines Location: Pole 248812 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Rain LFI (Y/N + Comments): No Follow up Required (select advisory)? Yes Additional fault restoration comments: Permit suspended, Crew has reached maximum hours and fatigued. Another crew will come in the daytime. Job half done, trees cleared off lines. Pole still to be erected by new crew, new permit 18/02/2025 Work continued Pole Replaced Power Restored 14:24 | .
551 |  | JE25005290 | TAHUNA SUB - MANGATEPARU - TAHUNA/2 | Eastern | MANGATEPARU | 2025-02-17 | 19:34 | 2025-02-18 | 15:05 | 0.29772 | 0.0015919 | 577 | 107911 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: CB 2 Protection flags (nil where none): EF, Phase C CAUSE: Car versus DTX TC1604 Pole , High Low Contact also Location: Pol;e 484110 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): Nil Circuit patrolled and type: Cursory Weather (wind/rain): Rain LFI (Y/N + Comments): None Follow up Required (select advisory)? No Additional fault restoration comments: Fault location information misleading at the 1st.Faultman went to wrong address at Transformer TP2833 instead of TC1604 (Hazard address) Transformer pole 484110 Broken in half. Replaced pole only, transformer to be replaced during day time. Power restored to Permit area at 02:19 EXCEPT TRANSFORMER TC1604, which will be replaced during day time 18/02/25 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): No Circuit that tripped: N/A DTF (KM): N/A ETA Advised to fire and police 20 mins | .
552 |  | JE25005297 | 195 WAIRIO ROAD,KAHUTARA,FEATHERSTON | Western | KUMENGA | 2025-02-17 | 22:21 | 2025-02-18 | 2:46 | 0.001754 | 1.9313e-05 | 7 | 636 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | ETA Advised 50 mins to an hour Transformer T3664 on fire. Isolated Fuses 8129 First at 22:20.then Further isolation at Fuses 7300 at 22:30 to allow Fire fighters to extinguish fire safely. Closed back Fuses 7300 after Fire was extinguished and contnued to replace Transformer T3664 under Access Permit. Full power restored 02:46 (18/02/25). 400V 3 phase service for one customer left open till daytime to confirm with phase rotation | .
553 |  | JE25005299 | 1962 3 ,MAXWELL,WANGANUI | Western | MAXWELL | 2025-02-17 | 21:46 | 2025-02-17 | 22:49 | 0.0038229 | 6.0697e-05 | 22 | 1386 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 774 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 22:49 Cause: unknown Weather (wind/rain): light rain Follow up required (select advisory)? | .
554 |  | JE25000643 | TOWNSHIP & LS | Eastern | TOWNSHIP & LS | 2025-02-16 | 8:30 | 2025-02-16 | 13:45 | 0.00086871 | 2.759e-06 | 1 | 315 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - FC5012/FC5017 | .
555 |  | JE25005031 | 86 MINGAROA ROAD,HALCOMBE,FEILDING | Western | KAKARIKI | 2025-02-16 | 7:09 | 2025-02-16 | 8:57 | 0.00089104 | 8.2769e-06 | 3 | 323 | Unplanned | WILDLIFE - BIRD | Fuses Location: M75 No. Fuses: 2 Fuse Amp Size: 15 TIME CLOSED: 08:57 Cause: Bird Strike Weather (wind/rain): calm Follow up required (select advisory)? | .
556 |  | JE25005033 | 12800 ROUTE 52,TIRAUMEA,EKETAHUNA | Western | TIRAUMEA | 2025-02-16 | 7:28 | 2025-02-16 | 9:33 | 0.0058391 | 4.6902e-05 | 17 | 2116 | Unplanned | WILDLIFE - BIRD | Fuses Location: V83 No. Fuses: 2 Fuse Amp Size: 8 TIME CLOSED: 09:32 Cause: Bird Strike Weather (wind/rain): calm Follow up required (select advisory)? | .
557 |  | JE25005044 | KIMBOLTON SUB - APITI - P47 | Western | APITI | 2025-02-16 | 11:20 | 2025-02-16 | 18:08 | 0.020598 | 0.00031176 | 43 | 7466 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV REC P47 Protection flags (nil where none): A ph O/C & E/F CAUSE: Damaged insulator due to bird Location: pole P12005 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: operational Weather (wind/rain): calm Follow up Required (select advisory)? N Additional fault restoration comments: Line isolated at ABS's P51 & E45 to replace insulator. | .
558 |  | JE25005051 | unknown TE RERENGA KUAOTUNU ROAD,Otapaurau,Rural | Eastern | OWERA RD | 2025-02-16 | 18:00 | 2025-02-16 | 19:47 | 0.00059161 | 5.5179e-06 | 2 | 214 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: Fuses FP69 No. Fuses: 1 Fuse Amp Size: 3A TIME CLOSED: 19:47 Cause: Blown lightning arrestor Weather (wind/rain): Rainy Follow up required (select advisory)? No Alos isolated at Fuses FP69 to replace blown centre phase lighting arrestor at pole 855359 cricifix | .
559 |  | JE25005059 | 3912 1 ,HUNTERVILLE,HUNTERVILLE | Western | HUNTERVILLE 22KV | 2025-02-16 | 18:07 | 2025-02-16 | 20:23 | 0.0018751 | 1.3795e-05 | 5 | 680 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: 4014 No. Fuses: 2 Fuse Amp Size: 8 TIME CLOSED: 20:22 Cause: unknown Weather (wind/rain): calm Follow up required (select advisory)?n Line patrolled | .
560 |  | JE25005062 | 65 LONGWOOD WEST ROAD,SOUTH FEATHERSTON,FEATHERSTON | Western | SOUTH FEATHERSTON | 2025-02-16 | 18:23 | 2025-02-16 | 20:06 | 0.00056861 | 5.5179e-06 | 2 | 206 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses 11001 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 20:05 Cause: Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? No | .
561 |  | JE25005065 | 5 KAWAKAWA STREET,MANGAWEKA,MANGAWEKA | Western | MANGAWEKA | 2025-02-16 | 20:55 | 2025-02-16 | 22:18 | 0.0027612 | 3.3108e-05 | 12 | 1001 | Unplanned | VEGETATION - INSIDE ZONE | Job in incorrect location, emap drawn incorrectly for HV Fuses for TFR X1629 Reported by fire comm's F4150261,Shed fire, bush fire under Pole 808597 Isolated at Fuses 741 Possible vegetation touching the HV lines and being so dry it has started a fire in the bamboo which has caused the end of cross arm to catch fire Insulator moved away from burnt section of the cross arm, Downer to defect and replace at a later date Customer at 6321 SH 1 has been disconnected as there Service cable has been burnt up, TAG C47445, Downer to return tomorrow with gear to repair/replaced/fix service Full power restored to HV Jeremy advised tag has been removed - C47445 Replaced low voltage cross arm and 30 meters of OH conductor, and 3x 40A fuse at the pole. Pole number# 808597 Customer has full power. FM advised he will put in a HV shut. | .
562 |  | JE25005070 | unknown BLUESKIN ROAD,Brunswick,Rural | Western | BRUNSWICK | 2025-02-16 | 22:09 | 2025-02-17 | 0:00 | 0.00061331 | 5.5179e-06 | 2 | 222 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: X3118 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 00:00 Cause: unknown Weather (wind/rain): calm Follow up required (select advisory)?n | .
563 |  | JE24046823 | COUNTY WATER | Eastern | COUNTY WATER | 2025-02-15 | 8:23 | 2025-02-15 | 10:35 | 0.00036377 | 2.759e-06 | 1 | 132 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV RMU oil maintenance at IC1955, T5424, T5459 & T6287 | .
564 |  | JE25004986 | 40 MIKKELSEN ROAD,TE AROHA,TE AROHA | Eastern | MAUNGAKAWA ROAD | 2025-02-15 | 5:24 | 2025-02-15 | 16:18 | 0.12027 | 0.0010925 | 396 | 43591 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Voltage device &amp; number: 11kV, CB 5 Protection flag indication: A/R,B, C Fault, E/F, OC, Ground Fault Patrolled &amp; type: No Follow-up required? (Select advisory): Weather at time of fault: Calm LFI Activation: Y Pole C12592, C13268 & C13284 Cause:- car Vs Pole Call in by Fire (F4149398) Pole and transformer replaced HV Restored at 16:17. 400V Fuses at Transformer TC228 open on time of restoring HV to enable Inspectors to test installations after line clash 400V transformer fuses closed & 319 Alexandra Road Reconnected Tag (Meter Bypassed retailer advised) 364 Alexandra Rd Disconnected, meter needs replacing no one living in house at present Tag Number 38324 | .
565 |  | JE25005002 | 3547 SOUTH RD,OPUNAKE,OPUNAKE | Western | PIHAMA | 2025-02-15 | 13:20 | 2025-02-15 | 14:30 | 0.00019179 | 2.759e-06 | 1 | 70 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Faultman found broken jumper to transformer 5402E, line was isolated at Fuses 6944 to repair the jumper - cause was due to deterioration of the joint | .
566 |  | JE25005010 | FEEDER FAULT - WAIHI SUB - WAIHI NORTH - REC13777 | Eastern | WAIHI NORTH | 2025-02-15 | 15:08 | 2025-02-15 | 16:34 | 0.019669 | 0.00022899 | 83 | 7129 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: Sectionaliser 13777 Protection flags (nil where none): EF CAUSE: Unknown Location: N/A Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Line patrolled, nothing found. | .
567 |  | JE25005022 | 18 WAIINU BEACH ROAD,WAITOTARA,WANGANUI | Western | WAITOTARA | 2025-02-15 | 23:05 | 2025-02-16 | 1:25 | 0.0042478 | 3.0349e-05 | 11 | 1540 | Unplanned | WILDLIFE - BIRD | Lines down at Pole 774738, lines still live as being back feed through down stream TFR's, small grass fire around pole 774738 (Put out by faultman) Isolated at Fuses 2716 (2 Fuses Blown) Dead bird found at lines down site, lines repaired, Fuses reloaded with 30A Loads, full power restored | .
568 |  | JE25000362 | MARANGAI | Western | MARANGAI | 2025-02-14 | 9:16 | 2025-02-14 | 13:27 | 0.0041558 | 1.6554e-05 | 6 | 1506 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re-conductor 11kV between poles 774057 & 468970 | .
569 |  | JE25001492 | PARK RD | Western | PARK RD | 2025-02-14 | 8:45 | 2025-02-14 | 15:49 | 0.050802 | 0.00012691 | 46 | 18414 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 819730, 819731 and 11kv cross arms on T603 open point will remain the same locked and tagged at site 819730 the required NCCN Will be put in place at a later date as advised from Gavin Paget Job ran over time, Phasing not carried out | .
570 |  | JE25001857 | KAIHERE | Eastern | KAIHERE | 2025-02-14 | 9:00 | 2025-02-14 | 13:35 | 0.0053049 | 1.9313e-05 | 7 | 1923 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles O435, 877411 and replace 2 spans of LV conductor | .
571 |  | JE25004869 | 7 WILSON ROAD NORTH,PAENGAROA,TE PUKE | Eastern | MAKETU | 2025-02-14 | 1:15 | 2025-02-14 | 1:16 | 0.0024012 | 0.0017961 | 651 | 870 | Unplanned | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | Voltage & Device ID: 11kV Rec 14788 Protection flags (nil where none): E/F Weather (wind/rain): Calm Follow up required (select advisory): LFI Activation: Y/N No | .
572 |  | JE25004881 | 416 NEWBURY LINE, BUNNYTHORPE, 4867 | Western | TE ARAKURA | 2025-02-14 | 9:14 | 2025-02-14 | 12:15 | 0.045587 | 0.00025107 | 91 | 16523 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Car V Pole P39292 Car V Pole did not trip the Recloser D77/2, no lines down or Line clash Back feed put in place Isolated at ABS D76, D77/1 & Links D77/6 Pole P39292 & Hardware replaced & cross arm replaced at Pole P39293 Full Power restored | .
573 |  | JE25004902 | 3 CLOTEN ROAD,STRATFORD,STRATFORD | Western | CLOTON RD WEST | 2025-02-14 | 10:25 | 2025-02-14 | 15:13 | 0.0029184 | 0.00047454 | 86 | 1058 | Unplanned | HUMAN ERROR - POTENTIAL WORKMANSHIP | City Care Water / Gerome / 0274846060 URGENT SO - 11kV UG Cable - Watermain repairs needed to be completed under urgent circumstances Located outside Can-am Taranaki Shop HV cable installed 3-4 years ago has been drilled through a sewer line, causing a leak into a stream. Cable had enough flex to be raised for sewer to be repaired and reinstated on completion of works. Cable is in a duct so work was completed deenergised | .
574 |  | JE25004945 | 80 POPLAR LANE, PAPAMOA | Eastern | BLACK STUMP | 2025-02-14 | 17:06 | 2025-02-14 | 17:56 | 0.00013689 | 2.759e-06 | 1 | 50 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: Sw/Gear 13625/3 Protection flags (nil where none): N/A CAUSE: Broken Fuses at Pole 220877 Location: Pole 220877 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): None Follow up Required (select advisory)? No Additional fault restoration comments: Fuses repaired under access permit. Isolation at Sw/Gear 13625/3. 1 X Fuse holder, candle stick and 10A Fuse replaced Full power restored at 17:55Hrs | .
575 |  | JE25004946 | 375 TIPOKA ROAD, RAHOTU, OPUNAKE, 4685 | Western | PUNGAREHU | 2025-02-14 | 16:18 | 2025-02-14 | 17:16 | 0.004872 | 8.5528e-05 | 31 | 1766 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Isolate at Fuses PU364 to repair 1 x jumper at Fuses 6993 | .
576 |  | JE25004961 | 994 MAIN DRAIN RD, RANGIOTU, PALMERSTON NORTH, 4477 | Western | TAIKOREA | 2025-02-14 | 17:58 | 2025-02-14 | 19:55 | 0.031231 | 0.00026762 | 97 | 11320 | Unplanned | ADVERSE ENVIRONMENT - FIRE | Scrub Fire near pole P36218. Cable and Ducting damaged at Pole P36218 (ABS 10194) Isolated at ABS's B21,B18 & 10194 Back feed installed via ABS B23 Line Break made at Pole 378406 Power restored 2R left open for testing on Monday DNO-2503001 made 01/03/25 Job to be completed under DNO | .
577 |  | JE24046636 | HUNTERVILLE 22KV | Western | HUNTERVILLE 22KV | 2025-02-13 | 9:30 | 2025-02-13 | 15:16 | 0.0095433 | 2.759e-05 | 10 | 3459 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace four red tagged poles 808537, 808534, 808531 & 808530 and replace leaking transformer Z167 on pole 808558 | .
578 |  | JE24046642 | NGATEA | Eastern | NGATEA | 2025-02-13 | 23:31 | 2025-02-14 | 1:35 | 0.052756 | 0.00042488 | 154 | 19122 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV RMU oil maintenance at Sw/Gear 9264 | .
579 |  | JE24046711 | FONTERRA WWTP | Western | FONTERRA WWTP | 2025-02-13 | 10:37 | 2025-02-13 | 12:30 | 0.00031259 | 2.759e-06 | 1 | 113 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Recloser 10240/2 maintenance on protection and CB | .
580 |  | JE24046713 | PASCAL ST 9 | Western | PASCAL ST 9 | 2025-02-13 | 9:01 | 2025-02-13 | 17:15 | 0.041486 | 8.8287e-05 | 32 | 15037 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11KV ABS A55 & A56 no fuses on emap for T6/34 at HV Level opened TEMP084 to create outage | .
581 |  | JE24046839 | LICHFIELD | Eastern | LICHFIELD | 2025-02-13 | 9:31 | 2025-02-13 | 16:41 | 0.081732 | 0.00019037 | 69 | 29624 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Shut 7 Maintenance Pole sites Pole Replacement: TIRPUT124. Cross-arm Replacement: TIRPUT120; TIRPUT121; TIRPUT122;TIRPUT125; TIRPUT138, TIRPUT125, TIRPUT129,TIRPUT131, M12604/M13294. | .
582 |  | JE25000373 | SOUTH RD NGARIKI | Western | SOUTH RD NGARIKI | 2025-02-13 | 8:46 | 2025-02-13 | 13:13 | 0.019925 | 7.4492e-05 | 27 | 7222 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace hv conductor from pole 713214 to 713222 with new bare kutu | .
583 |  | JE25000445 | RAETIHI | Western | RAETIHI | 2025-02-13 | 8:31 | 2025-02-13 | 14:22 | 0.021276 | 6.0697e-05 | 22 | 7712 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles & cross arms from pole 777815, 777811,777810,777812,777809 | .
584 |  | JE25001112 | KAIMAI DRIVE | Eastern | KAIMAI DRIVE | 2025-02-13 | 8:46 | 2025-02-13 | 13:48 | 0.0041739 | 1.3795e-05 | 5 | 1513 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv pole 211645. Replace 11kv cross arm @ pole 211644. Replace 11kv overhead conductors between poles 211642 & 211645 with ACSR Magpie | .
585 |  | JE25002254 | MAUNGARANGI RD | Eastern | MAUNGARANGI RD | 2025-02-13 | 8:35 | 2025-02-13 | 15:47 | 0.007159 | 1.6554e-05 | 6 | 2595 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 1. Replace pole 221927, 221932. 2. Install pole#1 btw 221460 & 221927 c/w Links 14934. 3. Liven UG cable btwn new pole#1 (from Links 14934) & RMU 14966/3 4. Liven UG cable btwn 489638 & RMU 14970/3 | .
586 |  | JE25003646 | WEST ST | Western | WEST ST | 2025-02-13 | 8:45 | 2025-02-13 | 14:29 | 0.048356 | 0.00014071 | 51 | 17527 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles and hardware and install new ABS 11504 at Pole 361412 | .
587 |  | JE25004663 | 77 UPPER OHAUITI ROAD, OHAUITI, TAURANGA, 3173 | Eastern | OHAUITI RD | 2025-02-13 | 12:06 | 2025-02-13 | 12:37 | 0.00085068 | 2.759e-05 | 10 | 308 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | no immediate danger 2r left open for repairs possible tomorrow. Unsecure Cable Support Arm, Resecured and now safe Outage Between 12:05 and 12:36 | .
588 |  | JE25004711 | 99A INLAND NORTH ROAD, WAITARA | Western | TIKORANGI | 2025-02-13 | 3:03 | 2025-02-13 | 7:16 | 0.018496 | 8.001e-05 | 29 | 6704 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Car V Pole called in by Police Event # P061599387 Pole 840574 Isolated at ABS's 5121, 5135, 5140, 5262, 5207, & 6224/1. Plus Links 12707/4, & 6224/6 Back Feds installed via Sw/Gear 5010/3, ABS 5128, & SEc 12583/2 NDR to follow | .
589 |  | JE25004718 | unknown LOWER WAIAU ROAD,Waverley,Waverley | Western | WAITOTARA | 2025-02-13 | 7:11 | 2025-02-13 | 9:51 | 0.014152 | 8.8287e-05 | 32 | 5130 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Line patrolled past Fuses 2719(2 blown Fuses), Lines down found at Pole 781394 Isolated at Fuses 2719 Lines repaired, Full power restored unknown what has caused line to come down, possible an old clash point, line broke above a drive way | .
590 |  | JE25004723 | 15 CANNOCK ROAD,HINAKURA,MARTINBOROUGH | Western | COLOGNE ST | 2025-02-13 | 6:24 | 2025-02-13 | 11:01 | 0.010528 | 4.6902e-05 | 17 | 3816 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Line patrolled Fuses Location: 7380 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 09:40 Cause: unknown Weather (wind/rain): calm Follow up required (select advisory)?n Fuses Location: 7382 No. Fuses: 1 Fuse Amp Size: 10 TIME CLOSED: 11:00 Cause: unknown Weather (wind/rain): calm Follow up required (select advisory)?n | .
591 |  | JE25004786 | 181 MANUTAHI ROAD,TARURUTANGI,NEW PLYMOUTH | Western | KATERE 5 | 2025-02-13 | 11:34 | 2025-02-13 | 13:55 | 0.0031062 | 2.2072e-05 | 8 | 1126 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | ETA 5 minutes, customer advised. Isolate Tfr 677 11kV Fuses for additional safety to repair LV lines down NDR to follow | .
592 |  | JE25004863 | 3 HAUROTO ROAD,HAWERA,HAWERA | Western | KETEMARAE RD | 2025-02-13 | 21:11 | 2025-02-13 | 22:10 | 0.0018165 | 3.0349e-05 | 11 | 658 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: WH831 No. Fuses: 2 Fuse Amp Size: 10 Amp TIME CLOSED: 22:10 Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)? N | .
593 |  | JE25004866 | sub_HST | Eastern | CHAPEL ST | 2025-02-13 | 22:16 | 2025-02-24 | 15:40 | 0.058239 | 0.000847 | 195 | 21109 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Cable Protection flags (nil where none): E/F CAUSE: Cable Fault Location: Cable from Sw/Gear 9018/4 Temp generation (state details when used): DTX TL1-002 Gen Installed 04:00, DTX TP2207 Gen Connected 05:00 DTX T2-1 Gen connected 12:30 PERFORMANCE DETAIL DNO (number or state No): 2502010 Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): Yes Follow up Required (select advisory)? Yes Additional fault restoration comments: Generators connected to three transformers. Cable fault finding in progress and repairs to be made Monday 17/02/25 Force restored outage due to Temp Conditions not working on emap. Job to be completed on DNO DNO 2502010 removed | .
594 |  | JE24045588 | TIRAUMEA | Western | TIRAUMEA | 2025-02-12 | 9:13 | 2025-02-12 | 15:49 | 0.048105 | 0.00012139 | 44 | 17436 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Vegetation Work - Tree Felling/Section felling between 11kV poles: P00776/P04211 and P00496 | .
595 |  | JE24045893 | DAIRY FACTORY | Western | DAIRY FACTORY | 2025-02-12 | 9:04 | 2025-02-12 | 14:06 | 0.029103 | 9.6564e-05 | 35 | 10548 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace S598 with new front mounted automated Entec switch | .
596 |  | JE24046643 | TOKO | Western | TOKO | 2025-02-12 | 8:32 | 2025-02-12 | 14:11 | 0.01775 | 5.242e-05 | 19 | 6434 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace lv poles 759302 , 759305. Replace hv pole and stay at pole and resag lv conductor from pole 759308 to 759312 759308. Replace lv arm and stay at pole 759312. Replace stay at pole 759304. Install new stay insulators and retention stay at pole 759301 | .
597 |  | JE24046658 | MOAWHANGO | Western | MOAWHANGO | 2025-02-12 | 10:01 | 2025-02-12 | 15:40 | 0.014033 | 4.1384e-05 | 15 | 5087 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install new links at pole 373420 (temp032) links to be left open and tagged the line from this point isolated | .
598 |  | JE24046666 | MATAKANA RD | Eastern | MATAKANA RD | 2025-02-12 | 9:07 | 2025-02-12 | 15:36 | 0.09889 | 0.00025382 | 92 | 35843 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 1: Install Generator for School and Te Kohanga Reo 2: Replace poles 202014, 202015, 202040, 202041, 202043. 3: Replace pole 202058, Install Temporary Pole Mount Links TEMP64. 4: Reconductor from 424885/424086 to 427403 5: Disconnect Generator | .
599 |  | JE24046693 | 13TH AVE | Eastern | 13TH AVE | 2025-02-12 | 8:46 | 2025-02-12 | 11:27 | 0.03955 | 0.00024555 | 89 | 14335 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To carry out PD tests and cleaning cable terminations at SK5-071/ SK5-072/ SK5-073 | .
600 |  | JE25001213 | OLD CAMBRIDGE RD | Eastern | OLD CAMBRIDGE RD | 2025-02-12 | 10:10 | 2025-02-12 | 13:06 | 0.018373 | 0.00010484 | 38 | 6660 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Repair HV cable at pole 262650 and reconnect back to overhead line | .
601 |  | JE25001851 | MANGATARATA | Eastern | MANGATARATA | 2025-02-12 | 9:34 | 2025-02-12 | 12:19 | 0.02278 | 0.00013795 | 50 | 8257 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Shutdown 2: Outage Area 2: 522, 9668/1, 9668/4, RC22/1, RC22/4 Reconductor LV: Poles O438 to O14192 | .
602 |  | JE25002300 | BARRETT RD | Eastern | BARRETT RD | 2025-02-12 | 9:06 | 2025-02-12 | 14:46 | 0.37382 | 0.0011091 | 402 | 135493 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace sectionaliser 9695/2 with an Entec & remove 9695/1 . This will get rid of DNO 2411005 | .
603 |  | JE25004569 | 131 CHAPEL STREET,MASTERTON,MASTERTON | Western | CORNWALL ST | 2025-02-12 | 2:30 | 2025-02-12 | 3:27 | 0.091881 | 0.0016305 | 591 | 33303 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV CB C856 Protection flags (nil where none): E/F A Ø CAUSE: Unknown Location: Unknown Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F3, entire line patrolled Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: No fault cause found. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
604 |  | JE25004571 | 434 NETHERTON ROAD,NETHERTON,PAEROA | Eastern | AWAITI | 2025-02-12 | 4:25 | 2025-02-12 | 8:35 | 0.016526 | 6.6215e-05 | 24 | 5990 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: FP1153 No. Fuses: 2 Fuse Amp Size:15A TIME CLOSED: 08:34 Cause: Lightning Weather (wind/rain): lightning Follow up required (select advisory)?n | .
605 |  | JE25004576 | 299 WANI ROAD,NETHERTON,PAEROA | Eastern | AWAITI | 2025-02-12 | 6:19 | 2025-02-12 | 10:07 | 0.011936 | 5.242e-05 | 19 | 4326 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses FP1146 No. Fuses: 2 Fuse Amp Size: 20A TIME CLOSED: 10:06 Cause: Bird Strike Weather (wind/rain): Fine Follow up required (select advisory)? No | .
606 |  | JE25004577 | 1011 PAEROA-TAHUNA ROAD,OTWAY,TE AROHA | Eastern | MOUNTAIN | 2025-02-12 | 6:27 | 2025-02-12 | 9:32 | 0.003565 | 1.9313e-05 | 7 | 1292 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses FC2120 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 09:31 Cause: Bird Strike Weather (wind/rain): Fine Follow up required (select advisory)? No | .
607 |  | JE25004689 | 2497 COAST ROAD, PONGAROA, PONGAROA, 4991 | Western | COAST ROAD | 2025-02-12 | 18:39 | 2025-02-12 | 19:55 | 0.025674 | 0.00033935 | 123 | 9305 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | eye bolt out of cross arm at Transformer T9/206 Isolated at ABS V63 & Links V62 eye bolt re-attached o cross arm | .
608 |  | JE25004703 | 432 ENDOWMENT ROAD,OTWAY,TE AROHA | Eastern | SPRINGDALE | 2025-02-12 | 20:58 | 2025-02-12 | 23:25 | 0.0012213 | 8.2769e-06 | 3 | 443 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: FC2377 No. Fuses: 2 & 2 x holders Fuse Amp Size: 6 TIME CLOSED: 23:25 Cause: unknown Weather (wind/rain): calm Follow up required (select advisory)? N | .
609 |  | JE25004707 | 469 PARATU ROAD,RICHMOND DOWNS,WALTON | Eastern | KEREONE | 2025-02-12 | 21:36 | 2025-02-12 | 23:08 | 0.00076266 | 8.2769e-06 | 3 | 276 | Unplanned | VEGETATION - OUTSIDE ZONE | Fuses Location: FP871 No. Fuses: 2 Fuse Amp Size: 8 TIME CLOSED: 23:08 Cause: Line clash due to fallen tree Weather (wind/rain): calm Follow up required (select advisory)?N | .
610 |  | JE24046497 | ROLLESTON ST | Eastern | ROLLESTON ST | 2025-02-11 | 9:20 | 2025-02-11 | 16:03 | 0.17578 | 0.00043592 | 158 | 63714 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE 11KV POLE T12573 AND STRAIGHTEN POLE T12574 | .
611 |  | JE24046573 | LINDERMANN RD | Eastern | LINDERMANN RD | 2025-02-11 | 9:18 | 2025-02-11 | 15:31 | 0.063029 | 0.00018209 | 66 | 22845 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv/400vt cross arms @ 204619,204620,204621,204622,204624, 249356.Replace LV pole 204623. .Isolation point @ SB1-002. | .
612 |  | JE24046617 | PASCAL ST 9 | Western | PASCAL ST 9 | 2025-02-11 | 9:01 | 2025-02-11 | 15:39 | 0.013117 | 3.3108e-05 | 12 | 4754 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Connect new 11KV UG at Double poles remove OH between T6/34 & T6/241 | .
613 |  | JE24046632 | RAETIHI | Western | RAETIHI | 2025-02-11 | 9:04 | 2025-02-11 | 14:37 | 0.020171 | 6.0697e-05 | 22 | 7311 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Jerusalem Replace poles 777830, 777828,777822,777819,777818,777817,777816,777815 | .
614 |  | JE24046634 | SOUTH RD NGARIKI | Western | SOUTH RD NGARIKI | 2025-02-11 | 9:30 | 2025-02-11 | 14:25 | 0.021851 | 7.4492e-05 | 27 | 7920 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace poles 713215, 713216, 713218, 713219, 713220 & 713221. replace fused abs and hard ware on pole 848072. | .
615 |  | JE25000646 | TIKORANGI | Western | TIKORANGI | 2025-02-11 | 8:45 | 2025-02-12 | 17:15 | 0.016646 | 2.759e-05 | 10 | 6033 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 754687, 754690/691 & 754688/689 and reconductor across the river (dual circuit). Remove OH span between 754687 & 754688/754689. Run new OH span for the new temporary link between 754789/788 (Mamuku Rd No. 1) & 754688/689. Job ran over time Line break in place at the End of work 11/02/2025 12/02/2025 Work Completed Network restored to Normal Configuration | .
616 |  | JE25001149 | PURIRI ST | Western | PURIRI ST | 2025-02-11 | 9:01 | 2025-02-11 | 14:46 | 0.44307 | 0.0012829 | 465 | 160594 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace/relocate Pole 453372, 765528 & 765612 closer to customer boundary & re align LV & HV conductor | .
617 |  | JE25001979 | OLD CAMBRIDGE RD | Eastern | OLD CAMBRIDGE RD | 2025-02-11 | 8:31 | 2025-02-11 | 11:26 | 0.0033755 | 1.9313e-05 | 7 | 1223 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | PQI - To upgrade transformer TC1839 to 50kVA 3 phase | .
618 |  | JE25003189 | RONGOMAI | Western | RONGOMAI | 2025-02-11 | 9:30 | 2025-02-11 | 14:32 | 0.077213 | 0.00025934 | 94 | 27986 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace ABS I39 with new Sectionaliser 10913/2 . Replace fuses I37 with fused ABS 10932 , Fuses I41 with Fused ABS 10943 , Fuses I43 with Fused ABS 10941 . | .
619 |  | JE25004434 | CLAREVILLE SUB - PARK RD - C408/2 | Western | PARK RD | 2025-02-11 | 7:19 | 2025-02-11 | 8:35 | 0.063806 | 0.00094632 | 343 | 23127 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11KV Rec C408 Protection flags (nil where none): A & B Phase O/C CAUSE: Unknown Location: Unknown Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Fine LFI (Y/N + Comments): There but not working Follow up Required (select advisory)? Additional fault restoration comments: There was a Hot line tag on the Rec C408 due to tree Trimmings working in Area CAC 118541 They were not on site when fault happen Called and got they not to start work . Once all Fault switching was done Called Tree Trimmers and allowed them to start work Again | .
620 |  | JE25004437 | 101 MCMAHON AVENUE,WHANGAPOUA,COROMANDEL | Eastern | OWERA RD | 2025-02-11 | 6:38 | 2025-02-11 | 7:40 | 0.0022471 | 3.5867e-05 | 13 | 814 | Unplanned | WILDLIFE - POSSUM | Fuses Location: Fuses FC2312 No. Fuses: 2 Fuse Amp Size: 15A TIME CLOSED: 07:40 Cause: Possum Weather (wind/rain): Calm Follow up required (select advisory)? No | .
621 |  | JE25004462 | 2965 SH 1,HUNTERVILLE,MARTON | Western | HUNTERVILLE 22KV | 2025-02-11 | 9:42 | 2025-02-11 | 13:18 | 0.0017875 | 8.2769e-06 | 3 | 648 | Unplanned | WILDLIFE - BIRD | Fuses Location: Transformer Z135 No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 13:18 Cause: Bird Strike Weather (wind/rain): Fine Follow up required (select advisory)? No | .
622 |  | JE25004494 | 368 WAIHI WHANGAMATA ROAD,WAIHI,WAIHI | Eastern | WAIHI NORTH | 2025-02-11 | 16:46 | 2025-02-11 | 18:01 | 0.0098903 | 0.00013243 | 48 | 3585 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Broken Cross arm at Pole WHIWGM042 Back feed put in place Isolated at ABS IC278, 9604/1 & Links 9604/4 Cross Arm Replaced, Full power restored, feeder restored to normal config | .
623 |  | JE25004535 | recloser_2032 | Western | WATERWORKS RD | 2025-02-11 | 16:47 | 2025-02-12 | 10:16 | 0.17845 | 0.0014733 | 141 | 64681 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kv Rec 2032 Protection flags (nil where none): C Phase E/F CAUSE: Lines down Plus floating conductor Location: between Poles 784080 & 784081 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Calm LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Isolated at ABS 085 Lines & Floater repaired Recloser tripped again on livening Second line down found between Poles 784094 & 784095 Isolated @ ABS 085 Lines repaired Recloser tripped again 6 min after livening Isolated at ABS 085 Lines found twisted at Pole 784098 Untwisted using Hot Sticks Recloser tripped again on livening Isolated at ABS 085 FM to return in day light 2R Left Open Patrolled Lines and Found Lines down at Pole 784081 Blue phase repaired and all liven up OK SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
624 |  | JE25004540 | 8 MARSHALL PLACE,KATIKATI,KATIKATI | Eastern | WHARAWHARA ROAD | 2025-02-11 | 17:10 | 2025-02-11 | 17:58 | 0.00086926 | 2.2072e-05 | 8 | 315 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | NAPA E00183 (DNO-2502001) New Cable installed and connected between Fuses S4670 & TFR T4601 Generators removed from network, LV breaks closed Full power restored | .
625 |  | JE25004557 | EST_STM | Western | STRATHMORE | 2025-02-11 | 19:50 | 2025-02-12 | 1:51 | 0.11026 | 0.0014016 | 264 | 39966 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 7131 Protection flags (nil where none): A Ph , E/F CAUSE: Broken Cross arm Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Isolated at ABS's 12085/1 & 4818. Plus Links 12085/4, 4950 & 8926 Back Feed install via Sec 6813 Cross arm replaced SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
626 |  | JE25004561 | recloser_9121:2 | Eastern | TE MIRO RD | 2025-02-11 | 21:02 | 2025-02-11 | 23:34 | 0.084081 | 0.0010319 | 374 | 30476 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 9121/2 Protection flags (nil where none): E/F CAUSE: Unknown Location: Unknown Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4, cursory patrolled. Weather (wind/rain): Calm LFI (Y/N + Comments): No indication Follow up Required (select advisory)? No Additional fault restoration comments: Lines sectionalized and patrolled, no fault cause could be found. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
627 |  | JE25004566 | sub_MOK | Western | MOTUKAWA 33kV | 2025-02-11 | 22:17 | 2025-02-13 | 15:38 | 0.19695 | 0.0090301 | 3101 | 71386 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 33kV CB 2742 Protection flags (nil where none): Red Ph E/F CAUSE: Unknown Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Due to work not be complete under NAPA 114637 there was a hole in the 33kV network and MOK, ING, & MCK Subs were being feed from Stratford GXP These were all lost on the tripping of CB 2742 at Stratford GXP LFI's were active at Pole 760328 & 760322 CB 3132 was opened to Isolated fault indicated area Sub were then brought back into service in steps while working other faults FM were stood down until morning once all power was restored, due to rick of causing further outages 2R left open for lines to be patrolled in day light SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): Attempted to restore MOK generation but when closed CB 210, it immediately tripped and also tripped HUI 1292 & MAM 3202. Suspect that a closed 3.3kV BUS at MAM may have resulted in unexpected protection issue. Restored lines and with CB 3202 open closed CB 210 without issue. escalate if CB 3202 can be left open while the temporary line | .
628 |  | JE24045572 | HARRIS BLOCK | Eastern | HARRIS BLOCK | 2025-02-10 | 8:48 | 2025-02-10 | 15:02 | 0.090816 | 0.00024279 | 88 | 32917 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FRANKLIN TREES REQUIRE OUTAGE FOR TREE CLEARING at pole B0825 | .
629 |  | JE24045576 | AUROA | Western | AUROA | 2025-02-10 | 8:45 | 2025-02-10 | 12:47 | 0.0013369 | 5.5179e-06 | 2 | 485 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | asplundh to cut trees between poles 716879 to 716881 | .
630 |  | JE24045693 | MARANGAI | Western | MARANGAI | 2025-02-10 | 9:18 | 2025-02-10 | 14:35 | 0.0052487 | 1.6554e-05 | 6 | 1902 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace all X-Arms & Transformer on pole 791956 - X2306 | .
631 |  | JE24046138 | COLVILLE | Eastern | COLVILLE | 2025-02-10 | 10:15 | 2025-02-10 | 14:35 | 0.0076947 | 0.00011036 | 40 | 2789 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To reinstall SWER Reclosers 9927 and 9929 after coil setting change and refurbish. | .
632 |  | JE24046364 | GORDON | Eastern | GORDON | 2025-02-10 | 9:45 | 2025-02-10 | 12:21 | 0.0042048 | 2.759e-05 | 10 | 1524 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole F12802 and replace HV xarm at pole F12804 | .
633 |  | JE24046413 | TAVERNER ST | Western | TAVERNER ST | 2025-02-10 | 8:45 | 2025-02-10 | 9:57 | 0.0047388 | 6.6215e-05 | 24 | 1718 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace binders and tighten hardware at pole 820162 | .
634 |  | JE24046420 | TE POI | Eastern | TE POI | 2025-02-10 | 9:30 | 2025-02-10 | 10:15 | 0.0014904 | 3.3108e-05 | 12 | 540 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Work Within M.A.D'S to repair stay on Pole F1948 | .
635 |  | JE24046581 | MANAIA | Western | MANAIA | 2025-02-10 | 9:01 | 2025-02-10 | 15:00 | 0.010883 | 3.0349e-05 | 11 | 3945 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace tx 5113E and re arm pole 718548 (same pole as tx) | .
636 |  | JE24046589 | BROOKLANDS 7 | Western | BROOKLANDS 7 | 2025-02-10 | 10:06 | 2025-02-10 | 12:34 | 0.031033 | 0.00020968 | 76 | 11248 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Straighten pole & re-sag low wires at pole 701817 to comply with ECP34 regulations. | .
637 |  | JE25001547 | SELWYN ST | Eastern | SELWYN ST | 2025-02-10 | 23:04 | 2025-02-11 | 4:12 | 0.017859 | 5.7938e-05 | 21 | 6473 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Isolate Switch gear SL3-119 , SL3-121 and SAL3-116 , Clean cable Termination . Carry out Insulation resistance and contact resistance on the contacts. Complete maintenance on switch . Liven and do a PD Test Sw/Gear maintenance was completed, on livening the cable to SL3-116 it was noted that there was a noise emanating from the live HV cable Northpower deemed it not safe to put the cable under load and the cable was isolated and earth. Back feeds are still in place. The DNO was not removed but updated with the relevant info. | .
638 |  | JE25001837 | MANGATARATA | Eastern | MANGATARATA | 2025-02-10 | 9:00 | 2025-02-10 | 15:53 | 0.096654 | 0.00023451 | 85 | 35033 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | "Shutdown 1: Outage Area 1: 507, 9668/1, 9668/4, RC22/1, RC22/4 G1: Replace pole O14192 G2: Replace pole O14191 G3: Replace pole O438 (Heavy Lift) G4: Replace arm O12421 & Insulate Stay O437 G5: Replace arms 877434, O439. 400V Re-conductor pole 263718 to O438 G6: Replace arms 389229, O440. 400V Re-conductor pole 263718 to O438 " | .
639 |  | JE25004267 | 2809 27 ,SPRINGDALE,MORRINSVILLE | Eastern | TE PUNINGA | 2025-02-10 | 0:25 | 2025-02-10 | 3:36 | 0.0010501 | 5.5179e-06 | 2 | 381 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses FC2156 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 03:35 Cause: Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? No | .
640 |  | JE25004401 | REC_2743 PARIHAUHAU ROAD,Parikino,Rural | Western | MAKIRIKIRI | 2025-02-10 | 17:08 | 2025-02-10 | 18:59 | 0.0076997 | 6.8974e-05 | 25 | 2791 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 2713 Protection flags (nil where none): A & B ph E/F CAUSE: Branch on lines Location: Pole 480493 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: cursory Weather (wind/rain): calm LFI (Y/N + Comments): N Follow up Required (select advisory)? Additional fault restoration comments: Fault men removed branch from lines with hot line sticks. | .
641 |  | JE25004403 | 64 PASCAL STREET,PALMERSTON NORTH,PALMERSTON NORTH | Western | PASCAL ST 8 | 2025-02-10 | 17:23 | 2025-02-10 | 20:46 | 0.058554 | 0.00084148 | 276 | 21223 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 8 Protection flags (nil where none): C ph E/F & O/C invt CAUSE: Cable Fault Location: Sw/Gear G137/B & Magnefix G135/A Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Yes - 2502007 Circuit patrolled and type: operational Weather (wind/rain): calm LFI (Y/N + Comments): Y Follow up Required (select advisory)? N Additional fault restoration comments: Cable isolated & Earthed between Sw/Gear G137/B & Magnefix G135/A | .
642 |  | JE25004406 | 17 TUKAKI ROAD,TIROHIA,PAEROA | Eastern | TIROHIA-KARANGAHAKE | 2025-02-10 | 17:35 | 2025-02-11 | 4:14 | 0.062382 | 0.00062628 | 187 | 22611 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 13420/2 Protection flags (nil where none): E/F CAUSE: Blown insulator Location: Pole C3176 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4, Operational pole top inspection Weather (wind/rain): Calm LFI (Y/N + Comments): Yes but not connected to faulty section due to line break and back feeds in place Follow up Required (select advisory)? Yes, NAPA required to restore TLB. Additional fault restoration comments: Fault finding process followed but could not find the fault with a cursory patrol. An operational pole top inspection was done and found the blown insulator. There is a temp line break at pole C14107 on a previous tripping (JE25003313) that was cut to lesson the outage area and this needs to be repaired with NAPA switching. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
643 |  | JE24045959 | ESSEX ST | Western | ESSEX ST | 2025-02-09 | 9:00 | 2025-02-09 | 11:00 | 0.0026438 | 2.2072e-05 | 8 | 958 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Create line break live line, replace 11kv strain arms at pole 831378 and re instate line break | .
644 |  | JE25004224 | 7 STOKES ROAD,MAUNGATAUTARI,CAMBRIDGE | Eastern | TOTMANS RD | 2025-02-09 | 1:22 | 2025-02-09 | 2:48 | 0.049077 | 0.00076423 | 277 | 17788 | Unplanned | WILDLIFE - POSSUM | REGULATORY INFORMATION Voltage & Device ID: Recloser 13085 Protection flags (nil where none): EF CAUSE: Possum Location: Pole D1317 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): Yes at Pole D1301 Follow up Required (select advisory)? No Additional fault restoration comments: Line patrol done. Possum found at Pole D1317, removed with hot stick and power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): N/A Circuit that tripped: N/A DTF (KM):N/A | .
645 |  | JE25004228 | 53 ROTOKOHU ROAD,PAEROA,PAEROA | Eastern | WILLOUGHBY ST | 2025-02-09 | 2:40 | 2025-02-09 | 4:23 | 0.088128 | 0.0020058 | 727 | 31943 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: CB 1 Protection flags (nil where none): EF, Phase B Fault CAUSE: Unknown Location: N/A Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Line patrolled, sectionalised, nothing found, Power restored whole feeder SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): N/A Circuit that tripped: N/A DTF (KM):N/A | .
646 |  | JE25004230 | 64 SEPTIMUS STREET,EKETAHUNA,EKETAHUNA | Western | EKETAHUNA | 2025-02-09 | 5:35 | 2025-02-09 | 12:51 | 0.16208 | 0.0021658 | 422 | 58746 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 2 Protection flags (nil where none): E/F, O/C A, B & C CAUSE: Tree Down over Lines Location: Pole P{27958 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Weather (wind/rain): Fine LFI (Y/N + Comments): no Follow up Required (select advisory)? Additional fault restoration comments: This fault Caused another Fault at Pole P15191 Which was Fault Current blow Fargos apart Replaced all 3 at that site 2 R left Open as some wire needs Replacement Phil to arrange shutdown to do this Going to put in shutdown | .
647 |  | JE25004257 | 389A UPPER KINA ROAD, OAONUI, OPUNAKE, 4681 | Western | SOUTH RD NGARIKI | 2025-02-09 | 21:30 | 2025-02-09 | 22:44 | 0.00082015 | 1.1036e-05 | 4 | 297 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: NG353 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 22:43 Cause: unknown Weather (wind/rain): calm Follow up required (select advisory)? | .
648 |  | JE25004184 | 26 LENIHAN DRIVE,TE PUKE,TE PUKE | Eastern | MOEHAU ST | 2025-02-08 | 2:49 | 2025-02-08 | 5:22 | 0.093949 | 0.001934 | 701 | 34052 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | CB 5 Tripped on A to Ground Flags Cable Fault Between Pole 222425 and Pole 409508 - Cable End Cut Away and line Break Created. DNO 2502006 | .
649 |  | JE25004188 | 1220 RANGITIKEI LINE,NEWBURY,PALMERSTON NORTH | Western | TE ARAKURA | 2025-02-08 | 5:23 | 2025-02-08 | 7:00 | 0.00053561 | 5.5179e-06 | 2 | 194 | Unplanned | WILDLIFE - BIRD | Fuses Location: D88 No. Fuses: 2 Fuse Amp Size: 15 TIME CLOSED: 07:00 Cause: Ducks Strike Weather (wind/rain): calm Follow up required (select advisory)? Job was logged at customers home but loss of supply was to cow sheds past Fuses D88 | .
650 |  | JE25004189 | 382 KAIHERE ROAD,KAIHERE,NGATEA | Eastern | PUHUNGA ISLAND RD | 2025-02-08 | 6:05 | 2025-02-08 | 7:15 | 0.0036781 | 5.242e-05 | 19 | 1333 | Unplanned | WILDLIFE - BIRD | Fuses Location: FC4174 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 07:15 Cause: Swan Weather (wind/rain): Calm Follow up required (select advisory)? No | .
651 |  | JE25004190 | 29 MATIPO STREET,TAKARO,PALMERSTON NORTH | Western | MAIN ST 15 | 2025-02-08 | 7:35 | 2025-02-08 | 8:08 | 9.1092e-05 | 2.759e-06 | 1 | 33 | Unplanned | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuse/Sw 10600/4 No. Fuses: 3 Fuse Amp Size: 40 TIME CLOSED: 08:08 Cause: unknown Weather (wind/rain): calm Follow up required (select advisory)? Faultman replaced all 3 (40 amp) of the fuses, will take the remaining 2 fuses to have them tested. | .
652 |  | JE25004196 | 264 RANGIURU ROAD,RANGIURU,TE PUKE | Eastern | MANGOREWA | 2025-02-08 | 11:31 | 2025-02-08 | 21:15 | 0.033529 | 5.7938e-05 | 21 | 12153 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Fuses Location: Fuses SE6-191 No. Fuses: Fuse Amp Size: TIME CLOSED: Cause: Weather (wind/rain): Follow up required (select advisory)? Cable blown in more than one spot. Gen to be connected. Isolated at Fuses SE6-191 400V Cable Break at Transformer TE6-240-Generator connected 19:15 Hrs 11kV Cable Break made at Link Box TE6-240LB-11kV Generator connected at 21:15 Hrs Cale faultfinding and repair to be done on Monday 10/02/25 11/02/25 - DNO 2402008 Cable fault between Fuses SE6-191 & Link Box TE6-240 | .
653 |  | JE25004218 | 3 AOKAUTERE DRIVE, FITZHERBERT, PALMERSTON NORTH, 4410 | Western | SUMMERHILL | 2025-02-08 | 22:19 | 2025-02-08 | 23:57 | 0.055286 | 0.00056559 | 205 | 20039 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Reports of smocking equipment around 3 Aokautere Drive faultman found a faulty pot head on pole P44476 back feeds put in place Isolated at ABS H36, Sw/Gear 391 & 10930/1 Line break cut at Pole P4889 - cable & faulty pot head have been isolated Power restored Downer to talk with Powerco on a fix - pot head replacement both ends of complete cable replacement as existing cable is an old paper lead cable Fault to be repaired under DNO-2502011 | .
654 |  | JE24046135 | TUTAENUI | Western | TUTAENUI | 2025-02-07 | 9:41 | 2025-02-07 | 13:30 | 0.01204 | 5.242e-05 | 19 | 4364 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace red tagged pole 802989 and pole 802970 | .
655 |  | JE25004072 | 2299 1 ,MARTON,MARTON | Western | PUTORINO | 2025-02-07 | 7:11 | 2025-02-07 | 8:46 | 0.0023474 | 2.4831e-05 | 9 | 851 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 1481 No. Fuses: 2 Fuse Amp Size: 5 amp TIME CLOSED: 845 am Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)? Nothing to report power restored | .
656 |  | JE25004102 | unknown unknown ,Homebush,Masterton | Western | CHURCH ST | 2025-02-07 | 9:51 | 2025-02-07 | 10:48 | 0.00015749 | 2.759e-06 | 1 | 57 | Unplanned | UNKNOWN - DATA QUALITY | Fuses Location: TX 698 No. Fuses: 2 Fuse Amp Size: 10 amp TIME CLOSED: 10:47am Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)? site was Tx 698 was not TX 4244 as listed injob Complete for now and will update details with AIteam | .
657 |  | JE25004107 | 53 MATENE PL,PAPAMOA BEACH,TAURANGA | Eastern | SANDHURST | 2025-02-07 | 11:05 | 2025-02-07 | 11:37 | 0.0037785 | 0.00011864 | 43 | 1370 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Fuses Location: Fuse/Sw 9579/2- Pole 215085 No. Fuses: 3 Fuse Amp Size: 16A TIME CLOSED: 11:37 Cause: Tractor v Pole (Driver stung by WASPS) Weather (wind/rain): Sunny Follow up required (select advisory)? No Tractor driver stung by wasps lost control of vehicle and hit p[ole 215085.Pole not damaged but blew Fuses at Fuse/Sw 9579/2. due to line clash. 3 x16A Fuses Fuses replaced & full power restored Faultman to generate NDR | .
658 |  | JE25004164 | 2351 OHURA ROAD,STRATHMORE,STRATFORD | Western | STRATHMORE | 2025-02-07 | 17:05 | 2025-02-07 | 19:00 | 0.00063646 | 5.5179e-06 | 2 | 231 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 2550T No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 19:00 Cause: lightning Weather (wind/rain): lightning Follow up required (select advisory)?n | .
659 |  | JE25004169 | unknown PAKU ROAD,Richmond Downs,Rural | Eastern | KEREONE | 2025-02-07 | 20:06 | 2025-02-08 | 2:00 | 0.00097764 | 2.759e-06 | 1 | 354 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Cause: private line down Tag no: A38254 Customer advised? yes, getting a PAC Disco safety register + emailed retailer: Y Is 2R required? N Additional Info: line NOT energised on arrival HV fuses also dropped, Les will call control for HV component Open as pre Caution - Tractor Brought LV Lines Down Private Lines - Going to be fixed by private contractor 3 x 6A Fuses Relivened at 02:00 | .
660 |  | JE25004178 | 1089 MAKAKAHI ROAD,MAKAKAHI,RAETIHI | Western | RAETIHI | 2025-02-07 | 20:37 | 2025-02-07 | 22:47 | 0.00071735 | 5.5179e-06 | 2 | 260 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Y62 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 22:47 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n Replaced 1 x barrel | .
661 |  | JE25003996 | unknown MARSHALL ROAD,Rangiwahia,Rural | Western | COLYTON | 2025-02-06 | 10:30 | 2025-02-06 | 11:37 | 0.0036924 | 5.5179e-05 | 20 | 1338 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FM to return in morning as farm said to dangerous to get over farm 2night 06/02/25 - Line patrolled, Broken Jumper found at Pole P17492 Back feed put in place Isolated at ABS N53, N21/1 & Links N21/6 Repaired Jumper & replaced a faulty DDO to TFR T5/297, Full power restored | .
662 |  | JE25004033 | 36 SLACKS ROAD, AWAPUNI, PALMERSTON NORTH, 4412 | Western | PIONEER | 2025-02-06 | 16:52 | 2025-02-06 | 19:30 | 0.02052 | 0.00012967 | 47 | 7438 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Check JE25004037 on closure T6/290 is the right transformer. Linked to wrong transformer on creation. ETA advised - 20 mins F4143471 Blown Cable crutch at pole P41597 Isolated at Fuses A69 & 400V Cable break at TFR T6/290 Bushings LV back feeds put in place 2R required for repair of Cable DNO-2503002 made 01/03/025 Job to be completed under DNO | .
663 |  | JE25004041 | 25 WEKA STREET, POHANGINA, ASHHURST | Western | POHANGINA | 2025-02-06 | 18:13 | 2025-02-06 | 19:01 | 0.00039867 | 8.2769e-06 | 3 | 145 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: Deterioration What was replaced? Stay wires Where was it replaced (pole/TX/pillar box)? Pole Is 2R required? Yes 2R Y - What is the timeframe for repairs? Completed Additional Info: Transformer T4/372 Isolated for repair of Stay wire Power off 18:12 Power on 19:00 Stay was replaced - 26/02/2025 CG as per Wiremu Kaipuke Jobs all linked - JE25007250 , JE25004043 | .
664 |  | JE24045947 | KATERE 5 | Western | KATERE 5 | 2025-02-05 | 8:52 | 2025-02-05 | 15:03 | 0.062407 | 0.0001683 | 61 | 22620 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove ABS 268 from pole 746610. Replace pole 746612 with a new double B11 with new sectionaliser 12745/2, new bypass ABS 12745/1 and two new sets of solid links 12745/4, 12745/6. Remove fuses 8163. | .
665 |  | JE24046211 | WAIHI NORTH | Eastern | WAIHI NORTH | 2025-02-05 | 9:51 | 2025-02-05 | 13:26 | 0.0047561 | 2.2072e-05 | 8 | 1724 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace leaking 50kVA micropad transformer TC6218 | .
666 |  | JE24046224 | PATETONGA | Eastern | PATETONGA | 2025-02-05 | 9:15 | 2025-02-05 | 15:02 | 0.035404 | 0.00010208 | 37 | 12832 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV conductor between poles K1508 & K13350 with Ferret | .
667 |  | JE24046471 | MAUNGAKAWA ROAD | Eastern | MAUNGAKAWA ROAD | 2025-02-05 | 8:49 | 2025-02-05 | 13:28 | 0.023911 | 8.5528e-05 | 31 | 8667 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole WHUKER021 & xarms at poles C12580 & C12582 | .
668 |  | JE24046593 | KOHETE RD | Western | KOHETE RD | 2025-02-05 | 9:30 | 2025-02-05 | 14:40 | 0.0017106 | 5.5179e-06 | 2 | 620 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Tx structures 2575T + 2347T + pole 760006 | .
669 |  | JE24046635 | ESSEX ST | Western | ESSEX ST | 2025-02-05 | 9:11 | 2025-02-05 | 14:15 | 0.016801 | 5.5179e-05 | 20 | 6090 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install new top mounted non automated Entec switch 11507/2 & Links /4 at pole 361904 | .
670 |  | JE25000407 | PARAPARA | Western | PARAPARA | 2025-02-05 | 9:01 | 2025-02-05 | 16:27 | 0.01725 | 0.00034211 | 69 | 6253 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re-conductor 11KV between ABS 596 & pole 783781 upgrading from Squirrel to Mink | .
671 |  | JE25001836 | KUMENGA | Western | KUMENGA | 2025-02-05 | 8:30 | 2025-02-05 | 12:20 | 0.025349 | 0.00011036 | 40 | 9188 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install new automated Entec switch 11495/2 & links 11495/4 on pole 798715 & remove ABS S531 from pole 469031/469019. Sec 11495/2 not SCADA commissioned on this NAPA | .
672 |  | JE25002642 | COLOGNE ST | Western | COLOGNE ST | 2025-02-05 | 9:51 | 2025-02-05 | 12:29 | 0.0043601 | 2.759e-05 | 10 | 1580 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install 3 Ground Stay Insulators (Pineapples) at Pole 816496 and Relocate centre phase Jumper from Fuses 7387 to increase distance to Ground Stay wire. JE25001524 signed off | .
673 |  | JE25003067 | BARRETT RD | Eastern | BARRETT RD | 2025-02-05 | 10:16 | 2025-02-05 | 14:40 | 0.089292 | 0.00034487 | 125 | 32364 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Connect new cable at poles 413070 & 413656 Connect new cable & install new fuses at pole 208602 to supply TC3-183 Remove generator | .
674 |  | JE25003802 | PURANGI | Eastern | PURANGI | 2025-02-05 | 10:07 | 2025-02-05 | 15:44 | 0.035352 | 0.00010484 | 38 | 12814 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Sw/Gear IC1466/FC2739/IC1454 with CFC RMU 15065 & reconnect transformer TC6180 to new RMU fused at 25A. Shut down rang over due to switch gear labelling errors & land access issues that didn't allow preworks to go ahead yesterday | .
675 |  | JE25003874 | 1962 3 ,MAXWELL,WANGANUI | Western | MAXWELL | 2025-02-05 | 10:05 | 2025-02-05 | 12:54 | 0.010282 | 6.0697e-05 | 22 | 3727 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faulty DDO's to TFR X268 at Pole 780045 Isolated at Fuses 774 DDO's Replaced, Full power restored | .
676 |  | JE25003877 | 173 CORNWALL ROAD,EAST TARATAHI,MASTERTON | Western | CHESTER RD | 2025-02-05 | 7:21 | 2025-02-05 | 8:14 | 0.00014712 | 2.759e-06 | 1 | 53 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: T3191 No. Fuses: 2 Fuse Amp Size: 2 amp TIME CLOSED: 8:14am Cause: Unknown Weather (wind/rain): calm Follow up required (select advisory)? N/a | .
677 |  | JE25003880 | 2599 PAHIATUA PONGAROA ROAD,MAKURI,PAHIATUA | Western | COONOOR | 2025-02-05 | 10:45 | 2025-02-05 | 16:49 | 0.0060228 | 1.6554e-05 | 6 | 2183 | Unplanned | VEGETATION - INSIDE ZONE | Tree through lines past Pole P46809 Isolated at Fuses T33 Tree cleared away from lines, lines repaired, full power restored | .
678 |  | JE25003892 | unknown KAHUTARA ROAD,Kahutara,Rural | Western | DAIRY FACTORY | 2025-02-05 | 11:26 | 2025-02-05 | 12:57 | 0.0045324 | 4.9661e-05 | 18 | 1643 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fault DDO's to TFR T3179 at Pole 799604 Isolated at ABS S1206 DDO's replaced, full power restored | .
679 |  | JE25003895 | 1 DULCIE STREET, PAEROA, 3600 | Eastern | RAILWAY ST | 2025-02-05 | 9:51 | 2025-02-05 | 11:15 | 0.057447 | 0.00068146 | 247 | 20822 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Burnt Out Ampac on HV Line at Pole 482682 - Isolated for Repair Grant Also Replaced HV Jumper | .
680 |  | JE25003966 | 727 KETEMARAE ROAD,NORMANBY,HAWERA | Western | CAMBRIA LS | 2025-02-05 | 14:51 | 2025-02-05 | 17:36 | 0.0018224 | 1.1036e-05 | 4 | 661 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: C6520 Fuses CAUSE: age Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: Weather (wind/rain): fine Follow up required (select advisory)? Additional fault restoration comments: Replace Tx C6520 | .
681 |  | JE25003988 | 173 WAIKAKAHI SETTLEMENT ROAD, PONGAROA | Western | COAST ROAD | 2025-02-05 | 18:38 | 2025-02-05 | 19:56 | 0.0032032 | 4.1384e-05 | 15 | 1161 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Replace 3 X Insulators and re Blind them Isolated at Fuses V52 | .
682 |  | JE24045557 | WESTMERE GLADSTONE | Western | WESTMERE GLADSTONE | 2025-02-04 | 8:46 | 2025-02-04 | 14:09 | 0.13124 | 0.00040557 | 147 | 47569 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re sag multiple sites past ABS S369 and ABS S194 Also Install Recloser C420/2 | .
683 |  | JE24046009 | COLOGNE ST | Western | COLOGNE ST | 2025-02-04 | 8:35 | 2025-02-04 | 14:44 | 0.065223 | 0.00017657 | 64 | 23641 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT: Replace pole 845617. Clear vegetation at poles 816765, 483011. Repair conductor at pole 353386. | .
684 |  | JE24046107 | PASCAL ST 9 | Western | PASCAL ST 9 | 2025-02-04 | 9:00 | 2025-02-04 | 13:31 | 0.0088748 | 3.3108e-05 | 12 | 3217 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install Double poles & replace 11KV Xarms between Temp084 & A56 replace TX T6/241 | .
685 |  | JE24046121 | MANAIA COROMANDEL | Eastern | MANAIA COROMANDEL | 2025-02-04 | 9:31 | 2025-02-04 | 15:13 | 0.074525 | 0.0014898 | 274 | 27012 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace HV Term arm at TC4666 Re-sag O/H lines | .
686 |  | JE24046143 | LOVEGROVE RD | Eastern | LOVEGROVE RD | 2025-02-04 | 9:45 | 2025-02-04 | 16:35 | 0.035079 | 8.5528e-05 | 31 | 12715 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Pole C342 and install new links 15032 | .
687 |  | JE24046144 | SOUTH RD NGARIKI | Western | SOUTH RD NGARIKI | 2025-02-04 | 9:16 | 2025-02-04 | 14:15 | 0.042973 | 0.00014347 | 52 | 15576 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace poles 713210, 713211, 713212, 713213, 713236, 713214, 713199 & 713202. install new stay at 713210. replace hv conductor from pole 713213 to 713214 with new kutu. replace LV conductor from pole 373636 to 713210 with new pvc kutu | .
688 |  | JE24046150 | LINDERMANN RD | Eastern | LINDERMANN RD | 2025-02-04 | 8:46 | 2025-02-04 | 14:44 | 0.056399 | 0.00015726 | 57 | 20442 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv/400vt cross arms @ 204509,204510,204511,204513,204514,204556, & 204527. Isolation point @ SB1-041. & 33kv ABS 1049 & 33kv ABS 66 | .
689 |  | JE24046257 | TURAKINA | Western | TURAKINA | 2025-02-04 | 8:45 | 2025-02-04 | 16:40 | 0.0065537 | 1.3795e-05 | 5 | 2375 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | HV reconductoring from and including pole 794716 to 375502. | .
690 |  | JE24046356 | PARAPARA | Western | PARAPARA | 2025-02-04 | 9:10 | 2025-02-04 | 13:41 | 0.0067395 | 2.4831e-05 | 9 | 2443 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Low Voltage conductor between 783763 & 783757 | .
691 |  | JE24046699 | BETHLEHEM | Eastern | BETHLEHEM | 2025-02-04 | 10:04 | 2025-02-04 | 12:48 | 0.0018051 | 1.1036e-05 | 4 | 654 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install new Pole 3 on finished batter of new highway. Install new 11kV cable between Pole 1 and new Pole 3. Swing conductor that runs between pole 423843 (TD3-310) and pole 390332 across to new Pole 3. Remove pole 390332 and conductor between Pole 2 and pole 390332 | .
692 |  | JE25003754 | FUSES v44 River Road, Akitio | Western | COAST ROAD | 2025-02-04 | 19:35 | 2025-02-05 | 17:29 | 0.036274 | 2.759e-05 | 10 | 13148 | Unplanned | ADVERSE ENVIRONMENT - LAND SLIPPAGE | called fm twice no answer called hub to track down for update known HV issue FM confirmed Lines hanging low, Bank slipping from when Gabriel went through FM instructed to put urgent request through for repairs to be done Low Lines between Poles P01282 & P01283, line was only 2m away from the ground Line Isolated at Fuses V42, left isolated overnight Pole P01282 - Pole straightened Pole P01286 - Pole straightened, turned into a strain point, added staywire Pole P01283 - Replaced binders Line is now 6.65m high, other faults fixed, full power restored | .
693 |  | JE25003837 | 13 RAKAU ROAD,CASTLECLIFF,WANGANUI | Western | POLSON ST | 2025-02-04 | 20:44 | 2025-02-04 | 22:06 | 0.0030745 | 4.4143e-05 | 16 | 1114 | Unplanned | WILDLIFE - OTHER | Found fuses at Fuse/Sw 16037-4 Blown Isolated and Earthed Opened up cover around Cable to find Huge Rats Nest Isolated at Switch gear 16035-3 to clean out and check other bay which had nests in as well Cleaned all nests out Relived Sw/Gear 16035-3 Then Relived Fuse/Sw 16037-4 All good | .
694 |  | JE25003843 | unknown SPUR ROAD,Pongaroa,Rural | Western | TIRAUMEA | 2025-02-04 | 16:12 | 2025-02-04 | 18:36 | 0.00079344 | 5.5179e-06 | 2 | 288 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T9/263 No. Fuses: 2 Fuse Amp Size: 3a TIME CLOSED: 1836 Cause: lightning from xmas as not used much Weather (wind/rain): fine Follow up required (select advisory)? | .
695 |  | JE25003850 | 141 NGATAI ROAD,OTUMOETAI,TAURANGA | Eastern | BURETA RD | 2025-02-04 | 20:32 | 2025-02-04 | 22:14 | 0.0086554 | 8.5528e-05 | 31 | 3137 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | 19:53 - ETA 30mins from SMC - advised FENZ Car hit transformer TC4-019, transformer was isolated at Fuses SC4-300 so that fault crew could make temp repairs to the doors as no other damage to transformer was found. 2 R to remain open to replace the doors. 28/02 - Paul Cooper advised Transformer has been replaced 25/02 NAPA 119837 | .
696 |  | JE25003851 | TP STRATFORD - KAPONGA - CB2862 | Western | KAPONGA 33kV | 2025-02-04 | 20:00 | 2025-02-05 | 11:12 | 0.0040584 | 0.0018182 | 658 | 1471 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 33kv CB2862 Protection flags (nil where none): E/F CAUSE: Unknown Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): 2502004 on ABS 353 Circuit patrolled and type: cursory Weather (wind/rain): fine LFI (Y/N + Comments): lit at ABS 514 not lit at ABS 449 Follow up Required (select advisory)? Additional fault restoration comments: Going to Patrol Cross Country sections in Day light SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Kaponga, Circuit that tripped: CB 2862 DTF (KM): One jumper connection on ABS 353 found glowing red hot under load. ELT Sub offloaded to reduce load. Can be used to support CAR & KAA sub in an emergency. DNO 2502004 | .
697 |  | JE25003861 | 18 WAIINU BEACH ROAD,WAITOTARA,WANGANUI | Western | WAITOTARA | 2025-02-04 | 23:01 | 2025-02-05 | 2:31 | 0.0063828 | 3.0349e-05 | 11 | 2313 | Unplanned | WILDLIFE - BIRD | Found Lines down at Pole 774737 Goose under lines cooked up Isolated at fuses 2716 Repaired Lines Tested fine Relived | .
698 |  | JE25003866 | 22 OPAKU ROAD,PATEA,PATEA | Western | OTAUTU | 2025-02-04 | 22:42 | 2025-02-05 | 0:34 | 0.0012296 | 1.1036e-05 | 4 | 446 | Unplanned | WILDLIFE - BIRD | Fuses Location: LI160 LI155 No. Fuses: 1 2 Fuse Amp Size: 6 Amp 10 TIME CLOSED: 00-33 Cause: Bird Weather (wind/rain): Fine Follow up required (select advisory)? linked to job no JE25007251 | .
699 |  | JE25003867 | 1005 TAONUI ROAD,COLYTON,FEILDING | Western | POHANGINA | 2025-02-04 | 23:13 | 2025-02-05 | 10:21 | 0.15163 | 0.00034487 | 125 | 54958 | Unplanned | VEGETATION - OUTSIDE ZONE | Voltage & Device ID: Rec E33 Protection flags (nil where none): B & C Phase O/C Weather (wind/rain): Fine Follow up required (select advisory): n LFI Activation: N Line patrolled Big branch found on the lines past Pole P14735 Isolated at Fuses E36 Branch cut away from lines, Full power restored | .
700 |  | JE24045970 | MOTUMAOHO | Eastern | MOTUMAOHO | 2025-02-03 | 9:30 | 2025-02-03 | 11:24 | 0.0003148 | 2.759e-06 | 1 | 114 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace HV Pin Arm at pole 855855 | .
701 |  | JE24045975 | PATETONGA | Eastern | PATETONGA | 2025-02-03 | 9:01 | 2025-02-03 | 14:06 | 0.031179 | 0.00010208 | 37 | 11301 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV conductor between poles K13350 & K13359 with Ferret | .
702 |  | JE24046022 | PUTORINO | Western | PUTORINO | 2025-02-03 | 11:01 | 2025-02-03 | 14:31 | 0.00116 | 5.5179e-06 | 2 | 420 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Defected Transformer Z66 on pole 806947 | .
703 |  | JE24046111 | COLOGNE ST | Western | COLOGNE ST | 2025-02-03 | 9:31 | 2025-02-03 | 15:04 | 0.0082641 | 2.4831e-05 | 9 | 2995 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT: Re-sag conductors between poles 816699 - 845146. Clear vegetation at pole 816699 | .
704 |  | JE24046147 | MAIN RD MOTONUI | Western | MAIN RD MOTONUI | 2025-02-03 | 8:31 | 2025-02-03 | 15:50 | 0.1746 | 0.00039729 | 144 | 63286 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove 11kv lines from between poles 480403 & 743065, Job Overrun Cause , Tree Branches dropped onto line on Ground, Had to be Cleared. | .
705 |  | JE24046179 | POIKE | Eastern | POIKE | 2025-02-03 | 23:01 | 2025-02-04 | 1:20 | 0.036975 | 0.00026486 | 96 | 13402 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Upgrade maximum demand meters and current transformers for TD4-113 due to incorrect rating | .
706 |  | JE24046499 | OMANU | Eastern | OMANU | 2025-02-03 | 23:30 | 2025-02-04 | 2:19 | 0.011174 | 6.6215e-05 | 24 | 4050 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV RMU oil maintenance at S5824/S5826/S5828 | .
707 |  | JE25000758 | CARLTON AVE | Western | CARLTON AVE | 2025-02-03 | 8:30 | 2025-02-03 | 16:06 | 0.12233 | 0.0011063 | 246 | 44340 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install new CFCC 16180 and convert OH lines to UG from 769152-443188 & 769727-453155 | .
708 |  | JE25003549 | 3000 TAIRUA ROAD,PUKEPOTO,HIKUAI | Eastern | HIKUAI | 2025-02-03 | 0:13 | 2025-02-03 | 2:16 | 0.10009 | 0.00084148 | 305 | 36279 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 9643/2 Protection flags (nil where none): A - B Ø O/C CAUSE: Unknown Location: Unknown Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4, cursory patrolled Weather (wind/rain): rain LFI (Y/N + Comments): Yes at ABS IC333 Follow up Required (select advisory)? No Additional fault restoration comments: No fault cause was found SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
709 |  | JE25003557 | 9 MARSHALL ROAD,KATIKATI,KATIKATI | Eastern | WHARAWHARA ROAD | 2025-02-03 | 12:40 | 2025-02-03 | 15:25 | 0.0034277 | 2.2072e-05 | 8 | 1242 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Fuses Location: S4670 No. Fuses: 1 Fuse Amp Size: 30 TIME CLOSED: 12:35 - Failed Cause: Cable fault between Fuses S4670 & TFR T4601 Weather (wind/rain): calm Follow up required (select advisory)?n Isolated & Earthed at Fuses S4670 400V Cable break made at TFR T4601 Bushings ot - Generator installed 400 TFR TP1928 Isolator ort - Generator installed DNO - 2502001 | .
710 |  | JE25003734 | 129 LOWER PAKIHIKURA ROAD,WAITUNA WEST,HUNTERVILLE | Western | WAITUNA | 2025-02-03 | 23:37 | 2025-02-04 | 4:28 | 0.017608 | 0.00015726 | 41 | 6382 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kv Sec K54 Protection flags (nil where none): N/*A CAUSE: Trees in Lines Location: Beyond ABS K54 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): fine LFI (Y/N + Comments): no Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
711 |  | JE25003740 | 810 ,, | Western | LINTON | 2025-02-03 | 23:55 | 2025-02-04 | 1:26 | 0.015031 | 0.00021796 | 79 | 5448 | Unplanned | WILDLIFE - POSSUM | REGULATORY INFORMATION Voltage & Device ID: Sec 10901 Protection flags (nil where none): B Phase O/C E/F CAUSE: Opossum Location: Pole P03630 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Fine LFI (Y/N + Comments): No Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
712 |  | JE24045957 | WORKSOP RD | Western | WORKSOP RD | 2025-02-02 | 9:00 | 2025-02-02 | 10:57 | 0.00096343 | 8.2769e-06 | 3 | 349 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace cross arms and hardware at pole 833506 | .
713 |  | JE24045964 | CHAPEL ST | Eastern | CHAPEL ST | 2025-02-02 | 8:31 | 2025-02-02 | 10:53 | 0.018783 | 0.00013243 | 48 | 6808 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To carry out PD Tests and Cleaning Cable Terms on RMU 9018 | .
714 |  | JE24045966 | PALM SPRINGS | Eastern | PALM SPRINGS | 2025-02-02 | 23:30 | 2025-02-03 | 3:19 | 0.18678 | 0.00081389 | 295 | 67698 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kV oil maintenance - S6165/S6167/S6169/S6171 | .
715 |  | JE25000767 | GUYTON ST | Western | GUYTON ST | 2025-02-02 | 8:30 | 2025-02-02 | 14:59 | 0.021456 | 5.5179e-05 | 20 | 7777 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install new Entech load break switch and new earthing at pole 360184. Change LV crossarms to Pin arms. ABS 4191 will be removed. | .
716 |  | JE25003500 | 3 CLOTEN ROAD,STRATFORD,STRATFORD | Western | CLOTON RD SOUTH | 2025-02-02 | 0:01 | 2025-02-02 | 2:27 | 0.076844 | 0.0019064 | 691 | 27853 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: CB 3 Protection flags (nil where none): B Phase E/F CAUSE: Unknown But suspect Opossum Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Curse Weather (wind/rain): Fine LFI (Y/N + Comments): Nil Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
717 |  | JE25003524 | 2290 CARRINGTON ROAD,PUKEITI,NEW PLYMOUTH | Western | INLAND COAST | 2025-02-02 | 20:28 | 2025-02-03 | 15:32 | 0.0063123 | 5.5179e-06 | 2 | 2288 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Arcing Pole. Fire Service Attending Cause: Blown HV Cable Termination Location: Isolation: Fused ABS 6854 Cable Repaired & Relivened @ 15:32 3/02/25 Michael Balfour advised for Kordia, 021960525 | .
718 |  | JE25003525 | 36D PEAT STREET,WHANGANUI,WANGANUI | Western | WESTMERE PEAT ST | 2025-02-02 | 19:08 | 2025-02-03 | 3:06 | 0.23695 | 0.0032363 | 1173 | 85885 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV, CB 5 Protection flags (nil where none): E/F, O/C A-B-C phase CAUSE: Car vs Pole Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Calm LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Transformer X916 left off overnight due to probable HV/LV Clash. Staff to return in morning with inspector to test & liven properties Tests completed on 03/02/25 and supply restored. | .
719 |  | JE25003526 | unknown TURAKINA VALLEY ROAD,Turakina,Rural | Western | TUTAENUI | 2025-02-02 | 19:22 | 2025-02-02 | 20:57 | 0.013685 | 0.00014347 | 52 | 4960 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | REGULATORY INFORMATION Voltage & Device ID: Rec 4237 / Sec 4856 Protection flags (nil where none): A - B Ø O/C CAUSE: Tree branch on lines Location: Pole 794480 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Yes / Cursory Weather (wind/rain): Windy LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Branch removed using Hot Stick SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
720 |  | JE25003544 | 626 2 ,TE PUNA,TAURANGA | Eastern | WAIPUNA | 2025-02-02 | 22:16 | 2025-02-02 | 23:31 | 0.055133 | 0.0010263 | 372 | 19983 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 1 / GMCB 13128/4 Protection flags (nil where none): E/F B Ø CAUSE: Gum tree bark on line Location: Pole 213184 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4, cursory patrolled. Weather (wind/rain): Rain LFI (Y/N + Comments): yes at FABS SD3-147 Follow up Required (select advisory)? No Additional fault restoration comments: Gum bark found at pole 213184 and removed with hot stick. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
721 |  | JE24045960 | EVANS RD | Eastern | EVANS RD | 2025-02-01 | 23:30 | 2025-02-02 | 0:56 | 0.00023621 | 2.759e-06 | 1 | 86 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9159 | .
722 |  | JE25003463 | 427 CARDIFF ROAD,PEMBROKE,STRATFORD | Western | CARDIFF RD | 2025-02-01 | 9:18 | 2025-02-01 | 10:32 | 0.0093901 | 0.00012691 | 46 | 3403 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 12709 Protection flags (nil where none): B Phase E/F O/C CAUSE: Unknown See Notes Below Location: Unknown Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Fine LFI (Y/N + Comments): Not Flashing on site Follow up Required (select advisory)? Additional fault restoration comments: Report of Sparking Lines at 199 Monmoutrh Rd Which is not in the sec Area BUT Rec 12700 Did do Auto Reclose at That Time Maybe setting between The two reclosers need looking At | .
723 |  | JE25003478 | 877 OHANGAI ROAD,OHANGAI,HAWERA | Western | MEREMERE | 2025-02-01 | 11:54 | 2025-02-01 | 16:06 | 0.0042282 | 1.9313e-05 | 7 | 1533 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Transformer 5396E Blown Up Needs replacement Replaced Transformer Unknown Cause as was Pretty New Transformer Also Found 1 X 6amp H/T Fuse at Fuses WH261 Replaced at 16-06 | .
724 |  | JE25003484 | 252 BOYLAN ROAD,TE ROTI,HAWERA | Western | TE ROTI | 2025-02-01 | 16:51 | 2025-02-01 | 18:56 | 0.0038072 | 3.0349e-05 | 11 | 1380 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: 5987 2379T No. Fuses: 2 2 Fuse Amp Size: TIME CLOSED: Cause: Replaced Failed Transformer 2379T 3 phase 30kVA & 3 Complete D/Outs Pole 733525 Site Weather (wind/rain): Fine Follow up required (select advisory)?Transformer 2379T and DDOs for Transformer needed replacement so Opened Fuses 5987 at and Closed at | .
725 |  | JE24044699 | LINDERMANN RD | Eastern | LINDERMANN RD | 2025-01-31 | 8:45 | 2025-01-31 | 14:37 | 0.063993 | 0.00018209 | 66 | 23195 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv/400vt cross arms @ 204614,204640,204616,204617. Replace LV pole 204639. Isolation point @ SB1-001. | .
726 |  | JE24045101 | HOROEKA | Western | HOROEKA | 2025-01-31 | 8:30 | 2025-01-31 | 13:48 | 0.058829 | 0.00018485 | 67 | 21323 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT: Multiple FFT sites to repair beyond isolation V6 between poles P06443 - P06280. | .
727 |  | JE24045276 | PATETONGA | Eastern | PATETONGA | 2025-01-31 | 9:31 | 2025-01-31 | 15:50 | 0.038677 | 0.00010208 | 37 | 14019 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV poles between 860321 - K13359 | .
728 |  | JE24045427 | KOHETE RD | Western | KOHETE RD | 2025-01-31 | 9:00 | 2025-01-31 | 16:11 | 0.073578 | 0.00017106 | 62 | 26669 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove Temp ABS 147. Remove ABS 5325. | .
729 |  | JE24045573 | KAIPI RD | Western | KAIPI RD | 2025-01-31 | 8:54 | 2025-01-31 | 12:38 | 0.021666 | 9.6564e-05 | 35 | 7853 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace existing Pole 747326 with a Double Busck 12.5m and install a new Sectionaliser 12741/2 and new swing links 12741/4 | .
730 |  | JE24045967 | CENTRAL OTUMOETAI | Eastern | CENTRAL OTUMOETAI | 2025-01-31 | 23:31 | 2025-02-01 | 3:06 | 0.046322 | 0.0002152 | 78 | 16790 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9037/1/2/3 | .
731 |  | JE25000353 | MARANGAI | Western | MARANGAI | 2025-01-31 | 9:46 | 2025-01-31 | 13:50 | 0.029038 | 0.00011864 | 43 | 10525 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re-conductor 11kV between poles 774073 - 774048 & 468970 | .
732 |  | JE25003312 | 115 PUTIKI DRIVE,PUTIKI,WANGANUI | Western | MARANGAI | 2025-01-31 | 2:59 | 2025-01-31 | 5:02 | 0.07787 | 0.0011781 | 427 | 28224 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | REGULATORY INFORMATION Voltage & Device ID: REC 4261 Protection flags (nil where none): A & B phase EF CAUSE: blown jumper Location: Links 4261/4 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: cursory Weather (wind/rain): fine LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: | .
733 |  | JE25003313 | 309 BOWLER ROAD,OTWAY,TE AROHA | Eastern | SPRINGDALE | 2025-01-31 | 4:10 | 2025-01-31 | 7:41 | 0.041157 | 0.00069526 | 221 | 14917 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec RP04 Protection flags (nil where none): E/F CAUSE: Unknown Location: Unknown Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4, Cursory Patrolled Weather (wind/rain): Calm LFI (Y/N + Comments): Yes at ABS 516 Follow up Required (select advisory)? Yes Additional fault restoration comments: No visible fault was found, a temp line break was cut at pole C14107 and back fed to limit customer outage areas. | .
734 |  | JE25003331 | 263 FAIRFIELD ROAD,HAWERA,HAWERA | Western | MANAWAPOU RD | 2025-01-31 | 8:31 | 2025-01-31 | 10:19 | 0.00029636 | 2.759e-06 | 1 | 107 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: WH822 No. Fuses: 2 Fuse Amp Size: 8 TIME CLOSED: 1018 Cause: DETERIORATION Weather (wind/rain): FINE Follow up required (select advisory)? 2R USED REPLACE 2X BARRELS | .
735 |  | JE25003332 | 4408 SOUTH ROAD,OPUNAKE,OPUNAKE | Western | OAONUI | 2025-01-31 | 6:43 | 2025-01-31 | 8:28 | 0.0078266 | 7.4492e-05 | 27 | 2837 | Unplanned | WILDLIFE - BIRD | Fuses Location: TA718 No. Fuses: 2 Fuse Amp Size: 25a TIME CLOSED: 0828 Cause: bird strike Weather (wind/rain): fine Follow up required (select advisory)? | .
736 |  | JE25003352 | 17 BENNER ROAD,PUKEHINA,TE PUKE | Eastern | KAITUNA | 2025-01-31 | 8:15 | 2025-01-31 | 9:26 | 0.00038903 | 5.5179e-06 | 2 | 141 | Unplanned | WILDLIFE - BIRD | Fuses Location: TE7-154 No. Fuses: 2 Fuse Amp Size:2A TIME CLOSED: 0925 Cause: BIRD NEST Weather (wind/rain): FINE Follow up required (select advisory)? | .
737 |  | JE25003374 | 170 WAUGHS ROAD,BUNNYTHORPE,FEILDING | Western | BUNNYTHORPE | 2025-01-31 | 8:38 | 2025-01-31 | 10:11 | 0.00051381 | 5.5179e-06 | 2 | 186 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: T2-513 No. Fuses: 2 Fuse Amp Size:3A TIME CLOSED: 1010 Cause: UNKNOWN Weather (wind/rain): FINE Follow up required (select advisory)? | .
738 |  | JE25003407 | unknown MAIN DRAIN ROAD,Rangiotu,Rural | Western | TAIKOREA | 2025-01-31 | 13:41 | 2025-01-31 | 14:53 | 0.00079482 | 1.1036e-05 | 4 | 288 | Unplanned | WILDLIFE - BIRD | Fuses Location: B19 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 1452 Cause: BIRD STRIKE Weather (wind/rain): FINE Follow up required (select advisory)? 2R USED FOR NEW CANDLE STICK AND LINE PATROL | .
739 |  | JE25003420 | 30 HUNTER ROAD, ELTHAM | Western | MANGATOKI | 2025-01-31 | 15:10 | 2025-01-31 | 19:08 | 0.0026289 | 1.1036e-05 | 4 | 953 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Replace 2 x cross arms at Poles 731318 & 731613 | .
740 |  | JE25003432 | 1286B UPPER OHAUITI ROAD,OHAUITI,TAURANGA | Eastern | OHAUITI RD | 2025-01-31 | 18:01 | 2025-01-31 | 19:52 | 0.00061387 | 5.5179e-06 | 2 | 223 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: Fuses S6109P Protection flags (nil where none): None CAUSE: Car vs Transformer Pad Location: Transformer TP667-P Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): None Follow up Required (select advisory)? Additional fault restoration comments: -Job at wrong Transformer , should be TO667-P Isolated at Fuses S6109P and rebuild Transformer TP667-P Platform. No damage to Transformer Job left open to come back later and redo the platform, but full power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): No Circuit that tripped: N/A DTF (KM):N/A | .
741 |  | JE25003434 | 387 RANGE ROAD,PONGAROA,PONGAROA | Western | HOROEKA | 2025-01-31 | 16:26 | 2025-01-31 | 18:50 | 0.00039623 | 2.759e-06 | 1 | 144 | Unplanned | THIRD PARTY INTERFERENCE - VANDALISM/THEFT | Fuses Location: T9/21 No. Fuses: 2 Fuse Amp Size: 2A and 2 x barrels TIME CLOSED: 1850 Cause: Weather (wind/rain): Follow up required (select advisory)? Phil reports that a member of the public approached him while he was leaving. The person told Phil that there is a dispute between the landlord and the tenant and a Scanpower Ute came to the property and removed the HV links from Transformer T9/21. It is unrelated to this outage but trees are growing up through the LV and burning in the 11kV lines around Transformer T9/21. 2r to be left open to get tree workers in to remove trees. 21/03/2025 - Chris Naylor advised that they had applied for NAPA to complete tree trimming, the farmer now wants the lines and transformer to be removed. 2R to be cancelled and this is to be sorted out with CIWR team | .
742 |  | JE24045075 | RONGOTEA | Western | RONGOTEA | 2025-01-30 | 9:30 | 2025-01-30 | 14:30 | 0.0091 | 3.0349e-05 | 11 | 3298 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace pole P33929 and replace transformer T1/435 | .
743 |  | JE24045097 | HOROEKA | Western | HOROEKA | 2025-01-30 | 8:47 | 2025-01-30 | 15:57 | 0.079403 | 0.00018485 | 67 | 28780 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT: Multiple FFT sites to repair beyond isolation V6 between poles P06443 - P06280. | .
744 |  | JE24045303 | WELCOME BAY | Eastern | WELCOME BAY | 2025-01-30 | 23:29 | 2025-01-31 | 4:18 | 0.14339 | 0.00049661 | 180 | 51973 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - SD4-761/SD4-763/SD4-767/SD4-765 | .
745 |  | JE24045428 | OKOROIRE | Eastern | OKOROIRE | 2025-01-30 | 8:30 | 2025-01-30 | 15:50 | 0.060578 | 0.00013795 | 50 | 21957 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Shut Maintenance Pole sites Pole Replacement: TIRPUT072, TIRPUT073, TIRPUT074 & TIRPUT079. Cross-arm Replacement: TIRPUT075, TIRPUT076, TIRPUT085, TIRPUT100, TIRPUT101, TIRPUT111, TIRPUT107/M13295, 855251 & TIRPUT109. | .
746 |  | JE24045439 | SOUTH RD NGARIKI | Western | SOUTH RD NGARIKI | 2025-01-30 | 9:17 | 2025-01-30 | 14:39 | 0.014211 | 4.4143e-05 | 16 | 5151 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace poles 712744, 712745, 712746, 712747, 712748, 712749, 373489 & 373409 replace lv conductor with new pvc Kutu from pole 373489 to 712748 . replace lv conductor with new pvc kutu from pole 373409 to 373473. replace hv conductor with new bare kutu from pole 372225 to 369824 | .
747 |  | JE24045450 | OWERA RD | Eastern | OWERA RD | 2025-01-30 | 9:48 | 2025-01-30 | 16:00 | 0.0051418 | 1.3795e-05 | 5 | 1864 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Recloser 9226 with Tavrida switch. Upgrade site with Source Side & Load Side links and by-pass ABS. New Recloser will be SCADA commissioned while under the AP. | .
748 |  | JE24045575 | PARAPARA | Western | PARAPARA | 2025-01-30 | 9:00 | 2025-01-30 | 15:33 | 0.027775 | 0.00015174 | 55 | 10067 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace multiple poles & x-arms between poles 783762 & 783684 | .
749 |  | JE25002819 | RANGIURU ROAD, RANGIURU, TE PUKE, 3188 | Eastern | MANGOREWA | 2025-01-30 | 9:35 | 2025-01-30 | 13:42 | 0.0020369 | 8.2769e-06 | 3 | 738 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: What was replaced? Where was it replaced (pole/TX/pillar box)? Is 2R required? Y 2R Y - What is the timeframe for repairs? FM unsure - Possibly by next week 07/02/2025. Additional Info: Tx leaking and will be replaced under 2R. FM confirmed site is safe for now and they will organise for it to be repaired as it will require a shutdown. E00180 30/01/25 0930-1400 - see child job | .
750 |  | JE25003123 | 23 FLYGERS LINE,MILSON,PALMERSTON NORTH | Western | GEMINI | 2025-01-30 | 5:47 | 2025-01-30 | 9:07 | 0.1542 | 0.0046626 | 1382 | 55889 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 4 Protection flags (nil where none): E/F, O/C -Cph CAUSE: cable fault Location: Sw/Gear 10796/1 to T6/454 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): 2501014 Circuit patrolled and type: operational Weather (wind/rain): calm LFI (Y/N + Comments): Y Follow up Required (select advisory)? Yes - Sw/Gear 10079 would not operate via Scada needs to be looked at. Additional fault restoration comments: Temp cable break was made at transformer T6/454 towards Sw/Gear 10796/1. Transformer livened from Sw/Gear 10171/3. | .
751 |  | JE25003165 | 6255 STATE HIGHWAY 27, WALTON, WAHAROA, 3474 | Eastern | WARDVILLE | 2025-01-30 | 13:20 | 2025-01-30 | 13:40 | 0.00016926 | 8.2769e-06 | 3 | 61 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Excessive voltage (+255Volts) required tapping down 1 tap to correct. Tapped down to tap 2, Voltages - 237 to 240 across phases. AW | .
752 |  | JE24043472 | HEWLETTS RD | Eastern | HEWLETTS RD | 2025-01-29 | 22:00 | 2025-01-30 | 1:18 | 0.011449 | 5.7938e-05 | 21 | 4150 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - SC4-259/SC4-260/SC4-839/SC4-770/SC4-316/SC4-262 | .
753 |  | JE24044694 | LINDERMANN RD | Eastern | LINDERMANN RD | 2025-01-29 | 8:56 | 2025-01-29 | 15:04 | 0.057851 | 0.00015726 | 57 | 20968 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv/400vt cross arms @ 204502,204503,204504,204505,204506,204507 & 204508. Isolation point @ SB1-041. | .
754 |  | JE24045092 | TOTARA | Eastern | TOTARA | 2025-01-29 | 9:38 | 2025-01-29 | 12:04 | 0.0012072 | 8.2769e-06 | 3 | 438 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv Pole S12638 with new 11m Busk | .
755 |  | JE24045218 | PATETONGA | Eastern | PATETONGA | 2025-01-29 | 9:16 | 2025-01-29 | 15:23 | 0.037546 | 0.00010208 | 37 | 13609 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV poles between 879019-K1540 & K13374-K13384. | .
756 |  | JE24046383 | WAIHI BEACH RD | Eastern | WAIHI BEACH RD | 2025-01-29 | 10:03 | 2025-01-29 | 15:15 | 0.0025871 | 8.2769e-06 | 3 | 938 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Transformer pole TC2991 and replace 2 x stays P0106 & P0107 | .
757 |  | JE25000460 | CITY 10 | Western | CITY 10 | 2025-01-29 | 23:01 | 2025-01-30 | 4:16 | 0.22045 | 0.00070629 | 256 | 79902 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 751814 with a new B11. Replace ABS 343 with a new automated Sectionaliser (12795/2) and solid knife links (12795/4) | .
758 |  | JE25001099 | TAVERNER ST | Western | TAVERNER ST | 2025-01-29 | 9:23 | 2025-01-29 | 15:01 | 0.0037261 | 1.1036e-05 | 4 | 1351 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace existing 10kVA 3ph transformer with new 50kVA 3ph transformer on existing structure, upgrade existing transformer arms and earthing system as required. New 50kVA Tx fused at 6A. | .
759 |  | JE25002965 | unknown ROUTE 52 ,Pongaroa,Rural | Western | WAIONE | 2025-01-29 | 1:52 | 2025-01-29 | 10:21 | 0.15937 | 0.00039177 | 114 | 57763 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec V27 Protection flags (nil where none): E/F, O/C C CAUSE: cracked insulator Location: Pole P00484 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state o): Circuit patrolled and type: cursory Weather (wind/rain): calm LFI (Y/N + Comments): N/A Follow up Required (select advisory)? n Additional fault restoration comments: Main line fault, most of the line is cross country between Rec V27 & ABS V35, no back feed, faultman was going to get LFI's to put on the line to help find fault. | .
760 |  | JE25002967 | 8 WEST ROAD,MANGATAINOKA,PAHIATUA | Western | RUAWHATA | 2025-01-29 | 6:52 | 2025-01-29 | 9:57 | 0.035266 | 0.00019037 | 69 | 12782 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Line down at Pole P16399. Attempted to isolate at Fuses Q86 but one fuse has welded closed and cannot be opened. DNO 2501013. Extended outage area to move isolations back to REC Q81 & ABS Q85 to repair. | .
761 |  | JE25002996 | KAIHERE | Eastern | KAIHERE | 2025-01-29 | 9:57 | 2025-01-29 | 10:37 | 0.00064946 | 1.6554e-05 | 6 | 235 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Device 3653545 also known as TC2647. Offloaded to repair LV line down Cause: Corrosion What was replaced? LV conductor joint & connector. LV fuseholder & 63A fuse link Where was it replaced (pole/TX/pillar box)? Transformer TC2647 pole Is 2R required? Yes 2R Y - What is the timeframe for repairs? Complete Additional Info: HV offloade for safety. | .
762 |  | JE25003014 | 221 WESTERN LAKE ROAD, FEATHERSTON, 5773 | Western | REVANS ST | 2025-01-29 | 12:05 | 2025-01-29 | 12:31 | 6.9882e-05 | 2.759e-06 | 1 | 25 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | a bolt securing DTX T1028 Fuses has come loose Isolate the fuses and resecure holders maintaining MAD and reliven. | .
763 |  | JE25003016 | PONGAROA SUB - TIRAUMEA - PONGAROA/4 | Western | TIRAUMEA | 2025-01-29 | 10:52 | 2025-01-29 | 12:53 | 0.022558 | 0.00036418 | 132 | 8176 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: CB 4 Protection flags (nil where none): A & B phase OC CAUSE: Unknown Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Work taking place under CAC 118333-3. Check crew and all OK, no one near the times. Tree workers stood down while switching. Sectionalised feeder, restored and advised tree workers to continue work. | .
764 |  | JE25003052 | WAVERLY SUB - RANGIKURA - REC 1112/2 | Western | RANGIKURA | 2025-01-29 | 13:01 | 2025-01-31 | 13:51 | 0.026195 | 0.00018761 | 68 | 9494 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: REC 1112 Protection flags (nil where none): B phase EF CAUSE: line down on private line Location: Pole 852890 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): calm LFI (Y/N + Comments): Nil Follow up Required (select advisory)? Additional fault restoration comments: Line is privately owned and is in need of a major rebuild. Open TLB at Pole 771570 to isolate the private line. Crew advised customer who will organise the work. Will need a Assurance for work and a advertised shutdown to close TLB | .
765 |  | JE25003076 | 80 WIKITORIA ROAD,WHANGANUI AIRPORT,WANGANUI | Western | MARANGAI | 2025-01-29 | 16:41 | 2025-01-29 | 18:23 | 0.023681 | 0.00040005 | 145 | 8583 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolate at ABS 566 to replace 3 x Fuses at FABS 2971 | .
766 |  | JE25003078 | 66 DUDDINGS LINE,TAUHERENIKAU,FEATHERSTON | Western | DAIRY FACTORY | 2025-01-29 | 17:40 | 2025-01-29 | 20:27 | 0.0041558 | 2.4831e-05 | 9 | 1506 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: DTX T979 3 Phase 50kVA CAUSE: Failed?? Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: Weather (wind/rain): Fine Follow up required (select advisory)? Additional fault restoration comments: | .
767 |  | JE25003113 | 663 MAIN DRAIN ROAD,RANGIOTU,PALMERSTON NORTH | Western | TAIKOREA | 2025-01-29 | 20:44 | 2025-01-29 | 22:29 | 0.010936 | 0.00010484 | 38 | 3964 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: B12 No. Fuses: 2 Fuse Amp Size: 15 TIME CLOSED: 22:28 Cause: unknown Weather (wind/rain): calm Follow up required (select advisory)?n Line Patrolled | .
768 |  | JE25003120 | 720 FLETCHER BAY ROAD,FLETCHER BAY,COROMANDEL | Eastern | COLVILLE | 2025-01-29 | 22:55 | 2025-01-30 | 3:05 | 0.0024191 | 7.1733e-05 | 26 | 877 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: SWER Line Protection flags (nil where none): Nil CAUSE: Lead off Fuses FC1474 Location: Fuses FC1474 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Curse Weather (wind/rain): Calm LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Blown Fuse @ Fuses 9927/4 Replaced @ 03:05 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
769 |  | JE24045034 | PARK RD | Western | PARK RD | 2025-01-28 | 9:15 | 2025-01-28 | 13:15 | 0.0046277 | 1.9313e-05 | 7 | 1677 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re-sag 11kv conductors at multiple sites from 11kv fuses 7172 to pole 841901 | .
770 |  | JE24045161 | POHANGINA | Western | POHANGINA | 2025-01-28 | 8:50 | 2025-01-28 | 11:12 | 0.064859 | 0.00045799 | 166 | 23508 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Collect oil sample from regulator 10081 | .
771 |  | JE24045391 | PROSPECT ST | Eastern | PROSPECT ST | 2025-01-28 | 8:31 | 2025-01-28 | 14:46 | 0.034141 | 9.1046e-05 | 33 | 12374 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Shut 5 Maintenance Pole sites. Pole Replacement: TIRPUT044, TIRPUT047, TIRPUT059, TIRPUT051 & TIRPUT065. Cross-arm Replacement: TIRPUT042, D12345, M13520, TIRPUT061, TIRPUT060, and TIRPUT043. | .
772 |  | JE24045414 | SOUTH RD NGARIKI | Western | SOUTH RD NGARIKI | 2025-01-28 | 8:46 | 2025-01-28 | 15:19 | 0.01735 | 4.4143e-05 | 16 | 6289 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace poles 712729, 712731, 712733, 712734, 712735, 712736, 712737, 712739, 712740, 712741 & 712743 38 Lower Kina Road Left off after shutdown due to meter being inside the premises, unable to test. | .
773 |  | JE24045438 | LINTON | Western | LINTON | 2025-01-28 | 10:15 | 2025-01-28 | 11:21 | 0.0028855 | 4.4143e-05 | 16 | 1046 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace insulator at pole P03610 | .
774 |  | JE24045571 | PARAPARA | Western | PARAPARA | 2025-01-28 | 9:15 | 2025-01-28 | 16:12 | 0.032156 | 7.7251e-05 | 28 | 11655 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace multiple poles & x-arms between poles 783762 & 783684 | .
775 |  | JE24045708 | 26 HENDERSON STREET, KIMBOLTON | Western | RANGIWAHIA | 2025-01-28 | 11:18 | 2025-01-28 | 11:25 | 0.00018899 | 2.759e-05 | 10 | 69 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Chris Naylor to return tomorrow and they may tap transformer depending on Results. Chris has spoken to property owner who wants to install solar. He will put in a shutdown application to lower Tap Setting 28/01/25 - TFR T5/261 tapped down under JE25002801 | .
776 |  | JE24046200 | KOHETE RD | Western | KOHETE RD | 2025-01-28 | 9:01 | 2025-01-28 | 14:58 | 0.013786 | 3.8625e-05 | 14 | 4997 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Xarms from poles 760188 to 760197. Install 30kVA duel Tx at 3305T & 4882T | .
777 |  | JE25002301 | AOKAUTERE | Western | AOKAUTERE | 2025-01-28 | 10:00 | 2025-01-28 | 14:21 | 0.01221 | 4.6902e-05 | 17 | 4426 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT: Replace insulators & rusted hardware on poles P21365, P21363 & P21362 & replace crossarm at P21411 | .
778 |  | JE25002786 | 511B KINA ROAD,OAONUI,OPUNAKE | Western | SOUTH RD NGARIKI | 2025-01-28 | 8:21 | 2025-01-28 | 10:19 | 0.00064771 | 5.5179e-06 | 2 | 235 | Unplanned | WILDLIFE - BIRD | Fuses Location: ng381 No. Fuses: 2 Fuse Amp Size: 2a TIME CLOSED: 1018 Cause: Bird strike Weather (wind/rain): fine Follow up required (select advisory)? n/a | .
779 |  | JE25002855 | 12 OPUA ROAD,TURUA,NGATEA | Eastern | HAURAKI RD | 2025-01-28 | 12:15 | 2025-01-28 | 13:10 | 0.0018238 | 3.3108e-05 | 12 | 661 | Unplanned | WILDLIFE - BIRD | Fuses Location: FP1996 No. Fuses: 2 Fuse Amp Size: 10a TIME CLOSED: 1310 Cause: Bird strike Weather (wind/rain): Fine Follow up required (select advisory)? | .
780 |  | JE25002900 | 1325 HAURAKI ROAD,NETHERTON,PAEROA | Eastern | HAURAKI RD | 2025-01-28 | 18:00 | 2025-01-28 | 19:51 | 0.0012226 | 1.1036e-05 | 4 | 443 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Faultman found jumper had come out of sleeve and DDO's damaged on transformer TC3993. Line was isolated at Fuses FC1167 to replace a full set of DDO's and line had to be resag to transformer to refasten jumpers. | .
781 |  | JE25002917 | 72 BENNER ROAD,PUKEHINA,TE PUKE | Eastern | OTAMARAKAU | 2025-01-28 | 16:03 | 2025-01-28 | 19:20 | 0.0010864 | 5.5179e-06 | 2 | 394 | Unplanned | WILDLIFE - BIRD | Fuses Location: SE7-034 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 19:20 Cause: Duck Strike Weather (wind/rain): calm Follow up required (select advisory)? | .
782 |  | JE24044996 | PARK RD | Western | PARK RD | 2025-01-27 | 8:45 | 2025-01-27 | 15:25 | 0.0022066 | 5.5179e-06 | 2 | 800 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles on swer line past T332 | .
783 |  | JE24045108 | WESTMERE PEAT ST | Western | WESTMERE PEAT ST | 2025-01-27 | 9:31 | 2025-01-27 | 13:07 | 0.028583 | 0.00013243 | 48 | 10360 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace multiple 11KV Defected X-arms 774555, 774554, 774552 & 774420 | .
784 |  | JE25002622 | 28 COULTERS LINE,KIWITEA,FEILDING | Western | WAITUNA | 2025-01-27 | 2:41 | 2025-01-27 | 5:44 | 0.02175 | 0.00011864 | 43 | 7883 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Fuses P10 Protection flags (nil where none): None CAUSE: Burnt Cross arm Location: Pole P19667 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Light Rain LFI (Y/N + Comments): None Follow up Required (select advisory)? No Additional fault restoration comments: Replaced cross arm at Pole P19667 under Access Permit and 30A Fuse Power restored @ 05:43Hrs This job could be the cause of the Earlier feeder fault which tripped CB 7 (JE25002616) on 26/01/25. Faultman could have failed to see the hanging Fuses at Fuses P10and power restored to the feeder with customers Past Fuses P10 left single phasing | .
785 |  | JE25002624 | 309 BOWLER ROAD,OTWAY,TE AROHA | Eastern | SPRINGDALE | 2025-01-27 | 2:09 | 2025-01-27 | 9:12 | 0.068294 | 0.0011339 | 221 | 24753 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec RP04 Protection flags (nil where none): EF 1 CAUSE: Unknown, Suspect Failed Insulator in ABS 561 section Location: Fault Past ABS 561 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Opp patrolled nothing found Weather (wind/rain): Rain in morning cleared up and fault disappeared. LFI (Y/N + Comments): Yes Pole C14028 & C14104 Follow up Required (select advisory)? No Additional fault restoration comments: | .
786 |  | JE25002645 | 4 ,, | Eastern | LINDERMANN RD | 2025-01-27 | 11:23 | 2025-01-27 | 14:43 | 0.00827 | 4.1384e-05 | 15 | 2998 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuse was blown @ SB2-073, Relivened & Fuse Blew again, Cable Isolated & Tested , All OK ? Relivened all OK again?? Unknown why! | .
787 |  | JE25002654 | 1077D WILTSDOWN ROAD,KINLEITH,PUTARURU | Eastern | WAOTU | 2025-01-27 | 9:12 | 2025-01-27 | 12:06 | 0.0057706 | 3.3108e-05 | 12 | 2092 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: FP713 No. Fuses: 2 Fuse Amp Size: 15 TIME CLOSED: 1206 Cause: line clash from wind Weather (wind/rain): windy Follow up required (select advisory)?n/a | .
788 |  | JE25002673 | 333 WAITAO ROAD,WAITAO,TAURANGA | Eastern | BRUCE RD | 2025-01-27 | 10:36 | 2025-01-27 | 11:51 | 0.0014382 | 1.9313e-05 | 7 | 521 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | Fuses Location: SD5-137 No. Fuses: 2 Fuse Amp Size: 6a TIME CLOSED: 11:50 Cause: Tree branch Weather (wind/rain): windy Follow up required (select advisory)? N/A | .
789 |  | JE25002682 | 68 HACKETTS ROAD,ASHHURST,PALMERSTON NORTH | Western | ASHHURST | 2025-01-27 | 11:32 | 2025-01-27 | 14:05 | 0.00042382 | 2.759e-06 | 1 | 154 | Unplanned | WILDLIFE - BIRD | Fuses Location: 10778 No. Fuses: 2 Fuse Amp Size: 15A TIME CLOSED: 1405 Cause: Ducks Weather (wind/rain): windy Follow up required (select advisory)? | .
790 |  | JE25002694 | FEEDER FAULT - PONGAROA SUB - TIRAUMEA - CB4 | Western | TIRAUMEA | 2025-01-27 | 13:15 | 2025-01-27 | 13:22 | 0.0025278 | 0.00036418 | 132 | 916 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV, CB 4 Protection flags (nil where none): HLT, O/C A & C phase CAUSE: End of cut tree branch contacted 11kV lines. Workers working under CAC118333-01 at the time with safety measures applied. Location: Betwwen Poles P03282 & P00496 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: N/A Weather (wind/rain): Windy LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Tree Contractors stood down during feeder relivening and then continued with work as planned SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
791 |  | JE25002703 | 37 PINEDALE ROAD, LICHFIELD, PUTARURU, 3482 | Eastern | LICHFIELD | 2025-01-27 | 14:18 | 2025-01-27 | 18:56 | 0.003072 | 1.1036e-05 | 4 | 1113 | Unplanned | VEGETATION - INSIDE ZONE | Faultman found lines down due to a tree through the lines pole M13048, line was isolated at Fuses FP568 to repair the lines. | .
792 |  | JE25002705 | 1027 MANGAEHU ROAD,PUNIWHAKAU,STRATFORD | Western | STRATHMORE | 2025-01-27 | 13:51 | 2025-01-27 | 17:40 | 0.0069383 | 3.0349e-05 | 11 | 2515 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: Fuses 5453 No. Fuses: 2 Fuse Amp Size: 8A TIME CLOSED: Cause: 17:39 Weather (wind/rain): Wind Follow up required (select advisory)?No | .
793 |  | JE25002706 | BROOKLAND SUB - JUNCTION RD - 6777/5 | Western | JUNCTION RD | 2025-01-27 | 13:52 | 2025-01-27 | 17:27 | 0.10119 | 0.001545 | 560 | 36678 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 6777 / 5 Protection flags (nil where none): B - C - Ground CAUSE: Tree Branch Through Line Location: Between Pole 752492 & 752493 Temp generation (state details when used): NIL PERFORMANCE DETAIL DNO (number or state No): NIL Circuit patrolled and type: Cursory Weather (wind/rain): Fine LFI (Y/N + Comments): NIL Follow up Required (select advisory)? NIL Additional fault restoration comments: Centre Phase - was phase that broke | .
794 |  | JE25002711 | 206 MANGARERE ROAD,MANGAWEKA,MANGAWEKA | Western | MANGAWEKA | 2025-01-27 | 14:17 | 2025-01-27 | 19:20 | 0.0058666 | 1.9313e-05 | 7 | 2126 | Unplanned | VEGETATION - OUTSIDE ZONE | Fuses Location: Fuses 926 No. Fuses: 3 Fuse Amp Size: 6A TIME CLOSED: 19:20 Cause: Trees touching lines, (removed) Weather (wind/rain): Windy Follow up required (select advisory)?No | .
795 |  | JE25002721 | 5890 MOUNTAIN ROAD,NORMANBY,HAWERA | Western | CAMBRIA LS | 2025-01-27 | 16:41 | 2025-01-27 | 17:48 | 0.0024108 | 3.5867e-05 | 13 | 874 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Broken DDO Lead at Transformer C6506 - DDOs are at end of life - Outage to replace all 11kV Fuses and holders. | .
796 |  | JE25002735 | 699 KAUAERANGA VALLEY ROAD,THAMES,THAMES | Eastern | TOTARA | 2025-01-27 | 15:42 | 2025-01-27 | 17:18 | 0.0037095 | 3.8625e-05 | 14 | 1345 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | SWER Recloser 9930/2 Open Line Patrolled Nothing obvious seen , Suspect a Magpie Caused Power Restored 17:18 | .
797 |  | JE25002824 | 26 CAPAMAGIAN DRIVE, ATHENREE, KATIKATI, 3177 | Eastern | ATHENREE | 2025-01-27 | 13:14 | 2025-01-27 | 15:08 | 0.0069754 | 8.001e-05 | 29 | 2528 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Reconnect new 11kv cable at Line breaks Link Box SA2-030 & Transformer TA2-157 Note: DNO 2501010 | .
798 |  | JE25002517 | 247 OTAHU ROAD,WHANGAMATA,WHANGAMATA | Eastern | OTAHU RD | 2025-01-26 | 0:04 | 2025-01-26 | 4:52 | 0.44406 | 0.0015423 | 559 | 160952 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 9813 Protection flags (nil where none): E/F CAUSE: Brocken fuse holder at fuses FP1726 Location: Pole 861257 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Rain LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Full set replaced | .
799 |  | JE25002521 | 101 DUDLEY ROAD LOWER,INGLEWOOD,INGLEWOOD | Western | BROOKES ST | 2025-01-26 | 0:35 | 2025-01-26 | 5:49 | 0.06965 | 0.0026155 | 948 | 25245 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB I61 Protection flags (nil where none): B & C ph O/C & E/F CAUSE: Burnt cross arm Location: 763277 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: Cursory Weather (wind/rain): rain LFI (Y/N + Comments): Y - Sw/Gear 12416/1 & 3 Follow up Required (select advisory)? Additional fault restoration comments: Line was isolated at Sw/Gear 12416/3 & Links 12537/4 to replace burnt cross arm & hardware due to conductor on cross arm. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
800 |  | JE25002523 | 22 BREWER ROAD,STRATHMORE,STRATFORD | Western | STRATHMORE | 2025-01-26 | 1:30 | 2025-01-26 | 9:01 | 0.25727 | 0.00084976 | 264 | 93249 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 7131 Protection flags (nil where none): E/F, O/C B CAUSE: Broken binder/floating conductor Location: Pole 708959 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): wind, rain LFI (Y/N + Comments): n Follow up Required (select advisory)? Additional fault restoration comments: Line patrolled, Broken binder found at Pole 708959 Isolated at Fuses 5274 Broken binder replaced, full power restored Unable to to remotely put backfeed in place from Gas/Sw 12669/2 as the new Genset look like it has been left in test mode SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
801 |  | JE25002529 | 17 CARRINGTON STREET,NEW PLYMOUTH,NEW PLYMOUTH | Western | CITY 6 | 2025-01-26 | 4:47 | 2025-01-26 | 5:35 | 0.11045 | 0.0022955 | 832 | 40033 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 6 Protection flags (nil where none): O/C CAUSE: Branch on lines Location: 473350 & 473351 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: Cursory Weather (wind/rain): rain LFI (Y/N + Comments): N Follow up Required (select advisory)? Additional fault restoration comments: Branch removed with hot line sticks. | .
802 |  | JE25002530 | 254 SOMERVILLE ROAD,TAPAPA,TIRAU | Eastern | RANGITANUKU RD | 2025-01-26 | 4:55 | 2025-01-26 | 6:25 | 0.0012325 | 1.3795e-05 | 5 | 447 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: FP584 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 06:24 Cause: Patrolled/ Lightning Weather (wind/rain): Rain Follow up required (select advisory)? No | .
803 |  | JE25002534 | 5793 TURAKINA VALLEY ROAD,HUNTERVILLE,HUNTERVILLE | Western | HUNTERVILLE 22KV | 2025-01-26 | 6:27 | 2025-01-26 | 9:41 | 0.0016064 | 8.2769e-06 | 3 | 582 | Unplanned | WILDLIFE - POSSUM | Line patrolled, dead possum found at the bottom of Pole 810297 (TFR X2522) Fuses Location: X2522 No. Fuses: 2 Fuse Amp Size: 2 TIME CLOSED: 09:20 Cause: Possum at TFR X2522 Weather (wind/rain): wind, rain Follow up required (select advisory)?n Fuses Location: 1460 No. Fuses: 1 Fuse Amp Size: 8 TIME CLOSED: 09:40 Cause: Possum at TFR X2522 Weather (wind/rain): wind, rain Follow up required (select advisory)?n | .
804 |  | JE25002535 | 110 OLD COACH ROAD,KAIMARAMA,WHITIANGA | Eastern | COROGLEN | 2025-01-26 | 6:29 | 2025-01-26 | 11:01 | 0.0015006 | 5.5179e-06 | 2 | 544 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: TC5075 No. Fuses: 2 Fuse Amp Size: 2 TIME CLOSED: 11:01 Cause: Lightning Weather (wind/rain): Follow up required (select advisory)? | .
805 |  | JE25002536 | 25 HASZARD STREET,WAIHI,WAIHI | Eastern | KENNY ST | 2025-01-26 | 6:33 | 2025-01-26 | 11:10 | 0.13312 | 0.00063456 | 230 | 48251 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV GMCB 9967/4 pole 872926 Tree on line Protection flags (nil where none): O/C Inverse Time CAUSE: Tree on Lines Location: Pole 872926 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): no Circuit patrolled and type: Cursory Weather (wind/rain): High Winds & Lightning LFI (Y/N + Comments): no Follow up Required (select advisory)? Additional fault restoration comments: Tree Cut totally away from lines!! | .
806 |  | JE25002538 | 25 FARRELLY ROAD,WAIKINO,WAIHI | Eastern | WAITAWHETA | 2025-01-26 | 7:03 | 2025-01-26 | 9:20 | 0.0015102 | 1.1036e-05 | 4 | 547 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: dtx No. Fuses: 3 Fuse Amp Size: 2 TIME CLOSED: 09:19 Cause: Lightning Weather (wind/rain): Follow up required (select advisory)? | .
807 |  | JE25002551 | TE PUKE SUB - MANGOREWA - 14599/2 | Eastern | MANGOREWA | 2025-01-26 | 8:56 | 2025-01-26 | 14:14 | 0.06197 | 0.00054352 | 197 | 22461 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV Recloser 14599 Protection flags (nil where none): A,B, O/C CAUSE: Tree through Lines @ TF6-074 Pole 387998 Location: @ TF6-074 Pole 387998 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Rung In Weather (wind/rain): High wind gusts & Lightning LFI (Y/N + Comments): Yes Follow up Required (select advisory)? Additional fault restoration comments: | .
808 |  | JE25002555 | JE25002535 - 251 COACH ROAD,KAIMARAMA,WHITIANGA | Eastern | COROGLEN | 2025-01-26 | 11:28 | 2025-01-26 | 16:30 | 0.00083275 | 2.759e-06 | 1 | 302 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: 1 Phase 10kVA TC4985 Failed Replaced with 15kVA CAUSE: Lightning Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Cursory Weather (wind/rain): Lightning Follow up required (select advisory)? No Additional fault restoration comments: | .
809 |  | JE25002559 | 149 COACH ROAD,KAIMARAMA,WHITIANGA | Eastern | COROGLEN | 2025-01-26 | 11:21 | 2025-01-26 | 14:01 | 0.00044015 | 2.759e-06 | 1 | 160 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: 11kV 1 Phase 10kVA TC4884 replace with 15kVA CAUSE: Lightning Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Cursory Weather (wind/rain): Lightning Follow up required (select advisory)? No Additional fault restoration comments: | .
810 |  | JE25002561 | INGLEWOOD SUB - KAIMATA - 12690/2 | Western | KAIMATA | 2025-01-26 | 10:01 | 2025-01-26 | 12:49 | 0.017561 | 0.00020968 | 56 | 6365 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 12690/2 Protection flags (nil where none): E/F, O/C C CAUSE: Broken insulator due to old age Location: 761437 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): wind, rain LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Line patrolled, broken insulator found at pole 761437 due to old age Isolated at ABS 5515, 12690/1 & Links 12690/6, back feed put in place Broken insulator replaced, full power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
811 |  | JE25002565 | PEAT ST SUB - COLLEGE - PEATST/6 | Western | COLLEGE | 2025-01-26 | 10:35 | 2025-01-26 | 12:32 | 0.17371 | 0.0017078 | 619 | 62961 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 6 Protection flags (nil where none): O/C A & B CAUSE: Bird strike Location: 705414 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): wind, rain LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Feeder tripped, HLT was applied for LLP118245-01, contractor contacted, they where removing coverup gear and packing up at the time of the trip Line patrolled, dead bird found at the base of Pole 705414, Bird had landed on the cable crucifix below the Fuses to TFR X4375 2 x 15A Fuses re-loaded for TFR X4375, Full power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
812 |  | JE25002568 | 93 MANUTAHI ROAD, BELL BLOCK, NEW PLYMOUTH | Western | KATERE 5 | 2025-01-26 | 11:47 | 2025-01-26 | 16:26 | 0.0032955 | 3.3108e-05 | 12 | 1194 | Unplanned | VEGETATION - OUTSIDE ZONE | Palm trees leaf fell onto the lines, burning them down between Poles 746499 (Fuses 4860) & 746501 Isolated & Earthed at Fuses 4860, AP -01 issued to cut trees past Fuses 4860 Isolated at ABS 386 & Links 12251/6, AP-02, issued to fix/reconnect lines down from Fuses 4860 Lines repaired, full power restored | .
813 |  | JE25002576 | 106 COACH ROAD,KAIMARAMA,WHITIANGA | Eastern | COROGLEN | 2025-01-26 | 11:26 | 2025-01-26 | 19:22 | 0.0026232 | 5.5179e-06 | 2 | 951 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: Fuses FC991, Failed transformer TC6253, replace with 15kVA 1 phase CAUSE: Lightning Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Cursory Weather (wind/rain): Lightning Follow up required (select advisory)? No Additional fault restoration comments: | .
814 |  | JE25002578 | TAIRUA SUB - HIKUAI - 9643/2 | Eastern | HIKUAI | 2025-01-26 | 11:52 | 2025-01-26 | 18:09 | 0.036904 | 0.00025107 | 54 | 13376 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Sec 9787 Protection flags (nil where none): CAUSE: A, C, O/C Location: Pole U0577 Rotten Crossarm Failed Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Curse Weather (wind/rain): High Winds & Lightning LFI (Y/N + Comments): Yes Pole 942960 Follow up Required (select advisory)? Additional fault restoration comments: Links, so break before make required | .
815 |  | JE25002586 | 192 NGATIRA ROAD,LICHFIELD,PUTARURU | Eastern | LICHFIELD | 2025-01-26 | 14:48 | 2025-01-26 | 21:00 | 0.0051294 | 1.3795e-05 | 5 | 1859 | Unplanned | VEGETATION - OUTSIDE ZONE | Tree thorough the lines Pole M12259. Isolated at Fuses FC2168 to allow repairs. Possible 11kV /400V Clash inspection carried out at customers premises before reliveneing. All house relivened | .
816 |  | JE25002609 | 1E TAUPO QUAY,WHANGANUI,WANGANUI | Western | BASTIA HILL | 2025-01-26 | 17:03 | 2025-01-26 | 18:56 | 0.11743 | 0.001396 | 506 | 42562 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 11 Protection flags (nil where none): E/F, O/C A CAUSE: Faulty Insulator Location: Pole 767423 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: Cursory Weather (wind/rain): Rain LFI (Y/N + Comments): Yes @Sw/Gear 4869/2 Follow up Required (select advisory)? No Additional fault restoration comments: Insulator replaced under Access Permit, Power ON 18:55Hrs | .
817 |  | JE25002616 | 2810 KIMBOLTON ROAD,KIMBOLTON,FEILDING | Western | WAITUNA | 2025-01-26 | 20:10 | 2025-01-26 | 22:20 | 0.13805 | 0.0018844 | 683 | 50036 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: CB 7 Protection flags (nil where none): EF CAUSE: Unknown Location: N/A Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: Cursory Weather (wind/rain): Light Rain LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Line patrolled, sectionalised, nothing Found and power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): No Circuit that tripped: N/A DTF (KM):N/A | .
818 |  | JE25002619 | 53 ROTOKOHU ROAD,PAEROA,PAEROA | Eastern | TIROHIA-KARANGAHAKE | 2025-01-26 | 21:09 | 2025-01-26 | 22:46 | 0.017887 | 0.00037798 | 137 | 6483 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 3 Protection flags (nil where none): A,B,C Fault O/C CAUSE: Patrolled no fault found Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): Rain LFI (Y/N + Comments): Yes Pole 876695 Follow up Required (select advisory)? No Additional fault restoration comments: ABR schemes operated. | .
819 |  | JE25002490 | 1456 RANGITATAU EAST ROAD,PAPARANGI,WANGANUI | Western | WESTMERE PEAT ST | 2025-01-25 | 6:44 | 2025-01-25 | 14:11 | 0.049389 | 0.00011036 | 40 | 17901 | Unplanned | THIRD PARTY INTERFERENCE - TREES | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 1026 Protection flags (nil where none): E/F, O/C C CAUSE: Lines down due to tree being dropped through the line Location: between Poles 450198 to 784205 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): calm LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: faultman patrolled the line and found that a tree had been dropped through the lines between Poles 450198 & 784205 (Forestry contractor, NDR) Line isolated at ABS 1026/1 & Links 1026/6 Trees cleared away from lines, Lines repaired, full power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
820 |  | JE25002500 | 6 LESLIE ROAD,TAPAPA,PUTARURU | Eastern | TAUMANGI RD | 2025-01-25 | 11:01 | 2025-01-25 | 12:17 | 0.0084773 | 0.00011036 | 40 | 3073 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV HV Connection Failed Protection flags (nil where none): CAUSE: Failed Figure 6 / EPO Compression Connection Location: Pole M13438 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Windy LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: | .
821 |  | JE25002515 | 205 LOWER STUART ROAD,ELTHAM,HAWERA | Western | MANGATOKI | 2025-01-25 | 22:48 | 2025-01-26 | 0:18 | 0.00074572 | 8.2769e-06 | 3 | 270 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 5859 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 00:18 Cause: unknown Weather (wind/rain): rain Follow up required (select advisory)? | .
822 |  | JE25002522 | 3264 SOUTH ROAD,PIHAMA,OPUNAKE | Western | PIHAMA | 2025-01-25 | 23:55 | 2025-01-26 | 17:18 | 0.065743 | 0.00033108 | 120 | 23829 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 12194/2 Protection flags (nil where none): NIL - non Scada CAUSE: Car vs pole Location: 459205 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: operational Weather (wind/rain): rain LFI (Y/N + Comments): N Follow up Required (select advisory)? n Additional fault restoration comments: Line patrolled Line isolated at ABS TA801 & 8831/1. Crew will return in morning to replace transformer pole and rebind in line either side of hit pole. (Power works called in to complete repairs) Replaced Pole 459205 & TFR 5023E, Replaced broken cross arm and hardware at pole 718159, Replaced 1 x broken insulator at Pole 718161, Re-bind conductor back insulators at Poles 718160 & 718163 Fix Lines down between Poles 718161 & 718159 Full power restored | .
823 |  | JE24044401 | HAURAKI RD | Eastern | HAURAKI RD | 2025-01-24 | 9:20 | 2025-01-24 | 13:54 | 0.033355 | 0.00012139 | 44 | 12090 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv and 400v Xarms/Hardware at Pole's 873303,873342,873350,O12716,O12718,872916,O1241. Replace 11kv Pole O1233 | .
824 |  | JE24044695 | TUTAENUI | Western | TUTAENUI | 2025-01-24 | 9:23 | 2025-01-24 | 14:41 | 0.016691 | 5.242e-05 | 19 | 6050 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace defected poles 802952, 802958 & 802959 | .
825 |  | JE24044726 | LINTON | Western | LINTON | 2025-01-24 | 8:33 | 2025-01-24 | 15:05 | 0.053005 | 0.00013519 | 49 | 19212 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT - Multiple sites for vegetation and re-sagging conductors. Replace pole P01625 | .
826 |  | JE24044732 | PARK RD | Western | PARK RD | 2025-01-24 | 9:18 | 2025-01-24 | 13:22 | 0.0026957 | 1.1036e-05 | 4 | 977 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re-sag 11kv conductors at multiple sites from 11kv fuses 7171 to pole 841594 | .
827 |  | JE24044989 | PARK RD | Western | PARK RD | 2025-01-24 | 9:28 | 2025-01-24 | 14:47 | 0.00088107 | 2.759e-06 | 1 | 319 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace ABS S363 & hardware on pole 823859 | .
828 |  | JE24045060 | KOHETE RD | Western | KOHETE RD | 2025-01-24 | 9:01 | 2025-01-24 | 15:24 | 0.055956 | 0.00014623 | 53 | 20282 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace cross arms between poles 760109 and 760169 | .
829 |  | JE24045103 | HUNTERVILLE 22KV | Western | HUNTERVILLE 22KV | 2025-01-24 | 10:00 | 2025-01-24 | 11:22 | 0.0047268 | 5.7938e-05 | 21 | 1713 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace broken 11kV binder on pole 807225 raised by Helicopter Pole Top Topography | .
830 |  | JE24045107 | HUNTERVILLE 22KV | Western | HUNTERVILLE 22KV | 2025-01-24 | 11:03 | 2025-01-24 | 11:53 | 0.006902 | 0.00013795 | 50 | 2502 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11KV Binder on pole 804850 raised by Helicopter Pole Top Topography | .
831 |  | JE25002376 | 223 TUTAEKARA ROAD,PAHIATUA,PAHIATUA | Western | MANGAMAIRE | 2025-01-24 | 9:01 | 2025-01-24 | 10:02 | 0.013433 | 0.00021796 | 79 | 4869 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Urgent Job, Switching E00175 - Replace 11kv Crossarm at pole P44346 | .
832 |  | JE25002389 | 13A AHIPAIPA ROAD, HAWERA | Western | OKAIAWA | 2025-01-24 | 11:15 | 2025-01-24 | 13:02 | 0.012113 | 0.00011312 | 41 | 4390 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: Faulted 11kV Pin Insulator Isolation: MA481, MA456, MA465 Backfeeds: ABS 6708 What was replaced? HV Crossarm & Hardware, & extended HV jumpers Where was it replaced (pole/TX/pillar box)? Pole 718667 Additional Info: | .
833 |  | JE25002420 | 220 SUTHERLAND ROAD, MANAIA | Western | MANAIA | 2025-01-24 | 14:36 | 2025-01-24 | 15:46 | 0.0036886 | 5.242e-05 | 19 | 1337 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: Faulted HV Insulator What was replaced? HV Crossarm & Hardware Where was it replaced (pole/TX/pillar box)? Pole 718377 Isolation: Fuses MA574 Additional Info: | .
834 |  | JE24044593 | LONGBUSH | Western | LONGBUSH | 2025-01-23 | 9:18 | 2025-01-23 | 14:59 | 0.15157 | 0.00044419 | 161 | 54936 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Vegetation cutting at poles 823639 - 823642, 842214 - 842215 & 373249 - 823779 | .
835 |  | JE24044689 | ROWESDALE | Eastern | ROWESDALE | 2025-01-23 | 10:01 | 2025-01-23 | 13:18 | 0.065305 | 0.00033108 | 120 | 23670 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9241/1/2/3 | .
836 |  | JE24044690 | LINDERMANN RD | Eastern | LINDERMANN RD | 2025-01-23 | 9:04 | 2025-01-23 | 13:58 | 0.053526 | 0.00018209 | 66 | 19401 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv/400vt cross arms @ poles,204612,204613, Replace poleâ€™s 204608 & 204611. Isolation point @ SB1-002. | .
837 |  | JE24044700 | MANGOREWA | Eastern | MANGOREWA | 2025-01-23 | 9:15 | 2025-01-23 | 14:36 | 0.0053132 | 1.6554e-05 | 6 | 1926 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Cut trees between poles 481508 - 221271 | .
838 |  | JE24044714 | SOUTH RD NGARIKI | Western | SOUTH RD NGARIKI | 2025-01-23 | 8:57 | 2025-01-23 | 15:58 | 0.12213 | 0.00028969 | 105 | 44266 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace pole 713179, 713190, 713188, 712723, 713195, 713197 & 713200. Replace 11kv conductor with new Weke from pole 383070 to 487479 | .
839 |  | JE24044718 | LICHFIELD | Eastern | LICHFIELD | 2025-01-23 | 8:30 | 2025-01-23 | 14:59 | 0.042955 | 0.00011036 | 40 | 15569 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole M12345 with 11m Busck. Install nwe Entec Sectionaliser incl solid links. | .
840 |  | JE24045099 | KOHETE RD | Western | KOHETE RD | 2025-01-23 | 9:01 | 2025-01-23 | 15:40 | 0.034163 | 8.5528e-05 | 31 | 12382 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace xarms @ poles 760099,760100,760101,760102,760103,760104,760105,760106.Replace tx 2236T | .
841 |  | JE24045152 | COLOMBO RD | Western | COLOMBO RD | 2025-01-23 | 8:31 | 2025-01-23 | 15:50 | 0.66689 | 0.0015174 | 550 | 241716 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace S81 with new top mount non automated Entec switch | .
842 |  | JE24045281 | PARAPARA | Western | PARAPARA | 2025-01-23 | 9:16 | 2025-01-23 | 15:53 | 0.030727 | 7.7251e-05 | 28 | 11137 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace multiple poles & x-arms between poles 783762 & 783684 | .
843 |  | JE25002204 | 401 NO 2 LINE,OKOIA,WANGANUI | Western | UNION LINE | 2025-01-23 | 5:56 | 2025-01-23 | 14:32 | 0.084082 | 0.00062904 | 228 | 30476 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Car v Pole at Pole 793100 Initial AR on CB 3 followed by a number of no power jobs. Fire comms called about a car v pole and lines down causing a grass fire. Opened CB 3 for safety. Isolated at Fuses 075 and feeder relivened. | .
844 |  | JE25002215 | unknown SH 3 ,Waverley,Waverley | Western | RANGIKURA | 2025-01-23 | 7:31 | 2025-01-23 | 11:41 | 0.028245 | 0.00018761 | 68 | 10237 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 1112/2 Protection flags (nil where none): C ph E/F CAUSE: Unknown - But suspect bird strike Location: 359177 & 359302 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: cursory Weather (wind/rain): calm LFI (Y/N + Comments): N Follow up Required (select advisory)? N Additional fault restoration comments: Line was isolated at ABS663 to repair the lines down. | .
845 |  | JE25002217 | 202 MANGATEPARU LOOP ROAD,MANGATEPARU,MORRINSVILLE | Eastern | HORRELLS RD | 2025-01-23 | 8:01 | 2025-01-23 | 13:28 | 0.032764 | 0.00028969 | 105 | 11875 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: NIL - 11kV - No Tripping Protection flags (nil where none): NIL CAUSE: Lines Down Past ABS 604 Location: ABS 604 Temp generation (state details when used): NIL PERFORMANCE DETAIL DNO (number or state No): NIL Circuit patrolled and type: Cursory Weather (wind/rain): Fine LFI (Y/N + Comments): NIL Follow up Required (select advisory)? NIL Additional fault restoration comments: Deadend Burnt out at ABS 604, Dropped line onto ground, 11kV Line was Still energized on the ground upon arrival Copper Conductor and aluminum Dead End Joints. Replaced all Dead Ends and 2 x crossarms | .
846 |  | JE25002229 | unknown QUARRY ROAD,Te Wera,Rural | Western | STRATHMORE | 2025-01-23 | 8:42 | 2025-01-23 | 11:23 | 0.0017758 | 1.1036e-05 | 4 | 644 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 5680 No. Fuses: x 2 Fuse Amp Size: 8 amp TIME CLOSED: 11:23am Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)? | .
847 |  | JE25002236 | 178 RANGIURU ROAD,RANGIURU,TE PUKE | Eastern | MANGOREWA | 2025-01-23 | 10:56 | 2025-01-23 | 12:34 | 0.0018801 | 1.9313e-05 | 7 | 681 | Unplanned | WILDLIFE - POSSUM | Fuses Location: Fuse/Sw 14975/2 No. Fuses: 3 Fuse Amp Size: 6.3A TIME CLOSED: 12:33 Cause: Possum At Transformer TE6 155 Weather (wind/rain): Fine - Hot Follow up required (select advisory)? NIL | .
848 |  | JE25002257 | 137 LUND ROAD,AONGATETE,KATIKATI | Eastern | KATIKATI | 2025-01-23 | 10:04 | 2025-01-23 | 11:46 | 0.0025411 | 2.4831e-05 | 9 | 921 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: (SC-1009) - asset location of fault No. Fuses: x2 Fuse Amp Size: 8 amp TIME CLOSED: 11:45am Cause: unknown Weather (wind/rain): Calm Follow up required (select advisory)? | .
849 |  | JE25002280 | 2 STRATHMORE DRIVE,AONGATETE,KATIKATI | Eastern | WILLS RD | 2025-01-23 | 12:36 | 2025-01-23 | 14:59 | 0.0035336 | 2.4831e-05 | 9 | 1281 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | E00174/1648 - Connect new 35mm cable into Transformer TB2-081 & remove generator TB2-083 DNO2501006 | .
850 |  | JE25002290 | 11 RAHOTU ROAD,RAHOTU,OPUNAKE | Western | RAHOTU | 2025-01-23 | 13:53 | 2025-01-23 | 15:33 | 0.0027561 | 2.759e-05 | 10 | 999 | Unplanned | WILDLIFE - BIRD | Fuses Location: NG270 No. Fuses: 2 Fuse Amp Size: 15A TIME CLOSED: 15:33 Cause: Bird strike Weather (wind/rain): Fine Follow up required (select advisory)? Full power restored | .
851 |  | JE25002297 | 15 OLD HILL RD,TAHUNA,MORRINSVILLE | Eastern | PATETONGA | 2025-01-23 | 14:37 | 2025-01-23 | 18:40 | 0.010719 | 4.4143e-05 | 16 | 3885 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses FP1322 No. Fuses: 2 Fuse Amp Size: 8A TIME CLOSED: 18:40 Cause: Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)?No | .
852 |  | JE25002306 | 452 WELCOME BAY ROAD,WELCOME BAY,TAURANGA | Eastern | BRUCE RD | 2025-01-23 | 16:40 | 2025-01-23 | 18:48 | 0.01449 | 0.00011312 | 41 | 5252 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | ABS IP322 ARCHING. Bypassed on field and on Emap. DNO 2501012 | .
853 |  | JE25002333 | TUTAENUI - ARAHINA SUB - ARAHINA/5 REC | Western | TUTAENUI | 2025-01-23 | 18:27 | 2025-01-23 | 21:57 | 0.13762 | 0.0019892 | 721 | 49882 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: CB 5 Protection flags (nil where none): OC CAUSE: 2 x lines bought down by a duck Location: Pole 800503 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: N Weather (wind/rain): fine LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
854 |  | JE24040655 | BROOKLANDS 7 | Western | BROOKLANDS 7 | 2025-01-22 | 9:46 | 2025-01-22 | 12:31 | 0.05501 | 0.00033383 | 121 | 19939 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace arms on poles 701479 plus straighten pole | .
855 |  | JE24044352 | LINDERMANN RD | Eastern | LINDERMANN RD | 2025-01-22 | 8:45 | 2025-01-22 | 15:30 | 0.060921 | 0.00015726 | 57 | 22081 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv/400vt cross arms @ poles,204497,204498,204499,204500. Replace pole 11KV 204501. Isolation point @ SB1-041. Extra work done at Transformer TB1-008 and Transformer Fuses left open at 15:10.Closed in at 15 :30 | .
856 |  | JE24044383 | WESTMERE PEAT ST | Western | WESTMERE PEAT ST | 2025-01-22 | 9:15 | 2025-01-22 | 15:31 | 0.041421 | 0.00011036 | 40 | 15013 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Carry out 11KV Line Drop & Tree Cutting between poles 468625 & 784219 | .
857 |  | JE24044389 | PATETONGA | Eastern | PATETONGA | 2025-01-22 | 9:00 | 2025-01-22 | 15:35 | 0.040293 | 0.00010208 | 37 | 14605 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV poles & xarms beyond ABS IC484 | .
858 |  | JE24044391 | LONGBUSH | Western | LONGBUSH | 2025-01-22 | 9:00 | 2025-01-22 | 15:29 | 0.05258 | 0.00013519 | 49 | 19058 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles and hardware past S333 | .
859 |  | JE24044394 | GRENADA ST | Eastern | GRENADA ST | 2025-01-22 | 9:46 | 2025-01-22 | 13:34 | 0.045238 | 0.00019865 | 72 | 16397 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9360/1/2/3/4/5 | .
860 |  | JE24044404 | PARK RD | Western | PARK RD | 2025-01-22 | 8:51 | 2025-01-22 | 14:20 | 0.064404 | 0.00019589 | 71 | 23344 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re-sag 11kv conductors at multiple sites from 11kv fuses 7607 to pole 841588 | .
861 |  | JE24044662 | MAUNGAKAWA ROAD | Eastern | MAUNGAKAWA ROAD | 2025-01-22 | 9:16 | 2025-01-22 | 14:38 | 0.064805 | 0.0002014 | 73 | 23489 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace HV & LV xarms at poles C585, C578 - C13331, C13349, C13341 - C13346, C13364 & C13383 | .
862 |  | JE24044668 | COLYTON | Western | COLYTON | 2025-01-22 | 8:30 | 2025-01-22 | 13:50 | 0.024706 | 7.7251e-05 | 28 | 8955 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles and hardware between P38454 - P38473. | .
863 |  | JE25001266 | ATHENREE | Eastern | ATHENREE | 2025-01-22 | 8:57 | 2025-01-22 | 16:23 | 0.16554 | 0.0011395 | 286 | 60001 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace 11kv fuses SA2-018 with fused ABS connect new cable, remove 3 x generators | .
864 |  | JE25001967 | 5338 TAIHAPE-NAPIER ROAD, TAIHAPE, 4792 | Western | MOAWHANGO | 2025-01-22 | 11:35 | 2025-01-22 | 13:26 | 0.00030404 | 2.759e-06 | 1 | 110 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FM was unable to access this remote site as it was unsafe to do so due to dangerous conditions. FM will attend in the morning. FM replaced missing split pin in strain insulator | .
865 |  | JE25002009 | 609 PUKEHOI ROAD,EKETAHUNA,EKETAHUNA | Western | MANGAMAIRE | 2025-01-22 | 9:09 | 2025-01-22 | 10:28 | 0.0028502 | 3.5867e-05 | 13 | 1033 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Crew assessed site and it is safe to leave for now and they will submit an urgent NAPA to repair. 2r to be left open to complete repairs. Cross and hardware were replaced | .
866 |  | JE25002072 | 296 OPUA ROAD,OPUNAKE,OPUNAKE | Western | OAONUI | 2025-01-22 | 5:31 | 2025-01-22 | 7:15 | 0.00028735 | 2.759e-06 | 1 | 104 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Location of blown fuses (6999) CHILD OF JE25002072 No. Fuses: 2 Fuse Amp Size: 8AMP TIME CLOSED: 07:15AM Cause: uNKNOWN Weather (wind/rain): OVERCAST Follow up required (select advisory)?NO | .
867 |  | JE25002073 | 247 OTAHU ROAD,WHANGAMATA,WHANGAMATA | Eastern | OTAHU RD | 2025-01-22 | 7:26 | 2025-01-22 | 8:51 | 0.13107 | 0.0015423 | 559 | 47507 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: Recloser 9813/2 Protection flags (nil where none): EF CAUSE: Suspect Seagull Found dead on the ground Location: Pole 861277 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): None Follow up Required (select advisory)? Additional fault restoration comments: Nothing found on the lines but only a dead seagull on the ground at pole 861277. Power restored at 08:50 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): No Circuit that tripped: N/A DTF (KM):N/A | .
868 |  | JE25002084 | 15 NEWCASTLE STREET,HOKOWHITU,PALMERSTON NORTH | Western | KEITH ST 24 | 2025-01-22 | 10:41 | 2025-01-22 | 11:31 | 0.013675 | 0.00027314 | 99 | 4957 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: G255T No. Fuses: 1 Fuse Amp Size: 25 TIME CLOSED: 11:30 Cause: unknown Weather (wind/rain): calm Follow up required (select advisory)? | .
869 |  | JE25002112 | unknown unknown ,Mangaweka,Rural | Western | MANGAWEKA | 2025-01-22 | 16:34 | 2025-01-22 | 20:20 | 0.004365 | 1.9313e-05 | 7 | 1582 | Unplanned | VEGETATION - INSIDE ZONE | Remove tree branches from near the lines that have been contacting lines in the wind between Pole 807911 & 807910 | .
870 |  | JE25002114 | 15 NEWCASTLE STREET,HOKOWHITU,PALMERSTON NORTH | Western | KEITH ST 24 | 2025-01-22 | 14:00 | 2025-01-22 | 15:25 | 0.023035 | 0.00027314 | 99 | 8349 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Cause: LV cable fault What was replaced? UG cable fault has been repaired. Network back up to Powerco Standards. Phases back to normal. Where was it replaced (pole/TX/pillar box)? G255T Is 2R required? Y 2R Y - What is the timeframe for repairs? Completed Additional Info: Full power restored to the network Check if JE25002160 is related Whole TX needs replacing TX G255. Approx 100 customers effected but FM attempting to put in back feeds, may take a couple of hours. Will call back with update. Transformer G255T does not need replacing tracked down fault to yellow phase on LV circuit from pillar 6, crew will return after hours to locate fault and repair. Brendon McDonald went to site, LV cable fault on the network side on the yellow phase. FM went from transformer to junction box and identified two houses on the yellow phase: 6 and 10 Newcastle street. Temporarily 6 is moved to the red phase, and 10 to the blue phase. FM advised they would mark out, find the fault and mark it out. Thomas Childs have moved 6 Newcastle Street from blue phase to red phase, restoring power. The cable fault repairs are still ongoing. 31/01/2025 - FM have confirmed that all work has been completed. Network back up to Powerco standards. Network restored. MDP HV isolation 22/01/25 at Fuse/Sw G255T 1x 25amp HV fuse replaced | .
871 |  | JE25002122 | 93 MOWBRAYS ROAD, EKETAHUNA, 4995 | Western | MANGAMAIRE | 2025-01-22 | 13:31 | 2025-01-22 | 15:22 | 0.00061488 | 5.5179e-06 | 2 | 223 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Faultman found lines have been damaged by customers silage contractor, this line is a Private line, line was isolated at Fuses S20 and Scanpower are going to repair the lines. Scanpower's Mike Sandbrook repaired the customers lines and restored the supply. | .
872 |  | JE25002142 | 239 TUTAEKARA ROAD, PAHIATUA | Western | MANGAMAIRE | 2025-01-22 | 17:52 | 2025-01-23 | 11:53 | 0.0029825 | 2.759e-06 | 1 | 1081 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | `Faultman is going to contact customer to find out when they will use the wool shed as this is fed off Tfr T7/166 were the job is and not T7/164. The customer reported to Faultman that he is remotely disconnect at the moment by his retailer as not using the wool shed until sheering season starts again Faultman has isolated Tfr T7/166 and crew will return in morning to replace insulator as access is not easy. 23/01/25 - Faultman replaced broken insulator on transformer T7/166 | .
873 |  | JE25002168 | 413 DENBIGH ROAD, STRATFORD, 4394 | Western | CLOTON RD NORTH | 2025-01-22 | 19:33 | 2025-01-22 | 23:20 | 0.023177 | 0.00010208 | 37 | 8401 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | ** RED DEFECT ** Replace Pole 741598 | .
874 |  | JE25002172 | dtx_TC5419 | Eastern | COROGLEN | 2025-01-22 | 17:04 | 2025-01-22 | 19:56 | 0.00095175 | 5.5179e-06 | 2 | 345 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: DTX TC5419 Failed 1 phase 10kVA replaced with 1 Phase 15KVA CAUSE: Lightning Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: Weather (wind/rain): Follow up required (select advisory)? Additional fault restoration comments: | .
875 |  | JE24044009 | TUTAENUI | Western | TUTAENUI | 2025-01-21 | 9:34 | 2025-01-21 | 14:45 | 0.010303 | 3.3108e-05 | 12 | 3734 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 2 X Red Tagged Poles 794581 & 794602 | .
876 |  | JE24044083 | PARK RD | Western | PARK RD | 2025-01-21 | 8:34 | 2025-01-21 | 15:48 | 0.002393 | 5.5179e-06 | 2 | 867 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles on swer line past T332 | .
877 |  | JE24044277 | PONATAHI | Western | PONATAHI | 2025-01-21 | 9:18 | 2025-01-21 | 13:49 | 0.052308 | 0.00019313 | 70 | 18959 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Vegetation cutting between poles 471514 - 819295, 819220- 819217 & 819210 - 819209 | .
878 |  | JE24044405 | SOUTH RD NGARIKI | Western | SOUTH RD NGARIKI | 2025-01-21 | 9:15 | 2025-01-21 | 14:27 | 0.02148 | 6.8974e-05 | 25 | 7785 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace poles 713169, 713170, 713171, 713173, 713174, 713175, 713176 & 713177 | .
879 |  | JE24044504 | KOHETE RD | Western | KOHETE RD | 2025-01-21 | 9:00 | 2025-01-21 | 14:58 | 0.0088828 | 2.4831e-05 | 9 | 3220 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace xarms @ poles 760035,760036,760037,760038,760039,760040,760041,760042. Replace tx 3579T | .
880 |  | JE25001699 | WESTMERE GLADSTONE | Western | WESTMERE GLADSTONE | 2025-01-21 | 9:25 | 2025-01-21 | 12:34 | 0.037494 | 0.00019865 | 72 | 13590 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Tree Felling between poles 367705 and 365039 | .
881 |  | JE25001929 | 13 STATION ROAD,WAVERLEY,WAVERLEY | Western | WAVERLEY | 2025-01-21 | 6:21 | 2025-01-21 | 7:04 | 0.036174 | 0.00086631 | 314 | 13112 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Blown Jumper found feeding into Links 2941 Recloser 2680 Opened Isolated at ABS's 098 & 499 | .
882 |  | JE25001952 | 3 ENDOWMENT ROAD,OTWAY,TE AROHA | Eastern | TIROHIA-KARANGAHAKE | 2025-01-21 | 9:15 | 2025-01-21 | 10:30 | 0.00020879 | 2.759e-06 | 1 | 76 | Unplanned | VEGETATION - INSIDE ZONE | Fuses Location: Transformer TC1587 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 10:30 Cause: Trees rubbing lines Weather (wind/rain): Calm Follow up required (select advisory)? Yes HV Fuses closed but the 400V Fuses still open Franklin Trees to cut trees in the LV lines then Reliven the LV Trees are trimmed , tested, full power restored. LV Fuses closed 13:00Hrs | .
883 |  | JE25001966 | unknown WAIHI WHANGAMATA ROAD,Waihi,Waihi | Eastern | WAIHI NORTH | 2025-01-21 | 9:52 | 2025-01-21 | 10:58 | 0.029934 | 0.00046075 | 167 | 10850 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: Recloser 9604 Protection flags (nil where none): EF CAUSE: Unknown Location: N/A Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): LFI (Y/N + Comments): No LFIs lit Follow up Required (select advisory)? No Additional fault restoration comments: Circuit patrolled, nothing found. Tee cutters confirmed they did not cause the tripping. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
884 |  | JE25001985 | 2759 WAIHI WHANGAMATA ROAD,WHANGAMATA,WHANGAMATA | Eastern | HETHERINGTON RD | 2025-01-21 | 11:01 | 2025-01-22 | 19:43 | 0.19955 | 0.0040115 | 1384 | 72327 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: CB 1122 Protection flags (nil where none): EF, OC, Phase A Fault CAUSE: Failed Cable Termination Burnt with pole cracked and Termination cross arm also burnt down. Pole cross arm and cable termination to be replaced. Location: Pole R12540 Temp generation (state details when used): Yes at transformer TC3474 PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Rain LFI (Y/N + Comments): Yes at Sw/Gear 13530 /3 Follow up Required (select advisory)? Yes Additional fault restoration comments: Generator to be connected at Transformer TC3474 Generator connected 15:25Hrs (21/01/25) Disconnected 22/01/25 off 18:42 on 19:47 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): N/A Circuit that tripped: N/A DTF (KM):N/A | .
885 |  | JE25001999 | 68 hacketts road ,Ashhurst | Western | ASHHURST | 2025-01-21 | 11:54 | 2025-01-21 | 13:16 | 0.00022621 | 2.759e-06 | 1 | 82 | Unplanned | WILDLIFE - BIRD | Fuses Location: 10778 No. Fuses: 2 Fuse Amp Size: 15a TIME CLOSED: 1315 Cause: duck Weather (wind/rain): wind Follow up required (select advisory)? | .
886 |  | JE25002020 | 117 WHAREKAHO ROAD,WHAREKAHO,WHITIANGA | Eastern | BUFFALO BEACH | 2025-01-21 | 13:58 | 2025-01-21 | 14:26 | 0.00015368 | 5.5179e-06 | 2 | 56 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses FC2214 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 14:25 Cause: Unknown Weather (wind/rain): Windy and Rain Follow up required (select advisory)?No | .
887 |  | JE25002024 | 234 ATHENREE ROAD, KATIKATI, 3177 | Eastern | BOWENTOWN | 2025-01-21 | 18:38 | 2025-01-21 | 20:08 | 0.0019817 | 2.2072e-05 | 8 | 718 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: DTX TA2-019 Failed 3 phase 30kVA Transformer , CAUSE: LV Fault blew transformer up, Transformer Replaced & LV Circuits repaired Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: Weather (wind/rain): Follow up required (select advisory)? Additional fault restoration comments: | .
888 |  | JE25002040 | PAEROA SUB - RAILWAY ST - PAEROA/2 | Eastern | RAILWAY ST | 2025-01-21 | 16:04 | 2025-01-21 | 18:44 | 0.16854 | 0.0020113 | 729 | 61086 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB2 Protection flags (nil where none): Ph B, C OC CAUSE: Tree Branches on Lines Location: Pole 482983 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: Cursory Weather (wind/rain): Rain LFI (Y/N + Comments): None Follow up Required (select advisory)? No Additional fault restoration comments: Isolated at Switchgears 9544/2 and 13124/3 removed trees and restored power | .
889 |  | JE25002049 | PAEROA - WILLOUGHBY ST - REC 9920/2 | Eastern | WILLOUGHBY ST | 2025-01-21 | 16:47 | 2025-01-21 | 17:28 | 0.04459 | 0.001076 | 390 | 16162 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | REGULATORY INFORMATION Voltage & Device ID: Recloser 9920 Protection flags (nil where none): Ph B- OC CAUSE: Unknown Location: N/A Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): Yes LFI (Y/N + Comments): None Follow up Required (select advisory)? No Additional fault restoration comments: Line patrolled, nothing found, Power restored 17:28Hrs Suspect treee branches along Norwood Road at ABS 559.Should have hit the lines on their way down SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): N/A Circuit that tripped: N/A DTF (KM):N/A | .
890 |  | JE24041931 | CARTER H.H. | Eastern | CARTER H.H. | 2025-01-20 | 7:30 | 2025-03-04 | 17:07 | 0.00018834 | 1.1036e-05 | 2 | 68 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Matatoki Upgrade Project Stage 3 Fit New Protection Relays CB1, 3, 5 and 17. Install Blast Doors, Connect 18 to 17, Fit Arc Flash T1 Board . Engineering re backfeeding Matatoki in switchpack . | .
891 |  | JE24044139 | MCCABE ROAD | Eastern | MCCABE ROAD | 2025-01-20 | 8:26 | 2025-01-20 | 14:55 | 0.047324 | 0.00012139 | 44 | 17153 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace ABS 628 on pole C13595 | .
892 |  | JE24044675 | NO 3 ROAD | Eastern | NO 3 ROAD | 2025-01-20 | 9:15 | 2025-01-20 | 19:15 | 0.011581 | 1.9313e-05 | 7 | 4198 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Reconductor OH HV From 381334 to 381122 and from 223555 to 382033 Job had an over run as the old conductor keep breaking when it came under tension from the new conductor. | .
893 |  | JE24044697 | BARRETT RD | Eastern | BARRETT RD | 2025-01-20 | 14:00 | 2025-01-20 | 15:40 | 0.026206 | 0.00028417 | 103 | 9499 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To apply cover up gear on Pole 493884/489718 to allow recloser install using GB-T01. Connect new Noja recloser 15037/2 and link 15037/4 to 11kV line and carry out pre commissioning check and remove cover ups. Scada Commissioning carried out under NAPA 116529 (WA) | .
894 |  | JE25001830 | 4273 MOUNTAIN ROAD,NGAERE,STRATFORD | Western | CLOTON RD INDUSTRIAL | 2025-01-20 | 7:40 | 2025-01-20 | 7:46 | 3.3891e-05 | 5.5179e-06 | 2 | 12 | Unplanned | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 33kV CB 2782, 11kV Rec 6942 Protection flags (nil where none): E/F, O/C B & C CAUSE: unknown, possible bird strike Location: na Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: no Weather (wind/rain): unknown LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: CB 2782 tripped, Rec 6942 would have tripped on under voltage, 33kV Line stayed live on the powerco side, line was back feed through CLO Sub TFR 2082T CB 2782 closed, Cheal contacted and supply restored by closing Rec 6942 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
895 |  | JE25001853 | 164B Stanley Road, Te Aroha,TE AROHA | Eastern | MOUNTAIN | 2025-01-20 | 9:42 | 2025-01-20 | 11:56 | 0.00036986 | 2.759e-06 | 1 | 134 | Unplanned | WILDLIFE - BIRD | Fuses Location: FP358 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 1155 Cause: bird strike Weather (wind/rain): not bad little breeze Follow up required (select advisory)? | .
896 |  | JE25001895 | 544B ALEXANDRA ROAD,MANAWARU,TE AROHA | Eastern | MAUNGAKAWA ROAD | 2025-01-20 | 18:45 | 2025-01-20 | 19:36 | 0.0061278 | 0.00012139 | 44 | 2221 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faultman found broken DDO's at transformer TC2076, line was isolated at ABS's 659, IC672 & IC704 to replace the full set of DDO's. | .
897 |  | JE25001915 | unknown EMERTON ROAD,Waihi Beach,Waihi Beach | Eastern | ATHENREE | 2025-01-20 | 17:21 | 2025-01-21 | 11:21 | 0.075851 | 0.0015809 | 573 | 27493 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | FRM - Fredi De Lange contacted Control to advise that there is a cable fault from Link Box SA2-030, the out going cable to transformer TA2-157. A 11kV generator is going to be sourced and connected to feed the transformers from TA2-157 to the end except for transformer T5011 which is the council and they have there own generator that is been connected. 11kV Generator connected at Pole 207495 Power ON 11:20 (21/01/25) Transformer T5011 on private generator (Council | .
898 |  | JE24044978 | PUTARURU DOMAIN | Eastern | PUTARURU DOMAIN | 2025-01-19 | 9:31 | 2025-01-19 | 15:22 | 0.0026067 | 0.00017106 | 62 | 945 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE POLE M2211, AND INSTALL NEW UG HV CABLE. REMOVE POLE M13035 AND INSTALL AND COMMISION NEW SWITCH UNIT 15018. NEW CABLE FROM THE SWITCH UNIT TO POLE M13026 AND COMPLETE INLINE` HV JOINT.NEW SWITCH UNIT WILL CONTROL TC6202,TP203 & TC781. OVERHEAD LINE FROM POLE M2211 WILL BE REMOVED, WHICH INCLUDES FC2749 AND FC2476 | .
899 |  | JE25001418 | KOPU | Eastern | KOPU | 2025-01-19 | 7:20 | 2025-01-19 | 14:55 | 0.22475 | 0.00088287 | 297 | 81463 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Kerepehi Sub 11kV Busbars Inspection, requires full substation outage. Switching only & ADV to Open & Close Links 14732 KPE7 . Generator required re LST - TP101 . Previous switching NAPA 116698 . | .
900 |  | JE25001771 | 24 ALBERT LANE,WHAKAMARAMA,TAURANGA | Eastern | PLUMMERS POINT | 2025-01-19 | 0:02 | 2025-01-19 | 6:00 | 0.1955 | 0.0036473 | 1322 | 70861 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 6 Protection flags (nil where none): A O/C E/F CAUSE: Cable Fault Location: Temp Break created between Pole 208602 & 413656 Temp generation (state details when used): Yes at Transformer TC3-183 Connect at 06:00 PERFORMANCE DETAIL DNO (number or state No): 25016 Circuit patrolled and type: Cursory Weather (wind/rain): LFI (Y/N + Comments): Yes ABS IP594 Follow up Required (select advisory)? No Additional fault restoration comments: | .
901 |  | JE25001787 | 42 SWAN STREET, TAIHAPE, 4720 | Western | MATAROA A | 2025-01-19 | 11:39 | 2025-01-19 | 15:47 | 0.0075194 | 3.0349e-05 | 11 | 2725 | Unplanned | VEGETATION - OUTSIDE ZONE | Check - JE25001788 - related ETA requested by FENZ - 20 minutes ETA 19/01/2025 - Branch across lines, 45 Ruru road 19/01/2025 - Update - Fire and emergency rang to advise lines down on corner of Swan Street, and Ruru street. Tree brought lines down at pole 788779 Isolated at Fuses 2589 Swan St Patrolled with No issue found Lines Repaired | .
902 |  | JE25001791 | 1654 OHURA ROAD,DOUGLAS,STRATFORD | Western | HUIROA | 2025-01-19 | 11:55 | 2025-01-19 | 13:51 | 0.0060622 | 5.242e-05 | 19 | 2197 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Check fuses 4973 Check if JE25001792 is related Fuses Location: 4973 No. Fuses: 2 Fuse Amp Size: 10 Amp TIME CLOSED: 13:50 Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)? N | .
903 |  | JE25001817 | 15 OLD HILL RD,TAHUNA,MORRINSVILLE | Eastern | PATETONGA | 2025-01-19 | 18:12 | 2025-01-19 | 20:00 | 0.0047972 | 4.4143e-05 | 16 | 1739 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | Fuses Location: FP1322 No. Fuses: 2 Fuse Amp Size: 15 TIME CLOSED: 20:00 Cause: Tree branch Weather (wind/rain): calm Follow up required (select advisory)? | .
904 |  | JE25001739 | unknown TAWERA ROAD,Mangatainoka,Pahiatua | Western | RUAWHATA | 2025-01-18 | 9:08 | 2025-01-18 | 11:46 | 0.0047981 | 3.0349e-05 | 11 | 1739 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: T7/500 No. Fuses: 2 Fuse Amp Size: TIME CLOSED: Cause: Faulty Transformer Weather (wind/rain): Calm Follow up required (select advisory)? N FM provided wrong transformer number at start of job (T7/501, Transformer was T7/500) all data updated transformer T7/501 only had power off while fuses Q62 open Transformer T7/500 found to be faulty, Also Fuse base of transformer fuse broken. Fuses Q64 dressed as Open As FM advised they were isolation point, on checking fuse isolation was Q62, Fuses Q64 were never opened Isolated at Fuses Q62 & Fuses replaced Transformer Isolated at transformer fuses Transformer Replaced | .
905 |  | JE25001762 | 372 OKAUIA SPRINGS ROAD, OKAUIA, MATAMATA, 3471 | Eastern | GORDON | 2025-01-18 | 18:03 | 2025-01-19 | 0:08 | 0.06348 | 0.00017381 | 63 | 23009 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 6 Protection flags (nil where none): Nil CAUSE: Car vs pole Location: Pole F0756 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): NA Circuit patrolled and type: F4. Not patrolled. Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? NDR to follow Additional fault restoration comments: Pole F0756 replaced with 11m Double HV pin cross arm complete assembly SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
906 |  | JE25001769 | 3 CLOTEN ROAD,STRATFORD,STRATFORD | Western | CLOTON RD NORTH | 2025-01-18 | 20:29 | 2025-01-19 | 1:20 | 0.18558 | 0.0025603 | 928 | 67263 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: CB 5 Protection flags (nil where none): Ph A, B, C Fault, OC INVT, INTRP Send CAUSE: Lines Down caused by duck. Found lying dead on the ground Location: Pole 741366, road crossing SH3 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): None Circuit patrolled and type: Cursory Weather (wind/rain): LFI (Y + Comments): At Sw/Gear 12507/1 Follow up Required (select advisory)? No Additional fault restoration comments: Fault finding by sectionalising. Isolated fault area and repaired lines under Access Permit Power restored 01:19Hrs (19/01/25). Access permit delayed due to SH3 road crossing, Traffic Management required SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): N/A Circuit that tripped: N/A DTF (KM):N/A | .
907 |  | JE24043565 | CAMBRIA LS | Western | CAMBRIA LS | 2025-01-17 | 8:30 | 2025-01-17 | 15:31 | 0.0046404 | 1.1036e-05 | 4 | 1682 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace H structure pole 724880 & 724879 & replace H structure poles 724883 & 724884 | .
908 |  | JE24044079 | ROTOEHU | Eastern | ROTOEHU | 2025-01-17 | 9:15 | 2025-01-17 | 13:38 | 0.090557 | 0.00034487 | 125 | 32823 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV pole 229168 | .
909 |  | JE24044097 | LINTON | Western | LINTON | 2025-01-17 | 9:41 | 2025-01-17 | 15:30 | 0.014449 | 4.1384e-05 | 15 | 5237 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Vegetation cutting between poles P03320 to P03325 | .
910 |  | JE24044419 | BROOKLANDS 8 | Western | BROOKLANDS 8 | 2025-01-17 | 9:30 | 2025-01-17 | 13:46 | 0.053643 | 0.00020968 | 76 | 19443 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install TX LV isolation fuses/install new 185 AL cable & fuses, replace stub pole 701185, remove poles 701221 & 364810, divert UG services/remove LV overhead lines. | .
911 |  | JE24045220 | TE MATAI RD | Eastern | TE MATAI RD | 2025-01-17 | 9:00 | 2025-01-17 | 13:03 | 0.0058516 | 2.4831e-05 | 9 | 2121 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 1. Lower 11kV cable from pole 224864 feeding P/M TE6-297, join to new cable, connect to 14838/2 2. Lower 11kV cable from pole 224872 feeding G/M TE6-318 join to new cable, connect to 14845/2 3. Remove P/M TE6-144, tfr load to new G/M TE6-144 connected to 14838/4. 4. Remove P/M TP2159 & TE6-013, tfr combined load to new G/M TP4385 connected to 14840/2. | .
912 |  | JE24046590 | HOLDSWORTH | Western | HOLDSWORTH | 2025-01-17 | 8:56 | 2025-01-17 | 13:56 | 0.10107 | 0.00033659 | 122 | 36633 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install 11m Busck and SEL651R Tavrida recloser 11390/2 | .
913 |  | JE24046706 | RICHMOND ST | Eastern | RICHMOND ST | 2025-01-17 | 8:30 | 2025-01-17 | 16:24 | 0.49169 | 0.0010429 | 378 | 178214 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 394966 & remove Recloser 9882 & Bypass ABS. Remove sectionaliser 9883 from pole 390598 and install by pass ABS & Recloser 9882 from pole 390598. Replace crossarms on poles T0211 & T0210. Install sectionaliser 9883 on new pole 394966. Install Recloser 9882 on Pole 390958. | .
914 |  | JE25001621 | ELTHAM - MANGATOKI - ELTHAM/R51 | Western | MANGATOKI | 2025-01-17 | 8:02 | 2025-01-17 | 10:38 | 0.065575 | 0.001316 | 350 | 23768 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB R51 Protection flags (nil where none): E/F, O/C A, B & C CAUSE: Cable fault at the bottom of links 12714, due to the connection point on middle link failing causing a flash over Location: Links 12714 (Pole 734921) Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): calm LFI (Y/N + Comments): n Follow up Required (select advisory)? Additional fault restoration comments: Feeder tripped, unable to put a back feed in remotely due to Sec 12281 having low SF6 alarm / no remote operation Faultman started their patrol and found a cable fault at the bottom of links 12714 fault caused be the connection point on middle link failing causing a flash over Isolated at ABS 12633, 6098, 6005 & 6132 Back feeds put in place Cable termination repaired, middle link bypassed, Cable tested, full power restored, feeder restored to normal config NOTE - the 4 pole structure that these links and ABS's are on is getting removed with in the next month SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
915 |  | JE25001632 | 84 ,, | Eastern | APATA | 2025-01-17 | 8:36 | 2025-01-17 | 10:41 | 0.011029 | 8.8287e-05 | 32 | 3998 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | Fuses Location: SC2 - 057 No. Fuses: 2 Fuse Amp Size: 20A TIME CLOSED: 10:40 Cause: Gumtree branch Weather (wind/rain): Fine Follow up required (select advisory)? Full power restored | .
916 |  | JE25001667 | 189 EAST ROAD,STRATFORD,STRATFORD | Western | ELTHAM 33kV | 2025-01-17 | 10:31 | 2025-01-17 | 12:17 | 0.014285 | 0.0020472 | 742 | 5178 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 33kV CB 2822 Protection flags (nil where none): E/F CAUSE: unknown Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: cursory Weather (wind/rain): calm LFI (Y/N + Comments): n Follow up Required (select advisory)? Additional fault restoration comments: CB 2822 tripped, 1/2 bus lost at Eltham as R10 was open due to AVR faults, CB R08 opened, CB R10 closed full power restored to Eltham Sub Customers Line patrolled, no fault found, full power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): TFR T46 side of the bus (Bus coupler R10 was open due to AVR fault) & Waihapa Circuit that tripped: SFD CB 2822 DTF (KM): | .
917 |  | JE25001682 | 879 WESTERN LAKE ROAD,WESTERN LAKE,FEATHERSTON | Western | REVANS ST | 2025-01-17 | 12:02 | 2025-01-17 | 14:09 | 0.00070521 | 5.5179e-06 | 2 | 256 | Unplanned | WILDLIFE - BIRD | Fuses Location: 7144 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 14:09 Cause: Swans Weather (wind/rain): Fine Follow up required (select advisory)? Yes Power restored FM advises to change the last 4 poles to delta configuration to avoid future issues. This has happened on multiple occasions. | .
918 |  | JE24043594 | KOPANE | Western | KOPANE | 2025-01-16 | 9:03 | 2025-01-16 | 14:50 | 0.012438 | 3.5867e-05 | 13 | 4508 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11KV poles & crossarms between ABS H61 & A55 | .
919 |  | JE24043616 | NO 3 ROAD | Eastern | NO 3 ROAD | 2025-01-16 | 9:03 | 2025-01-16 | 15:56 | 0.0079826 | 1.9313e-05 | 7 | 2893 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles & xarms from 223548 to 223560. Install new poles between 381122 & 223555. Replace TF5-004 with single phase 30kVA Tx. Remove poles 269376 & 223554. Reconductor from 381122 to 223555 & to 381598. | .
920 |  | JE24043968 | REVANS ST | Western | REVANS ST | 2025-01-16 | 8:30 | 2025-01-16 | 13:41 | 0.00085666 | 2.759e-06 | 1 | 311 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Reconductor 11kv from 7260 to end of line | .
921 |  | JE24043982 | PIONEER RD | Western | PIONEER RD | 2025-01-16 | 10:40 | 2025-01-16 | 16:59 | 0.017751 | 4.6902e-05 | 17 | 6434 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Asplundh Climb & cut trees between poles 755283 & 755284 | .
922 |  | JE24044043 | PARK RD | Western | PARK RD | 2025-01-16 | 10:12 | 2025-01-16 | 15:53 | 0.030844 | 9.3805e-05 | 34 | 11180 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Vegetation cutting between poles 824358 to 824356 & replace defected Tx pole 824358 | .
923 |  | JE24044144 | MURAL TOWN | Eastern | MURAL TOWN | 2025-01-16 | 8:47 | 2025-01-16 | 14:40 | 0.064391 | 0.00018209 | 66 | 23339 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | : Replace 11kv/400vt cross arms @ poles,204598,204602,204603,204604, 204605, & 204609. Replace poles LV 204642 & 204607. Isolation points @ 11kv SB1-001. 33kv ABS 1049 & 33kv ABS 66 | .
924 |  | JE24044413 | PARAPARA | Western | PARAPARA | 2025-01-16 | 9:16 | 2025-01-16 | 16:17 | 0.032575 | 7.7251e-05 | 28 | 11807 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace multiple poles & x-arms between poles 783762 & 783684 | .
925 |  | JE24044594 | 10TH AVE | Eastern | 10TH AVE | 2025-01-16 | 21:03 | 2025-01-17 | 0:38 | 0.00059272 | 2.759e-06 | 1 | 215 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9207-1/2/3 | .
926 |  | JE24044596 | PARK RD | Western | PARK RD | 2025-01-16 | 9:30 | 2025-01-16 | 14:40 | 0.0017096 | 5.5179e-06 | 2 | 620 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove rotten 11kv Buck arms and rotten LV transformer arms on T2228 | .
927 |  | JE24044724 | KATERE 12 | Western | KATERE 12 | 2025-01-16 | 9:36 | 2025-01-16 | 14:43 | 0.0025413 | 8.2769e-06 | 3 | 921 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | PIHMS site. Replace Tx 1306 due to rust and low oil. | .
928 |  | JE24045109 | CAMBRIDGE RD TIRAU | Eastern | CAMBRIDGE RD TIRAU | 2025-01-16 | 8:46 | 2025-01-16 | 16:55 | 0.0094591 | 1.9313e-05 | 7 | 3428 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Shut 2 Cross- arm replacement: HINTIR085, HINTIR094, 264752, 264751. Pole replacement: E12352. D12349/D12350 - H Structure remove redundant 33kV ABS; remove redundant 33kV Recloser; remove redundant hardware & earth wire | .
929 |  | JE25001464 | 13 CAMPBELL STREET,WHITIANGA,WHITIANGA | Eastern | JOAN GASKELL DR | 2025-01-16 | 6:53 | 2025-01-18 | 14:51 | 0.072045 | 0.00033659 | 61 | 26113 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Fuses Location: Fused/Sw 9238/3 No. Fuses: 3 Fuse Amp Size: 31.5A TIME CLOSED: Cause: Cable fault Weather (wind/rain): Calm Follow up required (select advisory)? Yes, cable fault, Genset connected at 400V TC3760 tails at 13:45 DNO 2501008 Cable was repaired and returned into service 18/01/25 | .
930 |  | JE25001465 | 1220 RANGITIKEI LINE,NEWBURY,PALMERSTON NORTH | Western | TE ARAKURA | 2025-01-16 | 5:18 | 2025-01-16 | 7:16 | 0.00065194 | 5.5179e-06 | 2 | 236 | Unplanned | WILDLIFE - BIRD | Fuses Location: D88 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 07:15 Cause: Bird strike Weather (wind/rain): Fine Follow up required (select advisory)? Full power restored | .
931 |  | JE25001541 | unknown MIKIMIKI ROAD,Mikimiki,Rural | Western | MOUNT BRUCE | 2025-01-16 | 12:03 | 2025-01-16 | 12:09 | 0.00095143 | 0.00015726 | 57 | 345 | Unplanned | THIRD PARTY SERVICES - CUSTOMER REQUEST | Turned power Off for safety House / Woolshed to close to Lines Isolated at fuses 7030 Off at 1203 On at 1209 High load permit 0006785 | .
932 |  | JE25001551 | JE25001550 - 18 KAIWHA ROAD,WELCOME BAY,TAURANGA | Eastern | BRUCE RD | 2025-01-16 | 13:21 | 2025-01-16 | 15:15 | 0.0069084 | 6.0697e-05 | 22 | 2504 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | Fuses Location: SD4-130 No. Fuses: 2 Fuse Amp Size: 15a TIME CLOSED: 1515 Cause: branch on lines Weather (wind/rain): rain Follow up required (select advisory)? | .
933 |  | JE24043720 | LONGBUSH | Western | LONGBUSH | 2025-01-15 | 9:01 | 2025-01-15 | 15:11 | 0.05002 | 0.00013519 | 49 | 18130 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles and hardware past S333 . Install links 11494 at pole 823335 . | .
934 |  | JE24043775 | OMOKOROA RD | Eastern | OMOKOROA RD | 2025-01-15 | 23:31 | 2025-01-16 | 1:56 | 0.00040083 | 2.759e-06 | 1 | 145 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9262/1/2/3 | .
935 |  | JE24043778 | APITI | Western | APITI | 2025-01-15 | 9:50 | 2025-01-15 | 14:10 | 0.00071724 | 2.759e-06 | 1 | 260 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | G&B cut jumpers for isolation to replace DDO'S and transformer T4/290 and reconnect G&B DDO'S at pole P04074/P04075 | .
936 |  | JE24043947 | PURIRI | Eastern | PURIRI | 2025-01-15 | 9:44 | 2025-01-15 | 14:53 | 0.013641 | 4.4143e-05 | 16 | 4944 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV & 400V xarms at poles S12828, S0376 and S12834 | .
937 |  | JE24043969 | PATETONGA | Eastern | PATETONGA | 2025-01-15 | 8:46 | 2025-01-15 | 14:51 | 0.081565 | 0.00022348 | 81 | 29564 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV poles, crossarms and conductor between poles 263717 & K13384 | .
938 |  | JE24043997 | FAIRWAY DR | Eastern | FAIRWAY DR | 2025-01-15 | 9:46 | 2025-01-15 | 10:50 | 0.010313 | 0.00016002 | 58 | 3738 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACING J-TYPE LV FUSES AT TX TC3799. REQUIRE TX ISOLATION | .
939 |  | JE24044017 | LINTON | Western | LINTON | 2025-01-15 | 8:55 | 2025-01-15 | 15:27 | 0.015125 | 3.8625e-05 | 14 | 5482 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Vegetation cutting Between poles P25893 to P00136 | .
940 |  | JE24044141 | OTARAOA RD | Western | OTARAOA RD | 2025-01-15 | 9:46 | 2025-01-15 | 15:05 | 0.033414 | 0.00010484 | 38 | 12111 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | to change trany structure tx3781 with new pole plus change lv xarms on pole 760964. | .
941 |  | JE24044218 | OAKURA | Western | OAKURA | 2025-01-15 | 9:00 | 2025-01-15 | 14:51 | 0.27178 | 0.00078355 | 284 | 98509 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove ABS's 328 and 149 from poles 756088 and 756086 respectively and connect with Permanent jumpers | .
942 |  | JE24044225 | INLAND COAST | Western | INLAND COAST | 2025-01-15 | 9:30 | 2025-01-15 | 13:44 | 0.038429 | 0.00015174 | 55 | 13929 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 759073 with a new B11 and replace ABS 41 with a new horizontal ABS | .
943 |  | JE24044258 | BETHLEHEM | Eastern | BETHLEHEM | 2025-01-15 | 9:01 | 2025-01-15 | 16:35 | 0.37343 | 0.00082217 | 298 | 135352 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV pole 860319 | .
944 |  | JE24044281 | PUTORINO | Western | PUTORINO | 2025-01-15 | 11:21 | 2025-01-15 | 13:38 | 0.0045236 | 3.3108e-05 | 12 | 1640 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Defected pole 805534 & Replace 11KV X-Arm on pole 805508 | .
945 |  | JE24044722 | GLOVER RD EAST | Western | GLOVER RD EAST | 2025-01-15 | 10:33 | 2025-01-15 | 12:00 | 0.015671 | 0.00017933 | 65 | 5680 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Tx 5450E, replace 400V disconnect. | .
946 |  | JE24045049 | TE MATAI RD | Eastern | TE MATAI RD | 2025-01-15 | 9:17 | 2025-01-15 | 15:02 | 0.012828 | 4.4143e-05 | 15 | 4650 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 1. Remove P/M TX TE6-145, transfer LV to new G/M TX TP4508 connected to Fuse/Sw 14829/2. 2. Remove P/M TX TP2216, transfer LV to new G/M TX TP4511 connected to Fuse/Sw 14830/4. 3. Remove cable from Fuses SE6-006, join cable and connect TX TE6-201 to Fuse/Sw 14830/2. 4. Remove OH Line 224857 to 855791. 5. Remove cable from Fuses SE6-057, join cable and connect TX TE6-104 to Fuse/Sw 14836/2. 6. Remove cable from Fuses SE6-219, join cable and connect TX TE6-282 to Fuse/Sw 14836/4 | .
947 |  | JE24045229 | RAILWAY ST | Eastern | RAILWAY ST | 2025-01-15 | 10:36 | 2025-01-15 | 11:54 | 0.012551 | 0.00016002 | 58 | 4549 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV xarm at pole N0348 | .
948 |  | JE25001318 | 93 MOSSTON ROAD,CASTLECLIFF,WANGANUI | Western | HEADS RD | 2025-01-15 | 3:22 | 2025-01-15 | 4:46 | 0.18027 | 0.0040033 | 1217 | 65341 | Unplanned | WILDLIFE - POSSUM | REGULATORY INFORMATION Voltage & Device ID: REC 4775 Protection flags (nil where none): EF CAUSE: Possum Location: Pole 707645 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: cursory Weather (wind/rain): Fine LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: This is a very large ICP count for a recloser. Could we look into another protective device or installing LFI's to reduce outage area or fault finding time. | .
949 |  | JE25001323 | 1549 SOUTH ROAD,MANAIA,HAWERA | Western | OTAKEHO | 2025-01-15 | 7:38 | 2025-01-15 | 19:04 | 0.034051 | 0.00058766 | 213 | 12342 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Car Versus Pole 717473. No Tripping Isolated at ABS 6894, 6714 to allow replacement of pole. On relivening ABS 6714 was found to be damaged. Isolations moved out to allow ABS 6714 to be cut away & DNO 2501007. DNO to follow 1526 SOUTH ROAD, MANAIA disco A43761 HV line clash full power restored | .
950 |  | JE25001337 | 8 TUAPIRO ROAD, KATIKATI | Eastern | BOWENTOWN | 2025-01-15 | 9:13 | 2025-01-15 | 11:24 | 0.015808 | 0.00036142 | 131 | 5730 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 2 Protection flags (nil where none): Nil CAUSE: Bird strike Location: Pole 396202 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: No Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Bird created a short circuit between the insulators and the line burnt down. 2 x HV pin insulators 5m Namu conductor SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
951 |  | JE25001366 | 575 EAST TARATAHI ROAD,EAST TARATAHI,MASTERTON | Western | SOMERSET RD | 2025-01-15 | 10:03 | 2025-01-15 | 11:18 | 0.0002074 | 2.759e-06 | 1 | 75 | Unplanned | WILDLIFE - BIRD | Fuses Location: T707 No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 11:17 Cause: Magpie Weather (wind/rain): Windy Follow up required (select advisory)? Barrell replace. 2R used for gear. Full power restored. | .
952 |  | JE24041685 | REVANS ST | Western | REVANS ST | 2025-01-14 | 8:30 | 2025-01-14 | 13:35 | 0.0008419 | 2.759e-06 | 1 | 305 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | change 11kv arms from 7260 to end of line | .
953 |  | JE24043550 | MAUNGAKAWA ROAD | Eastern | MAUNGAKAWA ROAD | 2025-01-14 | 9:51 | 2025-01-14 | 15:47 | 0.019643 | 5.5179e-05 | 20 | 7120 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Poles and Xarms replacement multiple sites. Worksite Poles C12678, C12683, C12689, C12690, C12692, C12693, C12695, C12696, C12697 & C12698. | .
954 |  | JE24043588 | NO 3 ROAD | Eastern | NO 3 ROAD | 2025-01-14 | 9:15 | 2025-01-14 | 15:23 | 0.077096 | 0.00020968 | 76 | 27944 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 223446 to 381334 & 223539. Reconductor HV from 223446 to 381334 and 223547 to 223539 | .
955 |  | JE24043592 | KOPANE | Western | KOPANE | 2025-01-14 | 9:00 | 2025-01-14 | 14:18 | 0.011413 | 3.5867e-05 | 13 | 4137 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11KV poles & crossarms between ABS H61 & A55 | .
956 |  | JE24043703 | LINDERMANN RD | Eastern | LINDERMANN RD | 2025-01-14 | 8:43 | 2025-01-14 | 14:35 | 0.05523 | 0.00015726 | 57 | 20018 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv/400vt cross arms @ poles 204491,204492,204493,204494,204495, & 204496. . Isolation point @ SB1-041. | .
957 |  | JE24043725 | SANDHURST | Eastern | SANDHURST | 2025-01-14 | 23:31 | 2025-01-15 | 0:55 | 0.0058226 | 6.8974e-05 | 25 | 2110 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9569/1/2/3 NOC cancelled job, traffic lights affected | .
958 |  | JE24043740 | MAUNGAKAWA ROAD | Eastern | MAUNGAKAWA ROAD | 2025-01-14 | 8:31 | 2025-01-14 | 14:27 | 0.013762 | 3.8625e-05 | 14 | 4988 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole C13422 & HV & LV xarms on poles C13399, C13410 - C13412, C13428 - C13430. | .
959 |  | JE24043789 | OLD TAURANGA RD | Eastern | OLD TAURANGA RD | 2025-01-14 | 9:38 | 2025-01-14 | 13:24 | 0.0093777 | 4.1384e-05 | 15 | 3399 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace xarms at pole P13345 and DDO arm at pole P13346. | .
960 |  | JE24043955 | PARK RD | Western | PARK RD | 2025-01-14 | 9:35 | 2025-01-14 | 15:05 | 0.004561 | 1.3795e-05 | 5 | 1653 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove rotten 11kv Buck arms and rotten LV transformer arms on T2227 | .
961 |  | JE24044008 | LINTON | Western | LINTON | 2025-01-14 | 9:31 | 2025-01-14 | 15:34 | 0.09516 | 0.0002621 | 95 | 34491 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Vegetation cutting between poles P03329 to P03331 & P00128 to P00139 | .
962 |  | JE24044075 | DYERVILLE | Western | DYERVILLE | 2025-01-14 | 9:00 | 2025-01-14 | 12:46 | 0.0086927 | 3.8625e-05 | 14 | 3151 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV pole 811523 and 11kV hardware past fuses 7395 | .
963 |  | JE24044197 | PARAPARA | Western | PARAPARA | 2025-01-14 | 9:16 | 2025-01-14 | 15:51 | 0.030254 | 0.00015174 | 55 | 10966 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace multiple poles & x-arms between poles 783762 & 783684 | .
964 |  | JE24044342 | KOHETE RD | Western | KOHETE RD | 2025-01-14 | 9:01 | 2025-01-14 | 17:06 | 0.04146 | 8.5528e-05 | 31 | 15027 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace xarms at poles 760089,760090,760091,760092,760093,760094,760095,760096 | .
965 |  | JE24044377 | KENNEDY DRIVE | Eastern | KENNEDY DRIVE | 2025-01-14 | 8:43 | 2025-01-14 | 16:09 | 0.13539 | 0.00030349 | 110 | 49073 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace transformer TC3821 | .
966 |  | JE24044653 | SOUTH RD NGARIKI | Western | SOUTH RD NGARIKI | 2025-01-14 | 8:46 | 2025-01-14 | 13:33 | 0.0087141 | 3.0349e-05 | 11 | 3158 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace poles 713098, 713099, 711936, 713101, 713102, 713107, 713109, 713111 & 713112 | .
967 |  | JE24044663 | CARLTON AVE | Western | CARLTON AVE | 2025-01-14 | 9:03 | 2025-01-14 | 15:15 | 0.15192 | 0.0012471 | 297 | 55066 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Poles 769150, 769152, 443188, 769159, 769727 and install new pole at boundary of 64 Alma Road | .
968 |  | JE24044983 | TOTMANS RD | Eastern | TOTMANS RD | 2025-01-14 | 9:05 | 2025-01-14 | 16:57 | 0.0091085 | 1.9313e-05 | 7 | 3301 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Shut 1 HINTIR001/E12359 Replace Pole Remove 33kV ABS 3821 Re-attach crucifix and 11kV cable up pole | .
969 |  | JE25000848 | recloser_9420 | Eastern | TIROHIA-KARANGAHAKE | 2025-01-14 | 9:51 | 2025-01-20 | 17:24 | 0.027964 | 0.00037798 | 137 | 10136 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Generation Site - Paeroa Sub - Tirohia Karangahake - REC 9420 - Supplies Tirohia Landfill Contact Control REC.9420 tripped with no trip flags. Faultman got in contact with Tirohia Landfill operator, there CB was opened REC 9420 closed it tripped, Faultman then asked for there Metering isolator to be opened and REC. 9420 was closed and stayed closed, Faultman advised operator & electrician that it was alive up to the metering unit and they will need to look for fault on there side. The operator reported that the person that did all the work on site was on holiday. 14/01/25 Faultman asked for isolation again at ABS IP191 to Issue Assurance to Tirohia Landfill to Fault find | .
970 |  | JE25001176 | 1 MARTINS ROAD,MARTINBOROUGH,MARTINBOROUGH | Western | COLOGNE ST | 2025-01-14 | 5:02 | 2025-01-14 | 6:49 | 0.072723 | 0.0006787 | 246 | 26359 | Unplanned | WILDLIFE - POSSUM | REGULATORY INFORMATION Voltage & Device ID: 11kV, Rec C638/2 Protection flags (nil where none): E/F, B phase CAUSE: Opossum Location: Pole 816559 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Yes / Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Opossum removed from lines using Hot Stick SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
971 |  | JE25001279 | 231 MASTERTON CASTLEPOINT ROAD, MATAIKONA, MASTERTON | Western | CASTLEPOINT | 2025-01-14 | 17:00 | 2025-01-14 | 19:01 | 0.015359 | 0.00012691 | 46 | 5567 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Fuses 7883 Protection flags (nil where none): na CAUSE: Centre Bolt fell out & Crossarm tipped over Location: Pole 478211 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Reported into NOC Weather (wind/rain): Windy LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
972 |  | JE25001292 | FEEDER FAULT - OMANU SUB - BAYFAIR - CB4 | Eastern | BAYFAIR | 2025-01-14 | 15:45 | 2025-01-14 | 16:18 | 0.048003 | 0.001465 | 531 | 17399 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: CB 4 Protection flags (nil where none): Ph B-OC CAUSE: Tree Branch Location: Pole 214304 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): None Follow up Required (select advisory)? No Additional fault restoration comments: Branch sitting on the LV. Could have brushed the HV on its way down. Removed with hot stick, power restored 16:17Hrs SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): No Circuit that tripped: N/A DTF (KM): N/A | .
973 |  | JE25001293 | 2 STRATHMORE DRIVE,AONGATETE,KATIKATI | Eastern | WILLS RD | 2025-01-14 | 18:14 | 2025-01-14 | 22:06 | 0.0048767 | 2.4831e-05 | 9 | 1768 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 4// Fuses SB2-034 Protection flags (nil where none): Nil CAUSE: Cable fault Location: Temp generation (state details when used): Yes PERFORMANCE DETAIL DNO (number or state No): 2501006 Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: TCB made at 400V bushings at transformer TB2-083 for the generator connection genset running at 22:05. 11kV TCB made at transformer TB2-081, cable piggy back connection made on HV bushings. Emap dressed with Genset and cable break | .
974 |  | JE25001299 | 60 AERODROME ROAD,MOUNT MAUNGANUI,TAURANGA | Eastern | MACDONALD ST | 2025-01-14 | 16:22 | 2025-01-14 | 16:45 | 6.3567e-05 | 2.759e-06 | 1 | 23 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: GMCB 13654/4 No. Fuses: Circuit Breaker Fuse Amp Size: N/A TIME CLOSED: 16:45 Cause: Unknown - Could be under voltage due to earlier feeder fault ON OMANU 4 Weather (wind/rain): Calm Follow up required (select advisory)? No Reset and closed GMCB 16:45 power restored | .
975 |  | JE24043614 | MVILLE SOUTH | Eastern | MVILLE SOUTH | 2025-01-13 | 8:31 | 2025-01-13 | 15:18 | 0.34189 | 0.00083872 | 304 | 123920 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Pole I13531: Replace existing pole with a 12.5m Busck Level 1: (10.298m) B3Â²/T2 (12 x Racoon Deadends) Install a set of PLP 11kV swing links on the side of the pole towards pole 384472 Level 2: (8.620m) Install a Side mounted ENTEC Load Break Switch. Surge arrestors to be fitted on both sides of the switch Level 3: (6.894m) b3/p (16mm cu) Level 4: (6.894m) a2/t Fly arm (16mm Cu) | .
976 |  | JE24043793 | MAURICEVILLE | Western | MAURICEVILLE | 2025-01-13 | 9:31 | 2025-01-13 | 12:03 | 0.0255 | 0.0001683 | 61 | 9243 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace stub pole and 11kV stay on recloser 10899 | .
977 |  | JE24044236 | BULLS | Western | BULLS | 2025-01-13 | 9:48 | 2025-01-13 | 13:23 | 0.0023734 | 1.1036e-05 | 4 | 860 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Straighten pole & replace 376937 & Replace 11KV X-arm to double termination. | .
978 |  | JE24044608 | RANGIURU | Eastern | RANGIURU | 2025-01-13 | 9:25 | 2025-01-13 | 15:24 | 0.016782 | 4.6902e-05 | 17 | 6083 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 1. Replace pole 220929, install Links 14821& term UG cable up pole 2. Replace P/M TE6-011 with G/M TE6-011 and transfer load. 3. Remove OH 11kV from 220937 (John Bird Rd) to 323952 (Te Matai Rd) 4. Terminate 11kV UG Cable from 14827/2 up pole 220937 (SE6-108 â€“ John Bird Rd) 5. Remove OH 11kV from 220929 to 220935 including ABS SE6-231. 6. Install UG cable from 220929 via 14825/1 to liven 8x RMU's | .
979 |  | JE25000789 | ATHENREE | Eastern | ATHENREE | 2025-01-13 | 8:50 | 2025-01-13 | 14:36 | 0.059014 | 0.00017106 | 62 | 21390 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Repair damaged 11kv cable at pole 207394 and reinstate cable break then reinstate cable break at 207500 and liven. REMOVES DNO2501003 | .
980 |  | JE25001169 | unknown TAWERA ROAD,Mangatainoka,Pahiatua | Western | RUAWHATA | 2025-01-13 | 20:23 | 2025-01-13 | 20:57 | 0.00046562 | 1.3795e-05 | 5 | 169 | Unplanned | WILDLIFE - BIRD | Fuses Location: T7/501 No. Fuses: 2 Fuse Amp Size: 2 TIME CLOSED: 20:56 Cause: Bird strike Weather (wind/rain): calm Follow up required (select advisory)? | .
981 |  | JE25000989 | 641 PYES PA ROAD, PYES PA, TAURANGA, 3173 | Eastern | PYES PA | 2025-01-12 | 3:37 | 2025-01-12 | 12:34 | 0.017845 | 0.0014678 | 532 | 6468 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Car V Pillar Police Called in Faultman found car had hit transformer T5054 and is all damaged, and has oil that has leaked out that needs to be dug up and transformer needs to be replaced in morning. To isolate Transformer T5054 CB 1 had to be opened as to dangerous to open Fuses FP1288 alive - to close to damaged transformer. Replaced GM DTX T5054 200KVA Transformer Power Restored 12:33 12/01/25 | .
982 |  | JE25000999 | JE25000995 - 357 MILLERS ROAD,PAHIATUA,PAHIATUA | Western | RUAWHATA | 2025-01-12 | 6:57 | 2025-01-12 | 9:07 | 0.0014365 | 1.1036e-05 | 4 | 521 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Q75 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 0907 Cause: Unknown Weather (wind/rain): fine Follow up required (select advisory)? | .
983 |  | JE25001005 | 519 TIRIRAUKAWA ROAD,TAIHAPE,TAIHAPE | Western | MATAROA A | 2025-01-12 | 9:45 | 2025-01-12 | 14:40 | 0.0056918 | 1.9313e-05 | 7 | 2063 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Outage from Fuses 914 to replace insulator at Pole 795155 & remove trees that were contacting lines. Suspect insulator caused the fault but trees removed while the power was off. | .
984 |  | JE25001032 | 353 NORFOLK ROAD LOWER,NORFOLK,INGLEWOOD | Western | KAIMATA | 2025-01-12 | 19:19 | 2025-01-12 | 20:38 | 0.00021739 | 2.759e-06 | 1 | 79 | Unplanned | WILDLIFE - BIRD | Fuses Location: 8851 No. Fuses: 2 Fuse Amp Size: 3 amp TIME CLOSED: 20:37 Cause: Bird Strike Weather (wind/rain): Windy Follow up required (select advisory)? N | .
985 |  | JE25000952 | 162 HAPAI ROAD,OTWAY,TE AROHA | Eastern | THOMAS ROAD | 2025-01-11 | 1:03 | 2025-01-11 | 3:06 | 0.0077756 | 6.3456e-05 | 23 | 2818 | Unplanned | WILDLIFE - BIRD | Fuses Location: FP182 No. Fuses: 3 Fuse Amp Size: 10A TIME CLOSED: 0305 Cause: Bird strike Weather (wind/rain): Calm Follow up required (select advisory)? No | .
986 |  | JE25000955 | 544 HIMATANGI BLOCK ROAD,FOXTON,FOXTON | Western | BAINESSE | 2025-01-11 | 5:43 | 2025-01-11 | 7:58 | 0.0022287 | 1.6554e-05 | 6 | 808 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: B32 No. Fuses: 2 Fuse Amp Size: 10 Amp TIME CLOSED: 07:57 Cause: Unknown Weather (wind/rain): Windy Follow up required (select advisory)? N | .
987 |  | JE25000957 | 787 ,, | Eastern | BOWENTOWN | 2025-01-11 | 10:13 | 2025-01-11 | 14:30 | 0.0093699 | 4.4143e-05 | 16 | 3396 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Fuses Location: SA2-018 blown on arrival, cable fault between Fuses SA018 & Link box SA2-037. 400V Generation installed. DNO 2501005 created | .
988 |  | JE25000959 | 1807 KAHUTARA ROAD,KAHUTARA,FEATHERSTON | Western | KUMENGA | 2025-01-11 | 10:56 | 2025-01-11 | 12:28 | 0.00025433 | 2.759e-06 | 1 | 92 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: Blown Fuses @ Fuses 7302 11kV Cable Saddles Failed , Slipped down pole , leads tightened & Bird caused Flashover, Blowing lead off. Protection flags (nil where none): nil CAUSE: 11kV Cable Saddles Failed , Slipped down pole , leads tightened & Bird caused Flashover, Blowing lead off Location: @ pole 799377 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Tested ( Failed) Weather (wind/rain): Fine LFI (Y/N + Comments): nil Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
989 |  | JE25000965 | corner of Hawken and Waiinu beach rd | Western | WAITOTARA | 2025-01-11 | 13:56 | 2025-01-11 | 15:13 | 0.022909 | 0.00029797 | 108 | 8303 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Arcing at Pole 774698 Isolated at ABS's 4088 & 4077 Fuse base & Carrier replaced at Fuses 2716 | .
990 |  | JE25000973 | unknown unknown ,Kahutara,Rural | Western | DAIRY FACTORY | 2025-01-11 | 15:00 | 2025-01-11 | 16:08 | 0.00018756 | 2.759e-06 | 1 | 68 | Unplanned | WILDLIFE - BIRD | Fuses Location: 7239 No. Fuses: 2 Fuse Amp Size: 2 TIME CLOSED: 16::07 Cause: bird strike Weather (wind/rain): windy Follow up required (select advisory)? | .
991 |  | JE25000978 | 541A HENRY WATSON ROAD,RICHMOND DOWNS,WALTON | Eastern | STATION RD | 2025-01-11 | 17:53 | 2025-01-11 | 18:57 | 0.00035555 | 5.5179e-06 | 2 | 129 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Tfr TC4381 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 18:56 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? | .
992 |  | JE24043635 | MOAWHANGO | Western | MOAWHANGO | 2025-01-10 | 8:31 | 2025-01-10 | 13:05 | 0.0045382 | 1.6554e-05 | 6 | 1645 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Trees to be trimmed along line past fuses 148. | .
993 |  | JE24043745 | PAHOIA | Eastern | PAHOIA | 2025-01-10 | 8:32 | 2025-01-10 | 12:00 | 0.0017212 | 8.2769e-06 | 3 | 624 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace Pole 209510 with a new 11kV concrete busck | .
994 |  | JE24044165 | GULLIVER RD | Eastern | GULLIVER RD | 2025-01-10 | 11:45 | 2025-01-10 | 12:00 | 0.0024936 | 0.0001683 | 61 | 904 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install LFI's on Pole 224190 while line is isolated. | .
995 |  | JE24044177 | FORDELL | Western | FORDELL | 2025-01-10 | 9:00 | 2025-01-10 | 13:27 | 0.025776 | 9.6564e-05 | 35 | 9343 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace two pole structure 791313, 791314, | .
996 |  | JE24044283 | TIKORANGI | Western | TIKORANGI | 2025-01-10 | 9:08 | 2025-01-10 | 14:53 | 0.019966 | 5.7938e-05 | 21 | 7237 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Hang and wire recloser 3568 on pole 760782. Terminate overhead lines and run new conductor between recloser pole 3568 & 33kV ABS pole 3564. | .
997 |  | JE24044639 | TOTARA ST | Western | TOTARA ST | 2025-01-10 | 9:31 | 2025-01-10 | 12:13 | 0.061428 | 0.00037798 | 137 | 22265 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv insulators at poles 828339 and 828305 | .
998 |  | JE25000840 | 294 WHANGAEHU BEACH ROAD,WHANGAEHU,WANGANUI | Western | FORDELL | 2025-01-10 | 5:00 | 2025-01-10 | 6:26 | 0.00071607 | 8.2769e-06 | 3 | 260 | Unplanned | WILDLIFE - BIRD | Fuses Location: 4018 No. Fuses: 2 Fuse Amp Size: 6 Amp TIME CLOSED: 06:26 Cause: Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? N | .
999 |  | JE25000842 | 6 CHURCH STREET,GATE PA,TAURANGA | Eastern | CAMERON RD | 2025-01-10 | 7:01 | 2025-01-10 | 10:17 | 0.074253 | 0.0011615 | 421 | 26913 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC. 9917/2 Protection flags (nil where none): E/F CAUSE: Cable Fault Location: Between pole 386034 & Sw/Gear 13212/3 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): Yes - DNO2501004 Circuit patrolled and type: operational Weather (wind/rain): calm LFI (Y/N + Comments): no Follow up Required (select advisory)? N Additional fault restoration comments: Feeder was sectionalised and fault found between pole 386034 and Sw/Gear 13212/3 Cable break was made at pole 386034 and Sw/Gear 13212/3 is Isolated & Earthed Cable to be repaired under DNO. | .
1000 |  | JE25000871 | 7506 SOUTH ROAD,OKATO,NEW PLYMOUTH | Western | WAREA | 2025-01-10 | 9:17 | 2025-01-10 | 12:15 | 0.0029621 | 1.6554e-05 | 6 | 1074 | Unplanned | WILDLIFE - BIRD | Fuses Location: PU204 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 12:15 Cause: Birdstrike Weather (wind/rain): Calm Follow up required (select advisory)? | .
1001 |  | JE25000947 | 140 HULL ROAD,MOUNT MAUNGANUI,TAURANGA | Eastern | CRANE SUPPLY | 2025-01-10 | 18:42 | 2025-01-10 | 20:59 | 0.0015119 | 1.1036e-05 | 4 | 548 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fused/Sw 13890/2 tripped. Found 1 HV 63A HRC fuse blown, replaced the set 3 x 63A HRC fuses Full power restored | .
1002 |  | JE24043697 | RANGITANUKU RD | Eastern | RANGITANUKU RD | 2025-01-09 | 9:00 | 2025-01-09 | 15:21 | 0.039857 | 0.00010484 | 38 | 14446 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole E12690 and install new ENTEC tie switch 14971 | .
1003 |  | JE24043817 | PALM SPRINGS | Eastern | PALM SPRINGS | 2025-01-09 | 23:00 | 2025-01-10 | 2:02 | 0.08015 | 0.00044143 | 160 | 29051 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9661 | .
1004 |  | JE24043976 | RONGOMAI | Western | RONGOMAI | 2025-01-09 | 9:31 | 2025-01-09 | 11:09 | 0.004895 | 4.9661e-05 | 18 | 1774 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace red tagged pole P06991 | .
1005 |  | JE24044033 | COLYTON | Western | COLYTON | 2025-01-09 | 8:30 | 2025-01-09 | 14:10 | 0.096682 | 0.00028417 | 103 | 35043 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles and hardware between P38428 and P38494. | .
1006 |  | JE24044182 | KATERE 5 | Western | KATERE 5 | 2025-01-09 | 8:46 | 2025-01-09 | 15:20 | 0.058315 | 0.00015174 | 55 | 21137 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace existing Pole 747008 with a Double Busck 11m. Replace ABS 548 with a new sectionaliser 12750/2 and solid knife links 12750/4 | .
1007 |  | JE24044254 | KOHETE RD | Western | KOHETE RD | 2025-01-09 | 9:00 | 2025-01-09 | 16:18 | 0.01087 | 2.4831e-05 | 9 | 3940 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace xarms @ poles 760022,760023,760024,760025,760026,760030,760031,760032,760033,760034 Job ran over due to equipment issues | .
1008 |  | JE24044272 | OTAKEHO | Western | OTAKEHO | 2025-01-09 | 10:01 | 2025-01-09 | 10:15 | 0.00015873 | 1.1036e-05 | 4 | 58 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | tap down tx M2020 by 1 tap Tapped down from Tap 3 (244V) to Tap 2 (234V) | .
1009 |  | JE25000722 | 742 COACH ROAD,PONGAKAWA,TE PUKE | Eastern | OLD COACH RD | 2025-01-09 | 3:00 | 2025-01-09 | 3:45 | 0.00024867 | 5.5179e-06 | 2 | 90 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Opened all 3 Fuse to trim hedge encroaching lines Time Off 03:00 Time On 03:45 Fuses Location: Transformer TF7-138 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 03:45 Cause: Unknown, SUSPECT TREES .THE CONDUCTORS ARE INSULATED SO IT COULDN'T BE TREES Weather (wind/rain): Calm Follow up required (select advisory)? No | .
1010 |  | JE25000760 | 14 PUKEHOU ROAD,BULLS,BULLS | Western | PAREWANUI | 2025-01-09 | 10:24 | 2025-01-09 | 12:11 | 0.0050177 | 4.6902e-05 | 17 | 1819 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: 612 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 12:10 Cause: unknown Weather (wind/rain): calm Follow up required (select advisory)?n | .
1011 |  | JE25000820 | 35 ROSEMOUNT ROAD,WAVERLEY,WAVERLEY | Western | WAVERLEY | 2025-01-09 | 20:37 | 2025-01-09 | 21:43 | 0.00036115 | 5.5179e-06 | 2 | 131 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Cause: Corrosion What was replaced? 1mtr of conductor, 1x Lug, & 1x Conductor Joint Where was it replaced (pole/TX/pillar box)? Pole 806372 Is 2R required? Yes 2R Y - What is the timeframe for repairs? Complete Additional Info: | .
1012 |  | JE25000826 | FEEDER FAULT - PAPAMOA SUB - RIED RD - CB8 | Eastern | REID RD | 2025-01-09 | 17:45 | 2025-01-09 | 21:36 | 0.052521 | 0.0006456 | 234 | 19036 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 8 Protection flags (nil where none): E/F O/C C Ø CAUSE: Line down Location: Car V Pole Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4, cursory patrolled Weather (wind/rain): Calm LFI (Y/N + Comments): Installed and flagged, But at ABS SD5-008 the LFI did not operate. Follow up Required (select advisory)? Yes LFI non operation Additional fault restoration comments: Car hit pole but left the scene pole scraped, lines broke due to shock loading. Lines were repaired. NDR to Follow SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1013 |  | JE25000835 | 563B MATAI ROAD,MATAMATA,MATAMATA | Eastern | STATION RD | 2025-01-09 | 23:14 | 2025-01-10 | 1:01 | 0.035306 | 0.00036142 | 127 | 12797 | Unplanned | WILDLIFE - POSSUM | REGULATORY INFORMATION Voltage & Device ID: Rec 9664 Auto reclosed / Sec 14403 and 13065 tripped Protection flags (nil where none): E/F B Ø CAUSE: Possum Location: Pole H1751 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4, Cursory patrolled. Weather (wind/rain): Calm LFI (Y/N + Comments): On BRN5 operated, WLN3 Installed but not working Follow up Required (select advisory)? Yes LFIs not working Additional fault restoration comments: Possum found up pole H1751 removed with Hot Stick, no damage to assets SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1014 |  | JE24043738 | MOTUMAOHO | Eastern | MOTUMAOHO | 2025-01-08 | 8:41 | 2025-01-08 | 14:56 | 0.069371 | 0.00018485 | 67 | 25144 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace HV and LV arms on Poles I0726, I0728, I0734, I1186, I1191, 857042, I1197, I1201, I1206, I0748, I13312 No phase rotation required for TP1704 - Pole I1206 - only straightening pole . | .
1015 |  | JE24043746 | WAIPUNA | Eastern | WAIPUNA | 2025-01-08 | 10:15 | 2025-01-08 | 10:41 | 0.0050722 | 0.00019313 | 70 | 1838 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To install LFIs on Pole 484730, 380004 and 320918 | .
1016 |  | JE24043804 | TE PUKE NORTH | Eastern | TE PUKE NORTH | 2025-01-08 | 22:00 | 2025-01-09 | 2:51 | 0.013519 | 4.6902e-05 | 17 | 4900 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9621/2/3/4/5/6/7/8 | .
1017 |  | JE24044074 | DYERVILLE | Western | DYERVILLE | 2025-01-08 | 8:01 | 2025-01-08 | 14:32 | 0.01513 | 3.8625e-05 | 14 | 5484 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV pole 811523 and 11kV hardware past fuses 7395 | .
1018 |  | JE25000625 | unknown SH 1 ,Utiku,Taihape | Western | MANGAWEKA | 2025-01-08 | 4:31 | 2025-01-08 | 6:15 | 0.0020181 | 1.9313e-05 | 7 | 731 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: 4015 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 06:15 Cause: unknown Weather (wind/rain): calm Follow up required (select advisory)?n Line Patrolled | .
1019 |  | JE25000679 | 66 OLIVERS ROAD,TE ORE ORE,MASTERTON | Western | CHURCH ST | 2025-01-08 | 8:51 | 2025-01-08 | 14:20 | 0.0036363 | 1.1036e-05 | 4 | 1318 | Unplanned | VEGETATION - INSIDE ZONE | Part of E00171 planned outage | .
1020 |  | JE25000711 | 181 PARK ROAD,PARKVALE,CARTERTON | Western | PARK RD | 2025-01-08 | 19:32 | 2025-01-08 | 22:58 | 0.019981 | 0.00026762 | 97 | 7242 | Unplanned | LIGHTNING - LIGHTNING STRIKE | REGULATORY INFORMATION Voltage & Device ID: CB C839 Protection flags (nil where none): None CAUSE: Broken Hardware Location: Transformer T1529 -Pole 822369 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Transformer Fuses T1529 blew while trying to reload reliven. Isolated to replace whole set of Fuses. Fuses blew again on relivening after repair. Isolated at the Fuses to replacer Transformer T1529. Transformer replaced and power restored - 23:58Hrs SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): No Circuit that tripped: N/A DTF (KM):N/A | .
1021 |  | JE25000721 | 2200 SOUTH ROAD,OKATO,NEW PLYMOUTH | Western | INLAND COAST | 2025-01-08 | 23:26 | 2025-01-09 | 13:22 | 0.061434 | 0.00024279 | 88 | 22267 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV, Sec 12720/2 Protection flags (nil where none): O/C C phase CAUSE: Faulted Transformer (Suspected lightning strike damage) Location: Tx 1834N Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Yes / Operational Weather (wind/rain): Calm LFI (Y/N + Comments): N/A Follow up Required (select advisory)? n Additional fault restoration comments: Line patrolled, Blown fuses found to TFR 1834N, Feeder livened, LV isolated at TFR 1834N, Reload Re-liven carried out, TFR 1834N Fuses operated, Isolated at TFR 1834N Fuses, Faultman on stand down, customers left off until day crew could organise TFR Replacement, TFR Replaced, Full power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1022 |  | JE24043785 | NGATI MARU | Eastern | NGATI MARU | 2025-01-07 | 8:30 | 2025-01-07 | 15:56 | 0.0012313 | 2.759e-06 | 1 | 446 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kV oil maintenance - 9350/1/2/3 & FC5009/FC5015 | .
1023 |  | JE24044408 | AUROA | Western | AUROA | 2025-01-07 | 10:01 | 2025-01-07 | 10:37 | 0.0046941 | 0.00012967 | 47 | 1701 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace stay wire eye bolt on pole 947806 (old pole 718277) | .
1024 |  | JE25000490 | KAIHERE | Eastern | KAIHERE | 2025-01-07 | 2:19 | 2025-01-07 | 2:27 | 0.045767 | 0.0094467 | 3424 | 16589 | Unplanned | DEFECTIVE EQUIPMENT - ZONE SUBSTATION | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 17 & 19 Protection flags (nil where none): B O/C E/F CAUSE: CB 1 not clearing fault. Location: Kerepehi Sub. Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Nil Weather (wind/rain): Calm LFI (Y/N + Comments): Yes Pole O305 Follow up Required (select advisory)? Yes protection issues regarding CB 1 not clearing possible fault Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Kerepehi Circuit that tripped: T1 & T2 CB 17 & 19 DTF (KM): nil | .
1025 |  | JE25000498 | 7533 TURAKINA VALLEY ROAD,PAPANUI JUNCTION,TAIHAPE | Western | MATAROA A | 2025-01-07 | 9:50 | 2025-01-07 | 15:55 | 0.016109 | 4.4143e-05 | 16 | 5839 | Unplanned | VEGETATION - OUTSIDE ZONE | Trees Through Lines at Pole 843156 - all three fuses at 840 where blown - Line Repaired and Power Restored | .
1026 |  | JE25000607 | unknown INMAN AVENUE,Tokoroa,Tokoroa | Eastern | HARRIS BLOCK | 2025-01-07 | 18:09 | 2025-01-08 | 1:18 | 0.0058804 | 3.3108e-05 | 12 | 2131 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: Transformer TC1602 No. Fuses: 1 Fuse Amp Size: 6A TIME CLOSED: 19:30 Cause: Weather (wind/rain): Follow up required (select advisory)? After re loading and relivening at TC1602. Faultman also realised one fuse was hanging at Main Line Fuses FP1647 Fuses Location: Fuses FP1647 No. Fuses: 1 Fuse Amp Size: 6A TIME CLOSED: 19:40 Cause: Weather (wind/rain): Follow up required (select advisory)? After reloading relivening, 1 fuse each blown at TC1602 and FP1647 Opened TC1602 Fuses and closed Fuses FP1647 Fuses Location: Fuses FP1647 No. Fuses: 1 Fuse Amp Size: 6A TIME CLOSED: 20:05 Cause: Unknown suspect Trf TC1602 Weather (wind/rain): Calm Follow up required (select advisory)? Job ongoing Relivened Transformer but voltages unbalanced at the LV, Isolated to replace transformer Transformer replaced under Access Permit- Power restored 01:18Hrs | .
1027 |  | JE25000610 | 150 OPUA ROAD,OPUNAKE,OPUNAKE | Western | OAONUI | 2025-01-07 | 18:36 | 2025-01-07 | 19:53 | 0.00042443 | 5.5179e-06 | 2 | 154 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: 5307E No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 1952 Cause: loose LV cable flicked into the HV. 2r to restrain the LV conductor as it is also too low on road cross . Weather (wind/rain): Fine Follow up required (select advisory)? | .
1028 |  | JE25000339 | 3 CORNWALL STREET,WAIHI,WAIHI | Eastern | WAITAWHETA | 2025-01-06 | 1:14 | 2025-01-06 | 14:56 | 0.011188 | 0.00013243 | 48 | 4055 | Unplanned | WILDLIFE - POSSUM | REGULATORY INFORMATION Voltage & Device ID: Sectionaliser 9454 Protection flags (nil where none): EF CAUSE: Possum Location: Pole 853520 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Line s patrolled and possum found at Pole 853520, removed with hot stick SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): No Circuit that tripped: N/A DTF (KM):N/A | .
1029 |  | JE25000372 | 1361B STATE HIGHWAY 2,WHAKAMARAMA,TAURANGA | Eastern | PAHOIA | 2025-01-06 | 14:07 | 2025-01-06 | 15:19 | 0.0075677 | 0.00010484 | 38 | 2743 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: CB 3 Protection flags (nil where none): None CAUSE: Deterioration Location: Pole 209196 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): None Follow up Required (select advisory)? No Additional fault restoration comments: Isolated and replaced all 3 set of fuses SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): N/A Circuit that tripped: N/A DTF (KM):N/A | .
1030 |  | JE25000391 | 58 CLOVERLEA ROAD,WESTBROOK,PALMERSTON NORTH | Western | TREMAINE AVE | 2025-01-06 | 11:21 | 2025-01-06 | 12:55 | 0.0012991 | 1.3795e-05 | 5 | 471 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses A/24 x 2 3amp Fuses + T6/146 x 1 x 3amp No. Fuses: 3 Fuse Amp Size: 3amp TIME CLOSED: 12:55pm Cause: Unknown cause Weather (wind/rain): Calm Follow up required (select advisory)? | .
1031 |  | JE25000436 | sub_OMO | Eastern | TE PUNA | 2025-01-06 | 13:47 | 2025-01-06 | 16:25 | 0.078305 | 0.0009684 | 351 | 28382 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | REGULATORY INFORMATION Voltage & Device ID: CB1 Protection flags (nil where none): Phase BC -OC CAUSE: Tree on lines Location: Pole 210308 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): Yes at Pole 496037 Flashing towards SD3-024 Follow up Required (select advisory)? No Additional fault restoration comments: Sectionalised and remove Branch on lines with hot stick. Restoration was delayed due to the Fire brigade requesting power to be left off so that the fire could be extinguished. ETA passed to FENZ of 15-20min trees on lines SHWY 2, Near intersection with Gill Lane | .
1032 |  | JE25000482 | FEEDER FAULT - PAENGAROA SUB - PAENGAROA 4 - REC 13607 | Eastern | YOUNG RD | 2025-01-06 | 17:35 | 2025-01-06 | 19:48 | 0.005856 | 4.4143e-05 | 16 | 2123 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: rECLOSER 13607/2 Protection flags (nil where none): EF CAUSE: Bird Jammed between Crossarm & Pole Pin Insulators @ Pole 484476 Location: Pole 484476 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: oper Weather (wind/rain): Fine LFI (Y/N + Comments): nil Follow up Required (select advisory)? Additional fault restoration comments: Bird Jammed between Crossarm & Pole Pin Insulators @ Pole 484476 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1033 |  | JE25000485 | FEEDER FAULT - LAKE RD - BUCKLAND RD - CB4 | Eastern | BUCKLAND RD | 2025-01-06 | 18:31 | 2025-01-07 | 5:50 | 0.19428 | 0.0014374 | 423 | 70419 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 4 Protection flags (nil where none): A,B, E/F CAUSE: Truck V Pole 489116 Location: Pole 489116 , 4533 S HWY 29 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Reported Weather (wind/rain): slight wind LFI (Y/N + Comments): Yes 100% Pole 851393 Follow up Required (select advisory)? Additional fault restoration comments: High Low Contact, All affected houses Tested & power restored | .
1034 |  | JE25000298 | 15 HENRY ROAD,KATIKATI,KATIKATI | Eastern | WHARAWHARA ROAD | 2025-01-05 | 10:15 | 2025-01-13 | 15:00 | 0.01446 | 8.2769e-05 | 15 | 5241 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Please check JE25000299 on closure Faultman found blown fuse at Fused ABS 652 after unsuccessful reload cables were sectionalised and cable found between out going cable at Links Box TD4-094 to incoming cable at Link Box TB1-095. Generators have been installed on remaining Tfr's. Update outage to hook up new cable approx 2 hours 13/01/25 Cable between Link Boxes TD4-094 & TB1-095repaired under access permit and connected. Generator removed at all concerned transformers and Normal network restored- Normal Power at 15:00Hrs Safety Manager toggled for BESS Generator Incident- Please see Michael Vickers for details - CJ 15/01 | .
1035 |  | JE25000316 | 328 STATION ROAD, MATAMATA, 3400 | Eastern | STATION RD | 2025-01-05 | 15:21 | 2025-01-05 | 17:37 | 0.019199 | 0.00014071 | 51 | 6959 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Chris Brown from North Power call to advise that insulator had come off termination arm as he was driving past. Faultman found termination arm insulator hanging off only held by binder, line was isolated at ABS IC1132 & Sw/Gear 14139/3 to replace insulator and rebind in conductor on pole G0153 | .
1036 |  | JE25000336 | unknown EMERTON ROAD,Waihi Beach,Waihi Beach | Eastern | ATHENREE | 2025-01-05 | 23:24 | 2025-01-06 | 1:13 | 0.017455 | 0.00017106 | 62 | 6327 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Cause: Cable Failed @ Pole 207394 Weather (wind/rain): Fine Follow up required (select advisory)? NAPA 118673 for monday 13th jan 14/01/25 Job completed under NAPA 118673 ON 13/01/24 | .
1037 |  | JE25000221 | 21 MUGGERIDGE ROAD,MANUTAHI,PATEA | Western | MANUTAHI | 2025-01-04 | 1:08 | 2025-01-04 | 12:14 | 0.022551 | 0.00018209 | 66 | 8174 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 12413/2 Protection flags (nil where none): E/F, O/C B & C CAUSE: trees in Private lines Location: Private Pole 846147 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): calm LFI (Y/N + Comments): n Follow up Required (select advisory)? Additional fault restoration comments: Feeder patrolled, Private line down found at Private Pole 846147, due to trees Isolated at Fuses 6745, feeder restored Westside energy notified of fault, Downer have cut the line away from Pole 846147 to make safe as the line was down over the farmers track, Westside Energy will get Obertech in to cut the trees and repair the line Lines repaired and restored | .
1038 |  | JE25000222 | 1456 RANGITATAU EAST ROAD,PAPARANGI,WANGANUI | Western | WESTMERE PEAT ST | 2025-01-04 | 2:51 | 2025-01-04 | 11:37 | 0.044761 | 0.00011036 | 40 | 16224 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 1026 Protection flags (nil where none): E/F, O/C C CAUSE: lines down Location: Between Poles 784217 & 784219 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Line patrolled, LFI flashing at Fuses 838, Faultman found 2 span of lines down between Poles 784217 & 784219 due to tree through lines Isolated at Fuses 838 New crew required to fix lines in day light hours Repaired lines down. Large number of tripping's at this Recloser. Suggest an operational patrol to reduce the numbers of outages | .
1039 |  | JE25000223 | 160 KOHINUI ROAD,MANGATAINOKA,PAHIATUA | Western | RUAWHATA | 2025-01-04 | 4:21 | 2025-01-04 | 6:34 | 0.051933 | 0.00053524 | 194 | 18824 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec Q61 Protection flags (nil where none): E/F, O/C B CAUSE: Broken Insulator due to old age Location: P45961 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): wind, rain LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Line patrolled, Broken Insulator at Pole P45961 Isolated at ABS Q67 & 10271, Back feed put in place Broken Insulator replaced, Full power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1040 |  | JE25000235 | 93 MOSSTON ROAD,CASTLECLIFF,WANGANUI | Western | HEADS RD | 2025-01-04 | 7:55 | 2025-01-04 | 9:09 | 0.22396 | 0.0033577 | 1217 | 81177 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: REC 4775 Protection flags (nil where none): A phase OC CAUSE: Burnt crossarm Location: Pole 707105 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): windy LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: | .
1041 |  | JE25000259 | 8 KAUKATEA VALLEY ROAD,OKOIA,WANGANUI | Western | NO 3 LINE | 2025-01-04 | 6:31 | 2025-01-04 | 11:33 | 0.031668 | 0.00010484 | 38 | 11478 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: 1138 No. Fuses: 2 Fuse Amp Size: 15A TIME CLOSED: 1132 Cause: line clash Weather (wind/rain): windy Follow up required (select advisory)? | .
1042 |  | JE25000263 | 1027 MANGAEHU ROAD,PUNIWHAKAU,STRATFORD | Western | STRATHMORE | 2025-01-04 | 10:33 | 2025-01-04 | 12:51 | 0.0041879 | 3.0349e-05 | 11 | 1518 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: 5453 No. Fuses: 2 Fuse Amp Size: 8A TIME CLOSED: 1251 Cause: suspect line clash Weather (wind/rain): windy Follow up required (select advisory)? | .
1043 |  | JE25000267 | 42 TOKOMARU EAST ROAD,BRUNSWICK,WANGANUI | Western | BRUNSWICK | 2025-01-04 | 7:18 | 2025-01-04 | 13:18 | 0.011909 | 3.3108e-05 | 12 | 4317 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: 986 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 1317 Cause: suspect line clash Weather (wind/rain): Windy Follow up required (select advisory)? | .
1044 |  | JE25000277 | 1281 HORAHORA ROAD,ARAPUNI,PUTARURU | Eastern | HORAHORA | 2025-01-04 | 14:58 | 2025-01-05 | 14:02 | 0.039021 | 0.00025382 | 73 | 14143 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 13780 Protection flags (nil where none): A & B Phase O/C CAUSE: Trees Location: Poles 424612 424663 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Temp Line Breaks in At Poles 424612 & 424663 ( Put on E Map By Coops ) Tree trimmers coming out on Sunday 05/01/25 to remove Trees and then Line Breaks to be Removed on Monday 06/01/25 Only 1 Span Down so no one off now 05/01/25 - Tree crew removed tree from lines and TLB at poles 424612 & 424663 were closed. | .
1045 |  | JE25000159 | 109 CORBETT ROAD,BELL BLOCK,NEW PLYMOUTH | Western | MANGATI RD | 2025-01-03 | 8:11 | 2025-01-03 | 16:16 | 0.088811 | 0.0036115 | 1309 | 32190 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Car V Pole reported by Fire Services Transformer 1557 Pole 947521 not in system CB 6 Opened to de-energize site on request from FM While putting Isolations in Place, there became confusion over which feeder the pole was on. FM Directed to check transformer de-energised. Transformer 351 not 1557. Making CB1 the feeder that needed to be Isolated. Switching done to de-energise site, Transformer 351 checked again Isolated at CB 1 & ABS 278. CB6 left back fed Via ABS 8692, encase it also needed to be Isolated as close to work Area. Traffic management organized along with hydovac Pole 947521 replaced, Cable Damaged TEMP Line break installed at Pole 947521 CB 1 to remain back fed from CB 6 Via Gas/Sw 820/2 Cable to be repaired under planned switching | .
1046 |  | JE25000192 | unknown GLENMORVEN ROAD,Morrisons Bush,Rural | Western | PONATAHI | 2025-01-03 | 12:45 | 2025-01-03 | 14:34 | 0.00060203 | 5.5179e-06 | 2 | 218 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: dtx T1073 No. Fuses: 2 x HV & 2 x Barrels & 2 x 63A LV Fuses Fuse Amp Size: 3 TIME CLOSED: 14:34 Cause: unknown Weather (wind/rain): fine Follow up required (select advisory)? | .
1047 |  | JE25000207 | unknown THAMES COAST ROAD,Te Mata,Rural | Eastern | MANAIA COROMANDEL | 2025-01-03 | 17:05 | 2025-01-04 | 9:05 | 0.0026489 | 2.759e-06 | 1 | 960 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: DTX TC5908 1 phase 15kVA Replaced CAUSE: Lightning Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: Weather (wind/rain): Follow up required (select advisory)? Additional fault restoration comments: | .
1048 |  | JE25000085 | 569A TE AWAITI ROAD, TE AWAITI, MARTINBOROUGH, 5782 | Western | TUTURUMURI | 2025-01-02 | 3:59 | 2025-01-02 | 4:46 | 0.0053071 | 0.00011312 | 41 | 1924 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Coach Bolt Come Out of Arm - Repaired 11kV Crossarm | .
1049 |  | JE25000091 | 26 COLEMAN AVENUE,WAVERLEY,WAVERLEY | Western | WAVERLEY | 2025-01-02 | 6:26 | 2025-01-02 | 11:59 | 0.034942 | 0.00010484 | 38 | 12665 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Transformer found to be faulty Bad test between HV bushes and earth Transformer replaced | .
1050 |  | JE25000136 | 2390 TIKI RD,PREECE POINT,COROMANDEL | Eastern | MANAIA COROMANDEL | 2025-01-02 | 17:27 | 2025-01-02 | 18:05 | 0.0002064 | 5.5179e-06 | 2 | 75 | Unplanned | WILDLIFE - BIRD | Fuses Location: FC:V0258/1 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 18-04 Cause: Duck Weather (wind/rain): Fine Follow up required (select advisory)? | .
1051 |  | JE25000139 | 2062 MORRINSVILLE-WALTON ROAD,RICHMOND DOWNS,WALTON | Eastern | PIAKOITI RD | 2025-01-02 | 18:11 | 2025-01-02 | 20:25 | 0.040313 | 0.0005242 | 190 | 14611 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | RC26 tripped open - Patrolled no Fault found beleive their is a fault with RC26 - Left Isolated and backfeed from other cirucits - DNO to be raised DNO2501001 for Recloser RC26 | .
1052 |  | JE25000152 | unknown SH 3 ,Waverley,Waverley | Western | RANGIKURA | 2025-01-02 | 21:15 | 2025-01-03 | 1:13 | 0.026206 | 0.00018761 | 68 | 9499 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 1112 Protection flags (nil where none): E/F, O/C B CAUSE: Lines down due to bird strike Location: Between Poles 470610 & 470710 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): calm LFI (Y/N + Comments): n Follow up Required (select advisory)? Additional fault restoration comments: line patrolled, lines down mid span found due to bird strike, Isolated at ABS 663 Lines repaired, full power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1053 |  | JE25000155 | 277 LAKE ALICE ROAD,LAKE ALICE,MARTON | Western | LAKE ALICE | 2025-01-02 | 22:37 | 2025-01-03 | 3:56 | 0.048521 | 0.00051593 | 187 | 17587 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 687 Protection flags (nil where none): E/F CAUSE: Lines down, possible Bird strike/line clash Location: between poles 803159 - 803160 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): calm LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: fire comm's called to advise of lines down Cnr of Santoft Rd & Duncan Rd, forest fire, faultman arrived confirmed faulted area, waited until safe to Isolate fault Isolated at Fuses 957 Faultman waited until fire was out and safe to commence repairs, Replaced 2 x conductors in the span between Poles 803159 & 803160 (200m of conductor replaced) faultman inspected downed conductor and found the conductor had splat marks on it which indicated that there was a line clash from a bird strike or flying debris from trees (possible damage from last weeks wind storm) faultman found 80A Fuse loads in Fuses 957, reload & Re-livened with 40A Fuse loads at per Powerco standard for 805kVA of TFR's past Fuses 957 Full Power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1054 |  | JE25000005 | 274 RANGITATAU EAST ROAD,KAI IWI,WANGANUI | Western | WESTMERE PEAT ST | 2025-01-01 | 6:21 | 2025-01-01 | 8:10 | 0.028481 | 0.00030073 | 109 | 10323 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 2032 Protection flags (nil where none): E/F, O/C A CAUSE: unknown Location: na Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): wind, rain LFI (Y/N + Comments):n Follow up Required (select advisory)? Additional fault restoration comments: Line patrolled, no fault found, full power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1055 |  | JE25000009 | unknown BALLANCE VALLEY ROAD,Ballance,Rural | Western | MANGATAINOKA | 2025-01-01 | 7:58 | 2025-01-01 | 9:55 | 0.0041879 | 3.5867e-05 | 13 | 1518 | Unplanned | WILDLIFE - BIRD | Fuses Location: R27 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 09:54 Cause: Bird strike Weather (wind/rain): calm Follow up required (select advisory)?n Line patrolled | .
1056 |  | JE25000012 | sub_KAR - recloser 10428 | Western | KOPANE | 2025-01-01 | 8:50 | 2025-01-01 | 11:24 | 0.083707 | 0.0013657 | 495 | 30340 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 10428/2 & Sec 10903/2 Trip Protection flags (nil where none): E/F, O/C B CAUSE: Broken Insulator (due to old age) Location: P32038 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): calm LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Fire comm's called in a pole on fire after feeder tripped, faultman confirmed correct Pole, Rec 10428/2 closed Isolated at Links 10903/4 & 10833/4 Broken Insulator replaced, Full power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1057 |  | JE25000023 | 21 TE WHITI SETTLEMENT ROAD,TE WHITI,MASTERTON | Western | PUKETIRO | 2025-01-01 | 11:08 | 2025-01-01 | 12:16 | 0.0062503 | 9.1046e-05 | 33 | 2265 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Blown Jumper at Fused ABS 8080 Isolated at Fuses 7639 Due to old age | .
1058 |  | JE25000034 | unknown LUND ROAD,Aongatete,Rural | Eastern | KATIKATI | 2025-01-01 | 13:09 | 2025-01-01 | 14:17 | 0.018623 | 0.0002759 | 100 | 6750 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Blown jumper at Fuses SC1-005 Isolated at Sec 13179 Repaired Jumper Full Power restored | .
1059 |  | JE25000035 | sub_KAI - REC 2032 | Western | WESTMERE PEAT ST | 2025-01-01 | 13:11 | 2025-01-01 | 17:57 | 0.069161 | 0.00030073 | 109 | 25068 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 2032 Protection flags (nil where none): E/F, O/C A CAUSE: Broken Insulator Location: 784082 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): wind, rain LFI (Y/N + Comments): n Follow up Required (select advisory)? Additional fault restoration comments: Line patrolled, broken insulator found at Pole 784082, Isolated at ABS 085, Insulator replaced, full power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1060 |  | JE25000054 | 1003A PONATAHI ROAD,MARTINBOROUGH,CARTERTON | Western | COLOGNE ST | 2025-01-01 | 19:48 | 2025-01-01 | 21:10 | 0.009716 | 0.00011864 | 43 | 3522 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Voltage & Device ID: 11kV CB C955 - 11kV REC S518 Protection flags (nil where none): B C - TRIP Weather (wind/rain): Rain - Wind Follow up required (select advisory): NIL LFI Activation: Y/N Yes 13601431 - B - C Flags Down Stream CB C955 Offload Load past Gas/Sw11487 for Fault Finding - Tripping Between Gas/Sw 11487 and Rec S518 - On Patrol Found Floating Conductor at Pole 819143 - Line Was isolate and insulator repaired. | .
1061 |  | JE25000057 | 2062 MORRINSVILLE-WALTON ROAD,RICHMOND DOWNS,WALTON | Eastern | PIAKOITI RD | 2025-01-01 | 17:36 | 2025-01-01 | 19:41 | 0.029102 | 0.0005242 | 190 | 10548 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Recloser RC26 Was Found Open, Loss Communication to Recloser RC26 - Was previously fixed on the 30th of December Raido Was found off and ants in the control Box, Line Was Patrolled and Sectionlized and nothing found. | .
1062 |  | JE24048023 | 3 CLOTEN ROAD,STRATFORD,STRATFORD | Western | CLOTON RD NORTH | 2024-12-31 | 3:42 | 2024-12-31 | 19:28 | 0.40024 | 0.009695 | 928 | 145068 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 5 Protection flags (nil where none): E/F, O/C B CAUSE: Broken Insulator (hair line crack) Location: 741519 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): wind, rain LFI (Y/N + Comments): installed on the line but the fault current was not enough to activate LFIs Follow up Required (select advisory)? n Additional fault restoration comments: unable to put automated back feeds in due to faulty Gas/Sw 6283(would not operate manually onsite for faultman) and Rec 12155 not in service due to being faulty, so CB 5 tripped multiple times hard to find fault, Line patrolled multiple times, LFI's installed down the line (would not activate), not enough fault current to blow the insulator up just enough to trip CB 5 all TFR's off loaded, 2 Amp fuse's used to liven line(any larger would trip CB 5), depending on the weather at the time the line would liven for a period of time and then trip or trip straight away, once the weather fined up more a thermal camera used to locate faulty insulator. hair line crack in insulator found at Pole 741519, Isolated at Fused ABS 5454, faulty insulator replaced, faulty looking lightning arrestor earth removed with hot stick at Pole 741482 | .
1063 |  | JE24048025 | 274 RANGITATAU EAST ROAD,KAI IWI,WANGANUI | Western | WESTMERE PEAT ST | 2024-12-31 | 3:59 | 2024-12-31 | 9:57 | 0.037445 | 0.000309 | 112 | 13572 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 2032 Protection flags (nil where none): O/C C CAUSE: Tree on lines Location: Between Poles 846290 - 781921/781922 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): wind, rain LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Line patrolled, Tree on lines found, Isolated at Fuses 4186, Faultman left site as they had run out of hours, new faultman turned up, Tree Removed, Full power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1064 |  | JE24048031 | 17 RIVERSDALE RD,WAIHAKEKE,CARTERTON | Western | TAVERNER ST | 2024-12-31 | 8:44 | 2024-12-31 | 9:33 | 0.0041951 | 8.5528e-05 | 31 | 1521 | Unplanned | WILDLIFE - BIRD | Centre Phase 11kv Lead on Fuses 7547 Blown Off - Isolated at Fuses 7547 for Repairs On Re Inspection of line after Livening found 1 x Centre Phase Fuse Blown at Fuses 11207 Fuses Location: 11207 No. Fuses: 1 Fuse Amp Size: 6A TIME CLOSED: 09:45 Cause: Bird Strike Weather (wind/rain): Rain Follow up required (select advisory)? NIL | .
1065 |  | JE24048037 | 996 RANGIOTU ROAD,RANGIOTU,PALMERSTON NORTH | Western | BAINESSE | 2024-12-31 | 8:45 | 2024-12-31 | 12:50 | 0.00067406 | 2.759e-06 | 1 | 244 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T1/569 No. Fuses: 1 Fuse Amp Size: 2 TIME CLOSED: Failed Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n Isolated & Earthed TFR T1/569 Fuses Replaced TFR, Full power restored | .
1066 |  | JE24048060 | unknown RANGITATAU EAST ROAD,Paparangi,Rural | Western | WESTMERE PEAT ST | 2024-12-31 | 10:30 | 2025-01-01 | 14:10 | 0.013742 | 8.2769e-06 | 3 | 4981 | Unplanned | VEGETATION - OUTSIDE ZONE | Tree through lines between Poles 481146 - 784177/784178 Isolated at Fuses 16077 Faultman will be back on the 01/01/25 as more crew and equipment are required as the lines down are in a pine forest, Customer off X1754 have a generator connected 01/01/25 - Tree cleared away from lines, lines repaired, full power restored Ongoing issue around these fuses, large pine forest that has been let go, no line corridor, trees are close to the lines Line was restored after feeder fault completed JE25000035 | .
1067 |  | JE24048075 | sub_KEG - CB13 | Western | ARMSTRONG ST | 2024-12-31 | 10:14 | 2024-12-31 | 17:18 | 0.054763 | 0.00034763 | 126 | 19849 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 13 Protection flags (nil where none): E/F, O/C A, B & C CAUSE: Blow up in Switch Gear due to Moisture ingress Location: 10181 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): calm, has been wet and windy LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Blow up on Sw/Gear 10181/1 & /3 due to cable boosts slipping down slightly and moisture ingress causing tracking across phases, Sw/Gear isolated at ABS D49 & Sw/Gear 314, faulty Sw/Gear replaced, full power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1068 |  | JE24048082 | 953 STATE HIGHWAY 29, TAURANGA | Eastern | KAIMAI DRIVE | 2024-12-31 | 14:51 | 2024-12-31 | 17:33 | 0.0089363 | 5.5179e-05 | 20 | 3239 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: LV & HV Arm Rotten Outage to replace Both What was replaced? HV & LV Cross Arm Where was it replaced (pole/TX/pillar box)? Pole 211514 Is 2R required? Y 2R Y - What is the timeframe for repairs? by the end of the day 31/12/24 Additional Info: Repairs Completed Crossarm being replaced by the end of the day, fm will call back once completed, site safe On Closer inspection when the crew where about to replace LV Arm they identified the HV Arm was unsafe, Network Isolated and repair of both Crossarms was conducted. | .
1069 |  | JE24048102 | 1580 WHITE ROCK ROAD,TUTURUMURI,MARTINBOROUGH | Western | HAU NUI 33KV | 2024-12-31 | 13:22 | 2024-12-31 | 15:45 | 0.00039476 | 2.759e-06 | 1 | 143 | Unplanned | WILDLIFE - BIRD | Fuses Location: 7920 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 15:45 Cause: Birds Weather (wind/rain): Rain Follow up required (select advisory)? NIL Job was logged to incorrect address job created to show correct location. | .
1070 |  | JE24048107 | 402 MILSON LINE,NEWBURY,PALMERSTON NORTH | Western | TE ARAKURA | 2024-12-31 | 14:57 | 2024-12-31 | 18:47 | 0.011685 | 0.00030349 | 110 | 4235 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | ETA 20-30 MINS Car V Pole, No Damage to Pole P39245 where the car hit but a Broken Cross Arm was found Incorrect Area Isolated as job info indicated fault was around TFR T2/182, (ABS D3 & D78) This was corrected by faultman Correct TFR was T2/383, this was only after power had been turned off, power restored Correct Back Feeds put in place, Sec 10249/2 would not operate, job raised for tech to investigate, Tech got Sec operational, new batteries required, JE24048130 was an indication error job as a whole lot of alarm were coming through when tech was trying to open onsite Isolated at ABS D80, D79/1, Links D79/6 & 10249/6 Broken Cross Arm Replaced at Pole P39245, Full Power Restored | .
1071 |  | JE24048109 | 1027 MANGAEHU ROAD,PUNIWHAKAU,STRATFORD | Western | STRATHMORE | 2024-12-31 | 14:17 | 2025-01-01 | 9:41 | 0.035323 | 3.0349e-05 | 11 | 12803 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: 5453 No. Fuses: 2 Fuse Amp Size: 8 TIME CLOSED: 09:41 Cause: Line clash due to Weather Weather (wind/rain): wind, rain Follow up required (select advisory)?n Line patrolled | .
1072 |  | JE24048135 | 2953 STATE HIGHWAY 3,WAITOTARA,WANGANUI | Western | WAITOTARA | 2024-12-31 | 16:55 | 2024-12-31 | 18:50 | 0.029903 | 0.00028141 | 102 | 10838 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 513 Protection flags (nil where none): B, C O/C CAUSE: Unk Location: Unk Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): Windy / Heavy Rain LFI (Y/N + Comments): Nil Follow up Required (select advisory)? Additional fault restoration comments: | .
1073 |  | JE24045559 | OTAMARAKAU | Eastern | OTAMARAKAU | 2024-12-30 | 10:00 | 2024-12-30 | 11:22 | 0.0027032 | 3.3108e-05 | 12 | 980 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | rebind in 3 x conductors , binders all broken at pole 221913 (Red defect) | .
1074 |  | JE24047933 | FEEDER FAULT -KATERE ROAD - KATERE 5 - CB5 | Western | KATERE 5 | 2024-12-30 | 9:23 | 2024-12-30 | 14:27 | 0.12006 | 0.001374 | 498 | 43516 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV, CB 5 Protection flags (nil where none): E/F CAUSE: Polymer Insulator failed Location: Pole 842744 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Yes / Cursory Weather (wind/rain): Calm / Heavy Rain LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Polymer Insulator rolled over until Jumper was sitting on crossarm and shorting out in the wet. Extra Insulator fitted & lines resagged SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1075 |  | JE24047950 | FEEDER FAULT - CLOTON RD - CLOTON NORTH - CB5 | Western | CLOTON RD NORTH | 2024-12-30 | 10:48 | 2024-12-30 | 12:10 | 0.17579 | 0.0025603 | 928 | 63716 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV, CB 5 Protection flags (nil where none): E/F CAUSE: Unknown Location: Unknown Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Yes / Cursory Weather (wind/rain): Calm / Light Rain LFI (Y/N + Comments): No LFI's indicated on SCADA. No LFI's were noticed as indicating by feild staff Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): Sectionalised & Patrolled with no fault found | .
1076 |  | JE24047966 | JE24047951 | Western | RAWHITIROA | 2024-12-30 | 13:00 | 2024-12-30 | 18:48 | 0.02291 | 0.00011864 | 43 | 8304 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 12246 Protection flags (nil where none): Unknown CAUSE: Unknown Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): Calm, light rain LFI (Y/N + Comments): N Follow up Required (select advisory)? Additional fault restoration comments: | .
1077 |  | JE24047968 | FEEDER FAULT - KIMBOLTON SUB -APITI - CB5 | Western | APITI | 2024-12-30 | 13:10 | 2024-12-30 | 17:06 | 0.12007 | 0.0014126 | 512 | 43520 | Unplanned | WILDLIFE - OTHER | REGULATORY INFORMATION Voltage & Device ID: 11kV, CB 5 Protection flags (nil where none): E/F CAUSE: Broken Staywire contacted HV Location: Tx T4/127 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: No Weather (wind/rain): Calm / Light Rain LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Stay Wire broke due to animals rubbing against it. Stay wire repaired, with some hardware replaced SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): ETA 20-30MIN | .
1078 |  | JE24047985 | 780 SOUTH ROAD,MOKOIA,HAWERA | Western | MANAWAPOU RD | 2024-12-30 | 21:39 | 2024-12-30 | 23:25 | 0.0011619 | 1.1036e-05 | 4 | 421 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Replace Transformer W1050 from lightning | .
1079 |  | JE24047992 | 18 MATAHIWI ROAD,MATAHIWI,MASTERTON | Western | MOUNT BRUCE | 2024-12-30 | 17:51 | 2024-12-30 | 23:55 | 0.093984 | 0.00084148 | 305 | 34065 | Unplanned | VEGETATION - OUTSIDE ZONE | F4119217 - ETA Required 20MIN ETA Faultman found tree had come down and broken pole 831900, line was isolated at ABS' S170, C1024/1 & Links C1024/6, to replace the pole. Faultman installed Fuses at pole 831897 and will apply for a number for the Fuses from Scada Team on 6/01/25 | .
1080 |  | JE24047993 | 1231 BALL ROAD,HURLEYVILLE,PATEA | Western | KAKARAMEA | 2024-12-30 | 18:01 | 2025-01-02 | 10:39 | 0.067393 | 9.3805e-05 | 22 | 24427 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Line down between Poles 444302 & 444401 Cause High Winds TLB cut at Pole 445923. Line down is a big gully span and will need a helicopter to restring. Generators installed on 31/12/24 at L4480 & L4490 02/01/2025 Isolated at ABS LI771 Lines repaired & TEMP Line break Closed Power restored. Generators removed from Transformers L4480 & L4490 | .
1081 |  | JE24047997 | 181 LUND ROAD,AONGATETE,KATIKATI | Eastern | KATIKATI | 2024-12-30 | 20:10 | 2024-12-30 | 22:19 | 0.019965 | 0.0001545 | 56 | 7236 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: SC1-005 No. Fuses: 2 Fuse Amp Size: 30 TIME CLOSED: 22:19 Cause: Line Clash - due to trees Weather (wind/rain): Very Windy Follow up required (select advisory)? Yes - Lots of Trees down Lund Rd need to be cut. | .
1082 |  | JE24048016 | 357 TAIKOREA ROAD,GLEN OROUA,PALMERSTON NORTH | Western | RONGOTEA | 2024-12-30 | 22:31 | 2024-12-31 | 11:20 | 0.060129 | 0.00056007 | 203 | 21794 | Unplanned | LIGHTNING - LIGHTNING STRIKE | REGULATORY INFORMATION Voltage & Device ID: REC O67 Protection flags (nil where none): EF CAUSE: Blown Transformer Location: T1/116 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): Lightning LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Transformer left of overnight. Crew will return in the morning with traffic management Isolated & Earthed at TFR T1/116 Fuses TFR Replaced, Full power restored | .
1083 |  | JE24047842 | 242D RAWHITI ROAD,TE AROHA,TE AROHA | Eastern | MOUNTAIN | 2024-12-29 | 0:22 | 2024-12-29 | 13:30 | 0.0047335 | 1.3795e-05 | 5 | 1716 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Protection flags (nil where none): CAUSE: 1st Fault, Stay strap bolt let go & Strap fell onto Jumper, 2nd Fault Failed DTX TP2679 ( Private Ownership) Location: Pole 857119 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Windy LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: 2nd Fault Private owned Transformer Failed DTX TP2679 Private Transformer TP2679 was replaced under Lynley Dunn noc on call manager she gave authorization. | .
1084 |  | JE24047846 | 73 KAIPIKARI ROAD UPPER,URENUI,URENUI | Western | MAIN RD MOTONUI | 2024-12-29 | 7:09 | 2024-12-29 | 18:19 | 0.047172 | 0.0002152 | 78 | 17098 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: 5196 No. Fuses: 2 Fuse Amp Size: 20Amp TIME CLOSED: 10:37 hrs Cause: Faulty Transformer 3946T Weather (wind/rain): Calm, Light Rain Follow up required (select advisory)? N Additional Info: Line beyond Fuses 3946T had to be sectionalised before finding faulted transformer. 15/11/3ph replaced with a 30/11/3ph | .
1085 |  | JE24047851 | 213 TOKORANGI ROAD,HALCOMBE,FEILDING | Western | KAKARIKI | 2024-12-29 | 6:15 | 2024-12-29 | 10:52 | 0.015979 | 0.0002152 | 78 | 5792 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Recloser 10300 Protection flags (nil where none): E/F CAUSE: Faulty Transformer Location: T3/33 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Yes / Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: FM replaced 3/11/15kVA Transformer with a 3/11/30kVA. Transformer was very old, but also may have been hit by last weeks lightning SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1086 |  | JE24047854 | 298 BEDFORD ROAD NORTH,KAIMIRO,INGLEWOOD | Western | MOUNTAIN RD | 2024-12-29 | 6:24 | 2024-12-29 | 7:48 | 0.003035 | 3.5867e-05 | 13 | 1100 | Unplanned | WILDLIFE - BIRD | Fuses Location: 5547 No. Fuses: 2 Fuse Amp Size: 15 Amp TIME CLOSED: 07:48 hrs Cause: Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? | .
1087 |  | JE24047865 | 12 Princess Street, Martinborough, 5711 | Western | NAPLES ST | 2024-12-29 | 9:56 | 2024-12-29 | 13:15 | 0.013081 | 0.00068422 | 248 | 4741 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV Protection flags (nil where none): NIL CAUSE: car vs pole Location: 357785 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: operational Weather (wind/rain): calm LFI (Y/N + Comments): N Follow up Required (select advisory)? N Additional fault restoration comments: Faultman found pole was not damaged just the insulator had broken off the cross arm, and cross arm is damaged, line was isolated at ABS's S584, S585 & CBC 892 to replace crossarm & hardware. | .
1088 |  | JE24047867 | 35 BATTERSEA ROAD,MORRISONS BUSH,GREYTOWN | Western | MOROA | 2024-12-29 | 9:09 | 2024-12-29 | 11:00 | 0.0012255 | 1.1036e-05 | 4 | 444 | Unplanned | WILDLIFE - BIRD | Fuses Location: T1192 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 11:00 Cause: Bird Weather (wind/rain): calm Follow up required (select advisory)? | .
1089 |  | JE24047890 | 87 ABATTOIR ROAD,TAIHAPE,TAIHAPE | Western | MOAWHANGO | 2024-12-29 | 13:24 | 2024-12-29 | 18:00 | 0.0015267 | 5.5179e-06 | 2 | 553 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: X4020 No. Fuses: 3 Fuse Amp Size: 2A, 3 x LV fuses units TIME CLOSED: 1800 Cause: Age Weather (wind/rain): Fine Follow up required (select advisory)? | .
1090 |  | JE24047906 | 1456 RANGITATAU EAST ROAD,PAPARANGI,WANGANUI | Western | WESTMERE PEAT ST | 2024-12-29 | 22:38 | 2024-12-30 | 12:21 | 0.068313 | 0.00014071 | 40 | 24760 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: REC 1026 Protection flags (nil where none): EF CAUSE: Lines Down due to fallen Tree Location: Pole 784207 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: cursory Weather (wind/rain): Calm / Heavy Rain LFI (Y/N + Comments): Indicated correctly Follow up Required (select advisory)? Additional fault restoration comments: Fault narrowed down to between Fuses 838 & Links 728. Crew have patrolled what they can but the rest is through forestry. 2r left open for crew to return at first light. Found 2x HV lines down due to a fallen tree. Lines repaired using squirrel conductor and tension sleeves | .
1091 |  | JE24047731 | unknown SH 2 ,Ngatea,Ngatea | Eastern | NGATEA | 2024-12-28 | 9:08 | 2024-12-28 | 9:52 | 0.0015871 | 3.5867e-05 | 13 | 575 | Unplanned | VEGETATION - OUTSIDE ZONE | Cause: Trees Took Lines Down What was replaced? Where was it replaced (pole/TX/pillar box)? Is 2R required? Y/N 2R Y - What is the timeframe for repairs? Additional Info: Isolated Transformer TC888 LV Fuses for Repairs Disconnect for safety to be sorted as well on related JOB Suspect HV/LV Line Clash. Transformer LV Left Isolated until inspections can be completed tomorrow under 2R tomorrow | .
1092 |  | JE24047783 | 65 WILTONS ROAD,WEST TARATAHI,CARTERTON | Western | CHESTER RD | 2024-12-28 | 9:42 | 2024-12-28 | 11:41 | 0.0003273 | 2.759e-06 | 1 | 119 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: T2312 CAUSE: Lightning Temp generation (stage details when used): N PERFORMANCE DETAIL DNO (number or state no): N Circuit patrolled & type: N/a Weather (wind/rain): lightning the day before Follow up required (select advisory)? Additional fault restoration comments: | .
1093 |  | JE24047796 | 24 HARTLEY AVENUE,CARTERTON,CARTERTON | Western | TAVERNER ST | 2024-12-28 | 10:31 | 2024-12-28 | 10:39 | 0.00060385 | 7.7251e-05 | 28 | 219 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Fuses Location: Fuse/Sw 11059/2 No. Fuses: 1 Fuse Amp Size: 25 TIME CLOSED: 10:39 Cause: unknown Weather (wind/rain): calm Follow up required (select advisory)? | .
1094 |  | JE24047841 | 79 WAIARUHE ROAD,TAIHAPE,TAIHAPE | Western | IRIRANGI | 2024-12-28 | 21:37 | 2024-12-29 | 12:50 | 0.099324 | 0.00088011 | 188 | 36000 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV Recloser 142 Protection flags (nil where none): E/F, B & C phase CAUSE: Line Down. Suspect Bird Strike Location: Pole 785527 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Yes / Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Line down repaired. Trees also cut away from lines at Pole 785424 whilst power was off. Fault found to be between ABS 1298 & Recloser 107. Line mainly cross country, patrol to continue in day light SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1095 |  | JE24047146 | 29 FISHERMANS BEND,WHIRITOA,WHANGAMATA | Eastern | WHIRITOA | 2024-12-27 | 9:17 | 2024-12-27 | 10:39 | 0.011752 | 0.00014347 | 52 | 4260 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Cause: Blue Ph Fuse Holder is Burning Up What was replaced? x1 200A Fuse, Replaced 27/12/24 New Andalec installed. Where was it replaced (pole/TX/pillar box)? Transformer TC2788 Is 2R required? Y 2R Y - What is the timeframe for repairs? Not Known Additional Info: Full Power Restored 24/12/24 - FM has replaced Blue Ph Fuse to restore Supply. Blue Ph Fuse Holder in TX is Burning up and needs replacing. FM will replace it under the 2R but he will have to take the Whole TX off to be able to do this. He did not want to do it today as it will tie him up for a long time. It is also the old Anderlect type of Fuse so he will have to get the parts. Blue ph may also be overloaded as FM tested and got 100A on Blue Ph and 20A on White Ph. FM will call back this afternoon to check and monitor the Blue Ph loading under the 2R also, Replaced 27/12/24 New Andelec -HV isolation at fuses 9389/4 see child JE24047401 | .
1096 |  | JE24047340 | 4 KING EDWARD STREET,ELTHAM,ELTHAM | Western | ELTHAM TOWN SOUTH | 2024-12-27 | 4:47 | 2024-12-27 | 7:18 | 0.17054 | 0.0014485 | 525 | 61814 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV CB R41 Protection flags (nil where none): E/F, O/C A, B & C CAUSE: unkown Location: ? Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: operational Weather (wind/rain): Very windy LFI (Y/N + Comments): N Follow up Required (select advisory)? N Additional fault restoration comments: Line patrolled and sectionalised and no fault was found | .
1097 |  | JE24047342 | 7506 SOUTH ROAD,OKATO,NEW PLYMOUTH | Western | WAREA | 2024-12-27 | 5:28 | 2024-12-27 | 9:18 | 0.013958 | 6.0697e-05 | 22 | 5059 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: PU231 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 09:18 Cause: line clash Weather (wind/rain): wind Follow up required (select advisory)?N | .
1098 |  | JE24047347 | 7 FRANCIS ROAD, WANGANUI, 4574 | Western | WESTMERE PEAT ST | 2024-12-27 | 6:07 | 2024-12-27 | 8:18 | 0.62316 | 0.0187 | 6778 | 225867 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 1 & CB 2 Protection flags (nil when none): CB 1 A,B,C ph E/F & CB 2 B ph E/f CAUSE: Tree on lines Location: pole 769185 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state no): N Circuit patrolled & type: cursory Weather (wind/rain): Very Windy Follow up required (select advisory)? Yes - Protection needs to be checked at Peat St Sub Additional fault restoration comments: Fault was on CB 5 due to tree on line, but CB 5 did not trip and both incomer's tripped SUBTRANSMISSION DETAIL LOS to sub (no or sub name): Peat St Circuit that tripped: CB 1 & CB 2 | .
1099 |  | JE24047348 | 1151 MAKURI ROAD,HUIROA,STRATFORD | Western | HUIROA | 2024-12-27 | 5:56 | 2024-12-28 | 13:30 | 0.21424 | 0.00011312 | 41 | 77651 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 12328/2, Rec 6413 Protection flags (nil where none): E/F, O/C C CAUSE: Trees through lines Location: Pole 709290 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: cursory Weather (wind/rain): Windy LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Faultman reported to dangerous to go in to cut trees or earth work area. | .
1100 |  | JE24047349 | 8A BRYCE STREET,CASTLECLIFF,WANGANUI | Western | CORNFOOT ST | 2024-12-27 | 5:56 | 2024-12-27 | 10:00 | 0.43212 | 0.0027534 | 998 | 156622 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 7 Protection flags (nil where none): E/F, O/C B CAUSE: Broken binders and damaged conductors Location: poles 376902 & 376995 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: Cursory Weather (wind/rain): Windy LFI (Y/N + Comments): N Follow up Required (select advisory)? N Additional fault restoration comments: Line was isolated at ABS 151 to repair lines and replace binders. | .
1101 |  | JE24047353 | 2192B RAWHITIROA ROAD,MATEMATEAONGA,ELTHAM | Western | RAWHITIROA | 2024-12-27 | 8:56 | 2024-12-27 | 11:55 | 0.010847 | 0.00011864 | 43 | 3932 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 6.6kV REC 12246 Protection flags (nil where none): Nil CAUSE: unknown Location: ? Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: cursory Weather (wind/rain): wind LFI (Y/N + Comments): N Follow up Required (select advisory)? N Additional fault restoration comments: REC 12246/2 found open, Lines patrolled and sectionalised no fault found | .
1102 |  | JE24047359 | 1741 PALMER ROAD,MAHOE,STRATFORD | Western | MAHOE | 2024-12-27 | 6:54 | 2024-12-27 | 11:05 | 0.00069176 | 2.759e-06 | 1 | 251 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: Fuses 8516 No. Fuses: 2x Fuse Amp Size: 6A TIME CLOSED: 11:05 Cause: Line Clash / Wind Weather (wind/rain): Windy Follow up required (select advisory)? | .
1103 |  | JE24047363 | 605 EGMONT RD,HILLSBOROUGH,NEW PLYMOUTH | Western | KATERE 5 | 2024-12-27 | 10:44 | 2024-12-27 | 12:53 | 0.0050052 | 3.8625e-05 | 14 | 1814 | Unplanned | VEGETATION - OUTSIDE ZONE | Faultman found tree through lines at pole 747243, line was isolated at Fuses 8196 to repair the lines. Cause high winds. 2 x 10 amp hv fuses replaced at Fuses 8196. | .
1104 |  | JE24047364 | 230 POHANGINA VALLEY EAST,POHANGINA,ASHHURST | Western | POHANGINA | 2024-12-27 | 7:05 | 2024-12-27 | 14:04 | 0.050615 | 0.00059594 | 134 | 18346 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC F26 Protection flags (nil when none): B & C ph O/C CAUSE: Trees through lines Location: Pole P14062 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state no): N Circuit patrolled & type: Operational Weather (wind/rain): Windy Follow up required (select advisory)? N Additional fault restoration comments: Line was isolated at ABS's F27, F28 & F33 to remove trees and repair the lines. SUBTRANSMISSION DETAIL LOS to sub (no or sub name): Circuit that tripped: DTF (KM): | .
1105 |  | JE24047374 | unknown WHARF ROAD,Colville,Rural | Eastern | COLVILLE | 2024-12-27 | 7:27 | 2024-12-27 | 9:32 | 0.00069095 | 5.5179e-06 | 2 | 250 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: dtx TC3286 No. Fuses: 2 Fuse Amp Size: 2 TIME CLOSED: 09:32 Cause: Lightning Weather (wind/rain): Follow up required (select advisory)? | .
1106 |  | JE24047378 | 4323 WAITOTARA VALLEY ROAD,NGAMATAPOURI,WANGANUI | Western | WAITOTARA | 2024-12-27 | 10:15 | 2024-12-27 | 19:35 | 0.089675 | 0.00016002 | 58 | 32503 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | check JE24047402 Faultman reported lines down by Tfr X2964, line was isolated at ABS 1372. Control of network handed over due to comms Repairs carrier out Network handed back Power restored | .
1107 |  | JE24047387 | FEEDER FAULT - RORBERTS AVE - ROBERTS 33kV | Western | PEAT ST INLAND | 2024-12-27 | 8:29 | 2024-12-27 | 10:05 | 0.56904 | 0.0067926 | 2462 | 206250 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | REGULATORY INFORMATION Voltage & Device ID: 33kV CB 3501 & 11kV CB's 1 & 2 Protection flags (nil where none): A ph O/C & E/F & T1 Diff CAUSE: Branch under insulator Location: 33kV ABS 3552 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: Operational Weather (wind/rain): Windy LFI (Y/N + Comments): N Follow up Required (select advisory)? Yes - Transformer maybe needed to be removed to clean and check insulators on 33kV ABS 3552 Additional fault restoration comments: Sub was back fed and the Controller called Paul Allen- Smith the on call Engineer and after he had done all the checks, was happy to restore transformer T1(W23) back into service SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): ROB Sub Circuit that tripped: | .
1108 |  | JE24047409 | FEEDER FAULT - CLAREVILLE - PARK RD - REC C422 | Western | PARK RD | 2024-12-27 | 9:53 | 2024-12-27 | 19:40 | 0.066533 | 0.0005987 | 217 | 24115 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11KV REC C422 Protection flags (nil where none): B phase E/F CAUSE: Pole on Ground Location: Transformer T853 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Windy LFI (Y/N + Comments): N Follow up Required (select advisory)? N Additional fault restoration comments: Took Over this job i think there maybe two jobs in this one but cnt work that out SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1109 |  | JE24047412 | 152 BLAIRLOGIE-LANGDALE ROAD,BLAIRLOGIE,MASTERTON | Western | BLAIRLOGIE | 2024-12-27 | 10:07 | 2024-12-27 | 11:28 | 0.12598 | 0.0015588 | 565 | 45661 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | REGULATORY INFORMATION Voltage & Device ID: 11kv CB C850 Protection flags (nil where none): A,B, CAUSE: Branch blown onto lines @ Pole 835310 Location: Branch blown onto lines @ Pole 835310 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Curse Weather (wind/rain): High Winds LFI (Y/N + Comments): No Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1110 |  | JE24047426 | FEEDER FAULT - DOUGLAS - HUIROA - CB D31 | Western | HUIROA | 2024-12-27 | 10:50 | 2024-12-28 | 15:08 | 0.17671 | 0.00040557 | 147 | 64050 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: CB D21 Protection flags (nil where none): B + C phase OC EF CAUSE: tree through the lines Location: Pole 759468 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: cursory Weather (wind/rain): windy LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: | .
1111 |  | JE24047565 | 748 NORFOLK ROAD,UPPER PLAIN,CARTERTON | Western | HOLDSWORTH | 2024-12-27 | 12:16 | 2024-12-27 | 14:03 | 0.00029506 | 2.759e-06 | 1 | 107 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | Fuses Location: 11129 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 14:02 Cause: Branch blown onto lines Weather (wind/rain): High winds Follow up required (select advisory)? | .
1112 |  | JE24047568 | 8763 MATAROA ROAD,TAIHAPE,TAIHAPE | Western | MOAWHANGO | 2024-12-27 | 8:36 | 2024-12-27 | 11:45 | 0.00052181 | 2.759e-06 | 1 | 189 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Fused ABS 2710 had to be isolated as transformer X3220 has no fusing on it. | .
1113 |  | JE24047582 | FEEDER FAULT - WAITARA EAST - MAIN RD MOTNUI - REC 5329 | Western | MAIN RD MOTONUI | 2024-12-27 | 13:02 | 2024-12-27 | 17:10 | 0.053306 | 0.000309 | 86 | 19321 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 5329/2 Protection flags (nil where none): A & B ph E/F CAUSE: branch touching lines Location: 763702 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): B Circuit patrolled and type: cursory Weather (wind/rain): wind LFI (Y/N + Comments): N Follow up Required (select advisory)? Yes - Faultman to defect second of line to get cut. Additional fault restoration comments: Faultman removed branch from lines. | .
1114 |  | JE24047586 | 8 KAUKATEA VALLEY ROAD,OKOIA,WANGANUI | Western | NO 3 LINE | 2024-12-27 | 13:15 | 2024-12-27 | 16:18 | 0.020739 | 0.00011312 | 41 | 7517 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: 1138 No. Fuses: 2 Fuse Amp Size: 15 TIME CLOSED: 16:18 Cause: Line clash Weather (wind/rain): windy Follow up required (select advisory)?N | .
1115 |  | JE24047591 | 78 MORIKAU ROAD,RANANA,WANGANUI | Western | RAETIHI | 2024-12-27 | 13:39 | 2024-12-27 | 19:00 | 0.013277 | 4.1384e-05 | 15 | 4812 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | check JE24047627 Fuses Location: 224 No. Fuses: 2 Fuse Amp Size: 12 TIME CLOSED: 19:00 Cause: wind line clash Weather (wind/rain): wind Follow up required (select advisory)? N | .
1116 |  | JE24047596 | FEEDER FAULT - PARKVILLE SUB - HUKANUI -CB1 | Western | HUKANUI | 2024-12-27 | 13:55 | 2024-12-27 | 21:11 | 0.088888 | 0.00060973 | 221 | 32218 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB1 Protection flags (nil where none): E/F CAUSE: Tree through lines Location: P10279 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: cursory Weather (wind/rain): wind LFI (Y/N + Comments): N Follow up Required (select advisory)? N Additional fault restoration comments: Line was isolated at ABS's S2 & S5 and Links 10850/6 to make the repairs. | .
1117 |  | JE24047604 | FEEDER FAULT MANGAMUTU SUB - MANGATAINOKA - CB 7 | Western | MANGATAINOKA | 2024-12-27 | 14:07 | 2024-12-27 | 16:43 | 0.083688 | 0.00072009 | 261 | 30333 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 7 & REC R12 Protection flags (nil where none): B & C ph E/F CAUSE: Fault 1: Private pole - Fault: 2 - Branch on line Location: F2: pole P23339 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: cursory Weather (wind/rain): windy LFI (Y/N + Comments): Y Pole 471447 Follow up Required (select advisory)? Additional fault restoration comments: Fault1: Was a private lv pole that came down Faultman cut away lv jumper at pole P40328. Fault 2: Branch on lines reported by electrician at Tui Brewery, Faultman report by time got on site branch had fallen off lines. | .
1118 |  | JE24047605 | 818 WANGANUI ROAD,TURAKINA,MARTON | Western | TURAKINA | 2024-12-27 | 14:07 | 2024-12-27 | 21:03 | 0.013773 | 3.3108e-05 | 12 | 4992 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | 1610hrs - Escalated to Downer advising that this is a waste water treatment plant, they will send someone as soon as they are free update tx to x4679 still showing as low priory Fuses Location: 1253 No. Fuses: 2 Fuse Amp Size: 15 Amp TIME CLOSED: 21:03 Cause: Weather Weather (wind/rain): Windy Follow up required (select advisory)? | .
1119 |  | JE24047610 | 42 TOKOMARU EAST ROAD,BRUNSWICK,WANGANUI | Western | BRUNSWICK | 2024-12-27 | 16:44 | 2024-12-27 | 18:53 | 0.0042659 | 3.3108e-05 | 12 | 1546 | Unplanned | VEGETATION - OUTSIDE ZONE | Branches contacting Lines at Pole 476465 Isolated at Fuses 986 Branches cut away | .
1120 |  | JE24047637 | unknown SH 25 ,Pipiroa,Rural | Eastern | HAURAKI RD | 2024-12-27 | 15:13 | 2024-12-27 | 15:54 | 0.0039044 | 9.6564e-05 | 35 | 1415 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV DTX TC2045 Protection flags (nil where none): nil CAUSE: Failed Lead out of top of D/Outs TC2045 Location: TC2045 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Windy LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Lead replaced back into D/Out SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1121 |  | JE24047656 | 120 GLUE POT ROAD, TAURANGA, 3173 | Eastern | WAIMAPU | 2024-12-27 | 15:42 | 2024-12-27 | 19:07 | 0.0039697 | 1.9313e-05 | 7 | 1439 | Unplanned | THIRD PARTY INTERFERENCE - OTHER | Fuses Location: Transformer TF4-034 (NOT T4591) No. Fuses: 2X Fuse Amp Size: 3A TIME CLOSED: 19:07 Cause: Kite in Lines Weather (wind/rain): Follow up required (select advisory)? 2R Used for Bucket Truck to retrieve kite | .
1122 |  | JE24047673 | ROBERTS AVE SUB - REC 2995 | Western | MAKIRIKIRI | 2024-12-27 | 16:06 | 2024-12-27 | 21:04 | 0.020918 | 0.0001076 | 39 | 7582 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 2995 Protection flags (nil where none): A, B, C Ph CAUSE: Tree contacting lines Location: Pole 357242 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Windy, Raining LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1123 |  | JE24047684 | unknown AWAITI ROAD,Awaiti,Rural | Eastern | TIROHIA-KARANGAHAKE | 2024-12-27 | 16:17 | 2024-12-27 | 20:11 | 0.0006435 | 2.759e-06 | 1 | 233 | Unplanned | WILDLIFE - BIRD | Fuses Location: 2360 No. Fuses: 2 Fuse Amp Size:6 TIME CLOSED: 20:10 Cause: Bird strike Weather (wind/rain):wind Follow up required (select advisory)? could not make verified job | .
1124 |  | JE24047702 | 123 BANKS ROAD,MATAMATA,MATAMATA | Eastern | FIRTH ST | 2024-12-27 | 16:48 | 2024-12-27 | 19:10 | 0.0003915 | 2.759e-06 | 1 | 142 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | Tree on Lines after Fuses FC783 Isolated and removed Tree Reliven all Good | .
1125 |  | JE24047758 | 143 OETE ROAD,PAHIATUA,PAHIATUA | Western | RUAWHATA | 2024-12-27 | 23:22 | 2024-12-28 | 13:34 | 0.0023509 | 2.759e-06 | 1 | 852 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: 7055P Wrong transformer supplied Transformer found to be faulty Fuses ORT to be replaced 28/12/24 Transformer 7055P replaced | .
1126 |  | JE24047223 | 315 WOOD STREET,WOODSIDE,GREYTOWN | Western | WEST ST | 2024-12-26 | 9:10 | 2024-12-26 | 16:18 | 0.0035444 | 8.2769e-06 | 3 | 1285 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: 3 Phase 15kVA Replaced DTX T813 CAUSE: Lightning Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: Weather (wind/rain): Follow up required (select advisory)? Additional fault restoration comments: | .
1127 |  | JE24047229 | 207A WOOD STREET,WOODSIDE,GREYTOWN | Western | WEST ST | 2024-12-26 | 8:07 | 2024-12-26 | 13:42 | 0.0055566 | 1.6554e-05 | 6 | 2014 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: T2338 CAUSE: 3 Phase 30kVA Failed Lightning Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: Weather (wind/rain): Lightning Follow up required (select advisory)? Additional fault restoration comments: | .
1128 |  | JE24047239 | 266 WOOD STREET,WOODSIDE,GREYTOWN | Western | WEST ST | 2024-12-26 | 13:01 | 2024-12-26 | 14:56 | 0.00063704 | 5.5179e-06 | 2 | 231 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: 3 Phase 15kVA Failed Lightning Strike CAUSE: Lightning Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: Weather (wind/rain): Follow up required (select advisory)? Additional fault restoration comments: | .
1129 |  | JE24047241 | 13 BROOKLYN ROAD,CARTERTON,CARTERTON | Western | TAVERNER ST | 2024-12-26 | 0:06 | 2024-12-28 | 22:52 | 0.18506 | 0.0014512 | 263 | 67077 | Unplanned | LIGHTNING - LIGHTNING STRIKE | SW/Gear 11078/2 - Fault on Internal Fuse Holder - Spoke with Adam whale - Oragnizing a generator for late morning. ***Generator on site T4351*****dressed on scada too Fuse/switch had fuses blown from a lightning strike. On further investigation the fuse holders had flashed over internally. Switchgear damaged & had to be replaced. Line breaks were cut & a generator installed. | .
1130 |  | JE24047242 | 2 ARBOR PLACE,GREYTOWN,GREYTOWN | Western | PONATAHI | 2024-12-26 | 4:04 | 2024-12-26 | 6:04 | 0.0013261 | 1.1036e-05 | 4 | 481 | Unplanned | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | Voltage & Device ID: CB 11kV C955 Protection flags (nil where none): A B C To Ground Weather (wind/rain): Rain - Lightning Follow up required (select advisory): NIL LFI Activation: Y/N 13601431 - A B C OC Reload Reliven At Transformer T857 1 x 2A Fuse - At 06:03 - Cause Lightning | .
1131 |  | JE24047247 | 314 LAKE FERRY ROAD,DYERVILLE,MARTINBOROUGH | Western | DYERVILLE | 2024-12-26 | 4:46 | 2024-12-26 | 16:34 | 0.028726 | 5.5179e-05 | 20 | 10412 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 7395 No. Fuses: 3 Fuse Amp Size: 10A TIME CLOSED: 15:15 Cause: lightning Weather (wind/rain): Follow up required (select advisory)? Fuses Location: T2759 No. Fuses: 3 Fuse Amp Size: 2A TIME CLOSED: 16:05 Cause: lightning Weather (wind/rain): Follow up required (select advisory)? Fuses Location: T1098 No. Fuses: 3 Fuse Amp Size: 3A TIME CLOSED: 16:23 Cause: lightning Weather (wind/rain): Follow up required (select advisory)? Fuses Location: T549 No. Fuses: Fuse Amp Size: 2A Plus Carrier TIME CLOSED: 16:33 Cause: lightning Weather (wind/rain): Follow up required (select advisory)? | .
1132 |  | JE24047249 | 30 COOKS ROAD,HUNTERVILLE,HUNTERVILLE | Western | HUNTERVILLE 22KV | 2024-12-26 | 6:37 | 2024-12-26 | 10:27 | 0.0063465 | 2.759e-05 | 10 | 2300 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 855 No. Fuses: 2 Fuse Amp Size: 10 Amp TIME CLOSED: 10:27 Cause: Unknown Weather (wind/rain): Raining Follow up required (select advisory)? N | .
1133 |  | JE24047261 | 357 TE MAIRE ROAD,KAHUTARA,FEATHERSTON | Western | DAIRY FACTORY | 2024-12-26 | 7:59 | 2024-12-26 | 11:01 | 0.001003 | 5.5179e-06 | 2 | 364 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 7230 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 11:00 Cause: Lightning Weather (wind/rain): Follow up required (select advisory)? | .
1134 |  | JE24047264 | 215 WOOD STREET,WOODSIDE,GREYTOWN | Western | WEST ST | 2024-12-26 | 8:50 | 2024-12-26 | 12:20 | 0.0034824 | 1.6554e-05 | 6 | 1262 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: 3 Phase 30kVA Failed Lightning CAUSE: Lightning Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: Weather (wind/rain): Lightning Follow up required (select advisory)? Additional fault restoration comments: | .
1135 |  | JE24047265 | 225 PAHAUTEA ROAD,KAHUTARA,FEATHERSTON | Western | DAIRY FACTORY | 2024-12-26 | 8:27 | 2024-12-26 | 13:39 | 0.005175 | 1.6554e-05 | 6 | 1876 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: dtx T1890 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 13:39 Cause: Lightning / Replaced Barrel Weather (wind/rain): Follow up required (select advisory)? | .
1136 |  | JE24047283 | 1162 WHITE ROCK ROAD,TUTURUMURI,MARTINBOROUGH | Western | DYERVILLE | 2024-12-26 | 10:06 | 2024-12-26 | 15:16 | 0.0017104 | 5.5179e-06 | 2 | 620 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T439 No. Fuses: 3 Fuse Amp Size:2 TIME CLOSED: 15:15 Cause: lightning Weather (wind/rain): na Follow up required (select advisory)? | .
1137 |  | JE24047285 | 372 PAHAUTEA ROAD,KAHUTARA,FEATHERSTON | Western | DAIRY FACTORY | 2024-12-26 | 5:09 | 2024-12-26 | 12:13 | 0.005848 | 1.3795e-05 | 5 | 2120 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: dtx T2737 No. Fuses: 3 Fuse Amp Size: 3 TIME CLOSED: 12:12 Cause: lightning Weather (wind/rain): Follow up required (select advisory)? | .
1138 |  | JE24047287 | 994 PONATAHI ROAD,MARTINBOROUGH,CARTERTON | Western | PONATAHI | 2024-12-26 | 10:34 | 2024-12-26 | 15:54 | 0.0017682 | 5.5179e-06 | 2 | 641 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 2199 No. Fuses: 2 Fuse Amp Size: 2 TIME CLOSED: 15:54 Cause: lighting Weather (wind/rain): Follow up required (select advisory)? | .
1139 |  | JE24047290 | 112 BROOKLYN ROAD,CARTERTON,CARTERTON | Western | TAVERNER ST | 2024-12-26 | 13:17 | 2024-12-26 | 17:58 | 0.051116 | 0.00018209 | 66 | 18527 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: 3 phase 200kVA Failed DTX T2602 Lightning CAUSE: Lightning Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: Weather (wind/rain): Follow up required (select advisory)? Additional fault restoration comments: DTX T2602 Failed | .
1140 |  | JE24047295 | 2200 SOUTH ROAD,OKATO,NEW PLYMOUTH | Western | INLAND COAST | 2024-12-26 | 11:21 | 2024-12-26 | 13:44 | 0.063677 | 0.0010043 | 364 | 23080 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Recloser 12725/2 Protection flags (nil where none): B Ph O/C CAUSE: Blown Insulator Location: Pole 844600 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Back Feed installed Via SEC 12718 up to SEC 12710 Blown Insulator found at Pole 844600 during sectionalizing Insulator replaced SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1141 |  | JE24047310 | 10 CAMBRIDGE STREET,PAHIATUA,PAHIATUA | Western | RUAWHATA | 2024-12-26 | 14:50 | 2024-12-26 | 15:55 | 0.0029939 | 7.7251e-05 | 28 | 1085 | Unplanned | WILDLIFE - BIRD | Fuses Location: Q12 No. Fuses: 2 Fuse Amp Size: 15 Amp TIME CLOSED: 15:25 Cause: Bird strike Weather (wind/rain): Raining Follow up required (select advisory)? N Fuses Location: Q13 No. Fuses: 2 Fuse Amp Size: 10 Amp TIME CLOSED: 15:54 Cause: Bird Strike Weather (wind/rain): Raining Follow up required (select advisory)? N Bird found between Poles P18109 & P18108 | .
1142 |  | JE24047322 | 936 THAMES COAST ROAD,TE MATA,THAMES | Eastern | MANAIA COROMANDEL | 2024-12-26 | 18:08 | 2024-12-26 | 20:14 | 0.00034682 | 2.759e-06 | 1 | 126 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Transformer TC 4963 No. Fuses: 2 Fuse Amp Size: 2 TIME CLOSED: 20-14 Cause: Lightening Weather (wind/rain): Rain / Lightening Follow up required (select advisory)? | .
1143 |  | JE24047327 | unknown WAIKAWAU VALLEY ROAD,Kereta,Rural | Eastern | MANAIA COROMANDEL | 2024-12-26 | 19:03 | 2024-12-26 | 20:47 | 0.00028492 | 2.759e-06 | 1 | 103 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Transformer TC4942 No. Fuses: 2 Fuse Amp Size: 2 TIME CLOSED: 20-46 Cause: Lightening Weather (wind/rain): Rain & Lightening Follow up required (select advisory)? | .
1144 |  | JE24047178 | 130 CANAL WEST ROAD,WAITAKARURU,THAMES | Eastern | MANGATARATA | 2024-12-25 | 3:58 | 2024-12-25 | 6:15 | 0.041336 | 0.00035039 | 127 | 14982 | Unplanned | WILDLIFE - POSSUM | REGULATORY INFORMATION Voltage & Device ID: 11kV RECLOSER 13066 Protection flags (nil where none): E/F CAUSE: Possum on crossarm Location: Pole 03280 Temp generation (state details when used): NIL PERFORMANCE DETAIL DNO (number or state No): NIL Circuit patrolled and type: Cursory Weather (wind/rain): Fine LFI (Y/N + Comments): NIL Follow up Required (select advisory)? NIL Additional fault restoration comments: NIL | .
1145 |  | JE24047185 | 725 FITZHERBERT EAST ROAD,AOKAUTERE,PALMERSTON NORTH | Western | AOKAUTERE | 2024-12-25 | 7:59 | 2024-12-25 | 9:10 | 0.0021587 | 3.0349e-05 | 11 | 782 | Unplanned | WILDLIFE - BIRD | Fuses Location: H47 No. Fuses: 2 Fuse Amp Size: 10 Amp TIME CLOSED: 09:10 Cause: Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? N | .
1146 |  | JE24047206 | 296 HIKUNUI ROAD,KAHUTARA,FEATHERSTON | Western | DAIRY FACTORY | 2024-12-25 | 18:48 | 2024-12-25 | 22:23 | 0.0029687 | 1.3795e-05 | 5 | 1076 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T2059 No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: Cause: 22:22 Weather (wind/rain): Rain Follow up required (select advisory)? NIL | .
1147 |  | JE24047208 | 36 MURPHYS ROAD,PAHIATUA,PAHIATUA | Western | RUAWHATA | 2024-12-25 | 20:09 | 2024-12-25 | 23:54 | 0.0031006 | 1.3795e-05 | 5 | 1124 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Faulty TFR T7/512 at Pole P15437 due to lightning strike Isolated and Earthed at TFR T7/512 Fuses TFR Replaced, full power restored | .
1148 |  | JE24047211 | 635 PAIERAU ROAD,OPAKI,MASTERTON | Western | MOUNT BRUCE | 2024-12-25 | 20:26 | 2024-12-25 | 21:56 | 0.00074498 | 8.2769e-06 | 3 | 270 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Transformer T925 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 21:56 Cause: Lightning Weather (wind/rain): Rain, Lightning Follow up required (select advisory)? NIL | .
1149 |  | JE24047213 | unknown KOHINUI ROAD,Pahiatua,Pahiatua | Western | RUAWHATA | 2024-12-25 | 20:50 | 2024-12-26 | 1:31 | 0.0015486 | 5.5179e-06 | 2 | 561 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Faulty TFR T7/511 at Pole P15424, due to lightning strike Isolated and Earthed at TFR T7/511 Fuses TFR Replaced, full power restored | .
1150 |  | JE24047215 | 65 WILTONS ROAD,TARATAHI WEST,CARTERTON | Western | CHESTER RD | 2024-12-25 | 20:47 | 2024-12-26 | 23:04 | 0.0043528 | 2.759e-06 | 1 | 1578 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Transformer T2312 No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 23:04 Cause: Lightning Weather (wind/rain): Rain Follow up required (select advisory)? | .
1151 |  | JE24047217 | 31 NEICHES LANE,CLAREVILLE,CARTERTON | Western | SOMERSET RD | 2024-12-25 | 20:59 | 2024-12-26 | 12:23 | 0.0025495 | 2.759e-06 | 1 | 924 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T2791 No. Fuses: 2 Fuse Amp Size: 2 TIME CLOSED: 12:22 Cause: lightning Weather (wind/rain): Follow up required (select advisory)? | .
1152 |  | JE24047219 | unknown SH 1 ,Utiku,Taihape | Western | MANGAWEKA | 2024-12-25 | 21:16 | 2024-12-26 | 0:10 | 0.003362 | 1.9313e-05 | 7 | 1219 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: 4015 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 00:10 Cause: unknown Weather (wind/rain): calm Follow up required (select advisory)?n Patrolled line | .
1153 |  | JE24047221 | 474 PAHAUTEA ROAD,KAHUTARA,FEATHERSTON | Western | DAIRY FACTORY | 2024-12-25 | 21:23 | 2024-12-26 | 11:43 | 0.004747 | 5.5179e-06 | 2 | 1721 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: dtx TC1817 No. Fuses: 3 Fuse Amp Size: 2A TIME CLOSED: 11:43 Cause: Lightning Weather (wind/rain): Follow up required (select advisory)? | .
1154 |  | JE24047224 | 246 WOOD STREET,WOODSIDE,GREYTOWN | Western | WEST ST | 2024-12-25 | 21:27 | 2024-12-25 | 22:25 | 0.00081296 | 1.3795e-05 | 5 | 295 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Tranformer T1586 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 22:25 Cause: Lightning Weather (wind/rain): Rain Follow up required (select advisory)? NIl | .
1155 |  | JE24047234 | 24 HARTLEY AVENUE,CARTERTON,CARTERTON | Western | TAVERNER ST | 2024-12-25 | 23:45 | 2024-12-26 | 10:41 | 0.074201 | 0.00011312 | 41 | 26895 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Transformer Fuse Blow at transformer x 1 - Isolated at switch Gear 11059/3 - Adam Whale Organizing a fuse for morning 20A Fuse Replaced Sw/Gear 11059/3 | .
1156 |  | JE24047237 | 243 TE MAIRE ROAD,KAHUTARA,FEATHERSTON | Western | DAIRY FACTORY | 2024-12-25 | 22:46 | 2024-12-26 | 10:37 | 0.0098146 | 1.3795e-05 | 5 | 3557 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 7228 No. Fuses: 4 Fuse Amp Size: 3A TIME CLOSED: 10:37 Cause: Lightning Weather (wind/rain): Follow up required (select advisory)? | .
1157 |  | JE24044086 | NGATAWA | Western | NGATAWA | 2024-12-24 | 8:01 | 2024-12-24 | 9:57 | 0.00031972 | 2.759e-06 | 1 | 116 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | CtVt Metering Calibration at Malteurop | .
1158 |  | JE24047124 | 450 WANGANUI ROAD,MARTON,MARTON | Western | TURAKINA | 2024-12-24 | 7:58 | 2024-12-24 | 10:10 | 0.0018306 | 1.3795e-05 | 5 | 664 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: 1362 No. Fuses: 2 Fuse Amp Size: 8 TIME CLOSED: 10:10 Cause: unknown Weather (wind/rain): unknown Follow up required (select advisory)?n Line patrolled | .
1159 |  | JE24047127 | 3 HAUROTO ROAD,HAWERA,HAWERA | Western | KETEMARAE RD | 2024-12-24 | 8:15 | 2024-12-24 | 8:48 | 0.00099148 | 3.0349e-05 | 11 | 359 | Unplanned | WILDLIFE - BIRD | Fuses Location: WH831 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 08:47 Cause: Bird strike/Line Clash by Pole 366462 Weather (wind/rain): calm Follow up required (select advisory)?n Line patrolled | .
1160 |  | JE24047133 | 53 EGMONT ROAD,WAIWHAKAIHO,NEW PLYMOUTH | Western | KATERE 8 | 2024-12-24 | 9:29 | 2024-12-24 | 10:13 | 0.21236 | 0.0048447 | 1756 | 76972 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | ETA 30 mins Call by Police and Fire, live lines on the car. Person still trapped. Control to isolate power. Feeder dropped. Escalated to the SMC. No Network Damage, car V house, Safety Disconnect 36 Riverdale Drive, Tag A42111 Retailer Notified of Safety Disconnection | .
1161 |  | JE24047152 | 656 HIMATANGI BLOCK ROAD, HIMATANGI, FOXTON | Western | BAINESSE | 2024-12-24 | 15:05 | 2024-12-24 | 17:36 | 0.010827 | 7.1733e-05 | 26 | 3924 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Broken cross arm found at Pole P34918, due to old age Isolated at Fuses B20 Cross arm and hardware replaced, fill power restored | .
1162 |  | JE24043465 | ARAMOHO INLAND | Western | ARAMOHO INLAND | 2024-12-23 | 13:01 | 2024-12-23 | 15:07 | 0.00034671 | 2.759e-06 | 1 | 126 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | CT & VT Calibration by Accucal of 11kV metering unit. | .
1163 |  | JE24047046 | 25 MAHUTA ROAD NORTH,WAITAKARURU,THAMES | Eastern | MANGATARATA | 2024-12-23 | 5:14 | 2024-12-23 | 6:37 | 0.0075321 | 9.1046e-05 | 33 | 2730 | Unplanned | WILDLIFE - BIRD | Fuses Location: FP1167 No. Fuses: 2 Fuse Amp Size: 5A TIME CLOSED: 06:36 Cause: Ducks - Wildlife Weather (wind/rain): Rain Wind Lightning Follow up required (select advisory)? NIL | .
1164 |  | JE24047048 | 6 BROWN STREET,INGLEWOOD,INGLEWOOD | Western | RATA ST | 2024-12-23 | 10:21 | 2025-01-10 | 16:58 | 0.0010204 | 5.5179e-06 | 1 | 370 | Unplanned | THIRD PARTY INTERFERENCE - VANDALISM/THEFT | Fuse/Sw 12016/4 has tripped due to copper theft attempt of HV cable Isolated & Earth at Fuse/Sw 12016/4 Private HV cable, LV Cables disconnected from LV Bushings, Generator Connected 10/01/25 -- NAPA E00172 Cable repaired by Downer, Generator removed, full power restored to customer | .
1165 |  | JE24047059 | 202 KAIKAHU ROAD,KEREPEHI,PAEROA | Eastern | AWAITI | 2024-12-23 | 9:13 | 2024-12-23 | 10:31 | 0.00086127 | 1.1036e-05 | 4 | 312 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Fuses FC1540 / Transformer TC2906 No. Fuses: Fuses FC1540 - 2x / Transformer TC2906 - 2x Fuse Amp Size: Fuses FC1540 - 3A / Transformer TC2906 - 3A TIME CLOSED: 10:30 Cause: Lightning Weather (wind/rain): Stormy Follow up required (select advisory)? Note: 2x Fuses Popped on both the Transformer & the Spur line Fuses - Power Restored to both at 10:30 | .
1166 |  | JE24047103 | 400 THAMES COAST ROAD,TE PURU,THAMES | Eastern | THAMES COAST | 2024-12-23 | 16:58 | 2024-12-23 | 18:10 | 0.069541 | 0.0009546 | 346 | 25206 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Sectionliser 13409 Protection flags (nil where none): A B - OC CAUSE: Unknown No Fault Found Location: SEC 13409 Temp generation (state details when used): NIL PERFORMANCE DETAIL DNO (number or state No): NIL Circuit patrolled and type: Cursory Patrol Weather (wind/rain): Fine LFI (Y/N + Comments): 13832503 - A B Follow up Required (select advisory)? NIL Additional fault restoration comments: Patrolled past ABS 1354 nothing found SEC 13409 Successfully closed | .
1167 |  | JE24042771 | YOUNG RD | Eastern | YOUNG RD | 2024-12-22 | 23:50 | 2024-12-23 | 3:02 | 0.042037 | 0.00052144 | 189 | 15236 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Paengaroa Upgrade Project - Final Stage Liven PGA2 & PGA3 to poles 393933 & 319641 to carry out live phasing at line breaks . Re-connect 11kV cable breaks at Poles 393933 and 319641 | .
1168 |  | JE24046972 | 3 HAUROTO ROAD,HAWERA,HAWERA | Western | KETEMARAE RD | 2024-12-22 | 3:33 | 2024-12-22 | 4:34 | 0.0018543 | 3.0349e-05 | 11 | 672 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: WH831 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 0434 Cause: Unknown, suspect bird strike Weather (wind/rain): Calm Follow up required (select advisory)? | .
1169 |  | JE24046981 | switch_9405:1 | Eastern | BOWENTOWN | 2024-12-22 | 9:04 | 2024-12-22 | 13:26 | 0.0014434 | 5.5179e-06 | 2 | 523 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Site Inspection - Tech Required - AC MAINS FAILURE SEC 9405 & SEC 9870 Please Investigate Center Phase DDO Out - At Transformer TP1348 Replaced Blown Transformer - Fixed Triup going to SEC 9405 | .
1170 |  | JE24046994 | unknown RUATITI ROAD,Raetihi,Raetihi | Western | RAETIHI | 2024-12-22 | 8:48 | 2024-12-22 | 10:40 | 0.00061978 | 5.5179e-06 | 2 | 225 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Y78 No. Fuses: 2 Fuse Amp Size: 2 Amp TIME CLOSED: 10:40 hrs Cause: Lightning Weather (wind/rain): Heavy Rain / Lightning Follow up required (select advisory)? | .
1171 |  | JE24046996 | 4607 STATE HIGHWAY 1,TOKOROA,TOKOROA | Eastern | OLD CAMBRIDGE RD | 2024-12-22 | 8:51 | 2024-12-22 | 17:26 | 0.011365 | 2.2072e-05 | 8 | 4119 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Lines Down At Pole 858154 - Creek Crossing Before Aerodrome - Isolated at Fuses FC905 at 08:50 Crossarm Replace Conductor re Strung and tensioned Full Power Restored at 17:25 | .
1172 |  | JE24046999 | 3307 TAIRUA WHITIANGA ROAD,WHITIANGA,WHITIANGA | Eastern | COROGLEN | 2024-12-22 | 9:24 | 2024-12-22 | 13:20 | 0.0084525 | 3.5867e-05 | 13 | 3064 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Transformer TC1108 - Blown Replaced Transformer - Fuses Closed at 13:19 Cause - Lighting | .
1173 |  | JE24047024 | 18 WAIINU BEACH ROAD,WAITOTARA,WANGANUI | Western | WAITOTARA | 2024-12-22 | 19:24 | 2024-12-22 | 21:25 | 0.0036782 | 3.0349e-05 | 11 | 1333 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Found 2 fuses blown at Fuses 2716. Isolated Fuses to replace insulators at Pole 362562. | .
1174 |  | JE24046443 | APITI | Western | APITI | 2024-12-21 | 10:01 | 2024-12-21 | 11:06 | 0.0014339 | 2.2072e-05 | 8 | 520 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Rebind Hv at Pole P12006 red defect | .
1175 |  | JE24046886 | 53 WHAKAMARA ROAD,MOKOIA,HAWERA | Western | WHAKAMARA | 2024-12-21 | 1:44 | 2024-12-21 | 3:58 | 0.042525 | 0.00075044 | 179 | 15414 | Unplanned | WILDLIFE - POSSUM | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 2 Protection flags (nil where none): A & B ph E/F CAUSE: Possum Location: Pole Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: cursory Weather (wind/rain): calm LFI (Y/N + Comments): N Follow up Required (select advisory)? N Additional fault restoration comments: Possum removed with hot line stick. | .
1176 |  | JE24046894 | 98 HIGHDEN ROAD,RONGOTEA,PALMERSTON NORTH | Western | KOPANE | 2024-12-21 | 7:32 | 2024-12-21 | 10:01 | 0.0020577 | 1.3795e-05 | 5 | 746 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: T1/515 No. Fuses: 2 Fuse Amp Size: 6 Amp TIME CLOSED: 10:00 Cause: Unknown Weather (wind/rain): Calm / Heavy Rain Follow up required (select advisory)? Additional Info: Also replaced 1x 100A LV fuse link at Tx T1/515 | .
1177 |  | JE24046901 | 6 INLAND NORTH ROAD,TIKORANGI,WAITARA | Western | TIKORANGI | 2024-12-21 | 10:08 | 2024-12-21 | 13:57 | 0.039439 | 0.00040833 | 148 | 14295 | Unplanned | WILDLIFE - POSSUM | REGULATORY INFORMATION Voltage & Device ID: 11kV, Sec 12581/2 Protection flags (nil where none): E/F, B phase CAUSE: Opossum Location: 763634 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): no Circuit patrolled and type: cursory Weather (wind/rain): Calm / Light Rain LFI (Y/N + Comments): Yes, Indicated correctly at Poles 762619 & 840556 Follow up Required (select advisory)? Additional fault restoration comments: Opossum caused jumper to touch and burn through one crossarm of double termination arm. Temp repairs made to restore power. 2R left open until follow up decision made.. Downer consider pole structure to be in poor condition and will go to NOC performance team to decide the next course of action. Note no possum guard was installed on pole. 22/12/24 NCTL Job closed out, If pole 2 be replaced new Red Defect will be raised | .
1178 |  | JE24046903 | 400 WHANGAEHU VALLEY ROAD,WHANGAEHU VALLEY,MASTERTON | Western | BIDEFORD | 2024-12-21 | 10:49 | 2024-12-21 | 11:50 | 0.00033749 | 5.5179e-06 | 2 | 122 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: T1017 No. Fuses: 2 Fuse Amp Size: 3 Amp TIME CLOSED: 11:50 Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)? N | .
1179 |  | JE24046904 | 527 RAPANUI ROAD,WESTMERE,WANGANUI | Western | WESTMERE PEAT ST | 2024-12-21 | 11:24 | 2024-12-21 | 12:16 | 0.00057132 | 1.1036e-05 | 4 | 207 | Unplanned | WILDLIFE - BIRD | Fuses Location: 1452 No. Fuses: 2 Fuse Amp Size: 6 Amp TIME CLOSED: 12:15 hrs Cause: Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? | .
1180 |  | JE24046910 | 87 DUKESON ROAD,LICHFIELD,PUTARURU | Eastern | LICHFIELD | 2024-12-21 | 13:14 | 2024-12-22 | 14:21 | 0.020789 | 1.3795e-05 | 5 | 7535 | Unplanned | VEGETATION - OUTSIDE ZONE | Tree through Lines, Isolated at Fuses FP1851 (Blown on Arrival) 1 x Pole broken, 4 x broken Cross arms Waiting for line crew to arrive on site Lines Poles and Crossarms Repaired - Installations tested no sign of line clash between 11kV and 400V 85 Dukeson was left Disconnect due to high loop impedance test Tag Number A38282 - Owner Notified Fuses FP1851 Close at 14:20 | .
1181 |  | JE24046918 | unknown OHURA ROAD,Strathmore,Rural | Western | STRATHMORE | 2024-12-21 | 14:47 | 2024-12-21 | 17:30 | 0.0027035 | 1.6554e-05 | 6 | 980 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: 5669 No. Fuses: 2 Fuse Amp Size: 6 Amp TIME CLOSED: 17:30 hrs Cause: Wind & line needs resagging Weather (wind/rain): Light Rain / Windy Follow up required (select advisory)? | .
1182 |  | JE24046919 | 800 STATE HIGHWAY 1,BULLS,MARTON | Western | CROFTON | 2024-12-21 | 14:55 | 2024-12-21 | 16:35 | 0.00027539 | 2.759e-06 | 1 | 100 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: 4238 No. Fuses: 2 Fuse Amp Size: 10 Amp TIME CLOSED: 16:35 hrs Cause: Wind Weather (wind/rain): Windy Follow up required (select advisory)? | .
1183 |  | JE24046920 | 23 FLYGERS LINE,MILSON,PALMERSTON NORTH | Western | TE ARAKURA | 2024-12-21 | 15:20 | 2024-12-21 | 16:00 | 0.055356 | 0.0020747 | 752 | 20064 | Unplanned | LIGHTNING - LIGHTNING STRIKE | REGULATORY INFORMATION Voltage & Device ID: 11kV, CB 9 Protection flags (nil where none): E/F, B phase CAUSE: Lightning Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): Lightning LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): Cursory patrolled, no fault found | .
1184 |  | JE24046921 | 91 OLD WEST ROAD,LINTON,unknown | Western | AOKAUTERE | 2024-12-21 | 15:19 | 2024-12-21 | 17:47 | 0.1993 | 0.0025769 | 934 | 72236 | Unplanned | LIGHTNING - LIGHTNING STRIKE | REGULATORY INFORMATION Voltage & Device ID: 11kV, CB 4 Protection flags (nil where none): O/C A-B-C phase CAUSE: Lightning Location: 482041 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): Heavy Rain / Lightning LFI (Y/N + Comments): None Follow up Required (select advisory)? Additional fault restoration comments: Lightning struck tree branch which fell onto line. Tree cleared from line and 1x HV Insulator replaced. NDR to follow | .
1185 |  | JE24046928 | 638 MILSON LINE, NEWBURY, PALMERSTON NORTH, 4478 | Western | TE ARAKURA | 2024-12-21 | 16:10 | 2024-12-21 | 19:11 | 0.0044886 | 2.4831e-05 | 9 | 1627 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Replace Tfr T2/182 due to lightning | .
1186 |  | JE24046930 | 641 MILSON LINE,NEWBURY,PALMERSTON NORTH | Western | TE ARAKURA | 2024-12-21 | 20:29 | 2024-12-21 | 22:26 | 0.00096619 | 8.2769e-06 | 3 | 350 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Replace Tfr T2/678 due to lightning | .
1187 |  | JE24046951 | 71 AOTEA CRESCENT,TOKOROA,TOKOROA | Eastern | OLD CAMBRIDGE RD | 2024-12-21 | 19:24 | 2024-12-21 | 22:28 | 0.09259 | 0.00097943 | 355 | 33560 | Unplanned | LIGHTNING - LIGHTNING STRIKE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 3 Protection flags (nil where none): A,B,C, E/F O/C CAUSE: Lightning Strike @ Pole 26250 , Blew Lead off Cable ( Requires Testing before reconnecting ) Location: Pole 26250 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): 2412029 Circuit patrolled and type: curse Weather (wind/rain): lightning LFI (Y/N + Comments): Yes A12633 Follow up Required (select advisory)? Additional fault restoration comments: Cable Cut away requires Testing. DNO Created | .
1188 |  | JE24046963 | 230 POHANGINA VALLEY EAST,POHANGINA,ASHHURST | Western | POHANGINA | 2024-12-21 | 22:27 | 2024-12-22 | 0:36 | 0.030516 | 0.0003697 | 134 | 11061 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: REC F26 Protection flags (nil where none): B & C phase OC CAUSE: Unknown Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): Windy, rain LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Line sectionalised , no fault found | .
1189 |  | JE24046966 | 1593 OTARAOA ROAD,TARATA,WAITARA | Western | OTARAOA RD | 2024-12-21 | 23:08 | 2024-12-22 | 11:36 | 0.018446 | 0.00010484 | 38 | 6686 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Original job closed out need a new one to replace Transformer 3935T - 2307hrs fuses ORT - tx needs to be replaced Cause: Transformer 3935T replaced due to lightning strike. 30/11/3ph Isolation: ABS's 5130 & 12037 Backfed via Gas/Sw 12707/2 | .
1190 |  | JE24043432 | MANGATARATA | Eastern | MANGATARATA | 2024-12-20 | 9:05 | 2024-12-20 | 10:55 | 0.0042623 | 3.8625e-05 | 14 | 1545 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV rotten red defect crossarms at pole O13950 | .
1191 |  | JE24043702 | 299 WANI ROAD, NETHERTON, PAEROA, 3671 | Eastern | AWAITI | 2024-12-20 | 8:49 | 2024-12-20 | 10:17 | 0.0085346 | 9.6564e-05 | 35 | 3093 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace hv crossarm at pole O13387 as red defect | .
1192 |  | JE24045934 | MANGATARATA | Eastern | MANGATARATA | 2024-12-20 | 11:48 | 2024-12-20 | 12:57 | 0.0030378 | 4.4143e-05 | 16 | 1101 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV rotten red defect crossarms at poles O2574 | .
1193 |  | JE24045982 | PUHUNGA ISLAND RD | Eastern | PUHUNGA ISLAND RD | 2024-12-20 | 12:19 | 2024-12-20 | 13:13 | 0.0001505 | 2.759e-06 | 1 | 55 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV rotten red defect crossarms at pole 877449 | .
1194 |  | JE24046742 | 46 COLEMAN AVENUE, WAVERLEY, 4591 | Western | WAVERLEY | 2024-12-20 | 1:44 | 2024-12-20 | 3:03 | 0.014711 | 0.00022623 | 82 | 5332 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faultman found cracked DDO's on transformer 4949W due to deterioration, line was isolated at ABS 4489 & Fuses 1257 to replace the full set of DDO's. | .
1195 |  | JE24046745 | 32 CAMBRIA STREET,HAWERA,HAWERA | Western | TAWHITI RD | 2024-12-20 | 1:07 | 2024-12-20 | 11:20 | 0.14308 | 0.0018485 | 578 | 51860 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 5 Protection flags (nil where none): A & B ph O/C CAUSE: Blown cable termination (suspect due to opossum) Location: Pole 856591 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: cursory Weather (wind/rain): wind LFI (Y/N + Comments): N Follow up Required (select advisory)? N Additional fault restoration comments: At first no fault was found suspected opossum was cause, then CB 5 was closed, and back feed removed, and supply went off, back feed was put back in place and then operational patrol was done and the blown cable terminations were found. Line was isolated at ABS 6814, Links 6811 & Sw/Gear 6820/1. Cable crew to return in morning to repair or replace cable termination 20/12/24 Crew put in temp links at pole 846577 and a temp Cable break at Pole 856591 will return in New Year to replace section of Cable all Power restored at 11-25 DNO2412019 | .
1196 |  | JE24046864 | 3169 WHITE ROCK ROAD,WHITE ROCK,MARTINBOROUGH | Western | TUTURUMURI | 2024-12-20 | 10:58 | 2024-12-21 | 14:41 | 0.10475 | 0.0001545 | 29 | 37969 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: REC C633 Protection flags (nil where none): B & C Phase fault CAUSE: Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Windy LFI (Y/N + Comments): Nil Follow up Required (select advisory)? Additional fault restoration comments: Recloser has no comms so actual outage time is unknown. 21/12/2024 Informed at Hand Over fault past ABS S1202 Line Break in Place at Pole 811651 FM to return in day light Branch found on lines at Pole 81640, cleared using hand saw and hot sticks Line proved as fault clear, Isolated again to close line break Power restored FM went to no power - found feeder fault investigations underway | .
1197 |  | JE24046873 | sub_BHM - CB1 | Eastern | WAIPUNA | 2024-12-20 | 17:14 | 2024-12-20 | 23:27 | 0.02968 | 0.0016554 | 552 | 10758 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 1 Protection flags (nil where none): E/F CAUSE: Tree Through Lines @ Pole 200619, Namu Conductor Location: Pole 200619 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Wind LFI (Y/N + Comments): Old LFI Operated at 13129/3 site, Bum Steer! Follow up Required (select advisory)? No Additional fault restoration comments: | .
1198 |  | JE24046875 | 282A NGARUA ROAD,WAITOA,WAITOA | Eastern | TOWNSHIP & LS | 2024-12-20 | 19:01 | 2024-12-21 | 0:05 | 0.0041936 | 1.3795e-05 | 5 | 1520 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: DTX TC1817 3 Phase 30kVA Failed , 1 Cow Shed & 3 Houses , 3 Phase 50KVA Installed CAUSE: Internal Transformer Fault Voltages hay wire 480V Between Phases Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Cursory Weather (wind/rain): Wind Follow up required (select advisory)? Yes Possibly overloaded? Additional fault restoration comments: upgraded to 50KVA | .
1199 |  | JE24046883 | 107 HUNT ROAD,WHANGAMATA,WHANGAMATA | Eastern | HETHERINGTON RD | 2024-12-20 | 21:28 | 2024-12-21 | 20:42 | 0.031745 | 0.00030349 | 55 | 11506 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 20/12/2024 Possible Cable Fault or Faulty Transformer , FAULTY SAFELINK Fuse Failed Again. Broken open & Thermal Element had blown!! Generator installed 21/12/24 00:39, Work to Continue in morning, Replaced Fuse & Removed Gen Set 21/12/24 20:25 25amp fuses replaced | .
1200 |  | JE24043388 | 54 MANGOREI ROAD, STRANDON, NEW PLYMOUTH, 4312 | Western | BROOKLANDS 10 | 2024-12-19 | 9:36 | 2024-12-19 | 11:53 | 0.00037738 | 2.759e-06 | 1 | 137 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Tx 244, replace severely rusted lid. | .
1201 |  | JE24043393 | 54 TURU ROAD, OAONUI, OPUNAKE, 4681 | Western | SOUTH RD NGARIKI | 2024-12-19 | 8:51 | 2024-12-19 | 15:33 | 0.012201 | 3.0349e-05 | 11 | 4422 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace poles 713082, 713083, 713084, 713085, 713086, 713087, 713088, 713091, 713092, 713093, 713094, 713095, 713096 & 713097 | .
1202 |  | JE24043412 | 914 NAPIER ROAD, WHAKARONGO, PALMERSTON NORTH, 4470 | Western | ASHHURST | 2024-12-19 | 9:16 | 2024-12-19 | 14:48 | 0.054089 | 0.00016278 | 59 | 19605 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace pole P01325 to new 12.5 pole due the road crossing getting hit multiple times. | .
1203 |  | JE24043420 | 1329 TINUI VALLEY ROAD, TINUI VALLEY, TINUI, 5894 | Western | CASTLEPOINT | 2024-12-19 | 8:46 | 2024-12-19 | 15:01 | 0.10864 | 0.00028969 | 105 | 39379 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles and hardware past S86 | .
1204 |  | JE24043436 | LINDERMANN RD | Eastern | LINDERMANN RD | 2024-12-19 | 8:54 | 2024-12-19 | 15:07 | 0.067881 | 0.00018209 | 66 | 24604 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv/400vt cross arms @ poles 204582, 204583, 204584, 204585, 204587, 204589. Replace 11kv/400vt pole 204588. Isolation point @ SB1-002 . Fuse SB1-034 to be replaced with Fused ABS SB1-034. | .
1205 |  | JE24043438 | 3556 1, LICHFIELD, TOKOROA, 3491 | Eastern | HARRIS BLOCK | 2024-12-19 | 9:46 | 2024-12-19 | 11:11 | 0.0014137 | 1.6554e-05 | 6 | 512 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace leaking 30kVA transformer TC601 | .
1206 |  | JE24043449 | 117 ASHHURST ROAD, BUNNYTHORPE, PALMERSTON NORTH, 4481 | Western | STONEY CREEK | 2024-12-19 | 8:31 | 2024-12-19 | 13:28 | 0.031148 | 0.00010484 | 38 | 11290 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace crossarms and poles between P40044 and P40851. | .
1207 |  | JE24043591 | 1033 TARATA ROAD, KAIMATA, INGLEWOOD, 4387 | Western | KOHETE RD | 2024-12-19 | 9:01 | 2024-12-19 | 16:09 | 0.036622 | 8.5528e-05 | 31 | 13274 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace 30kVA duel Tx at poles 760074 and 760083. replace arms between poles 760046 and 760083. | .
1208 |  | JE24043618 | 5137 4, KAKATAHI, WANGANUI, 4573 | Western | IRIRANGI | 2024-12-19 | 9:16 | 2024-12-19 | 15:54 | 0.029926 | 0.00015174 | 55 | 10847 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace multiple poles & x-arms between poles 783762 & 783684 | .
1209 |  | JE24044507 | 203 BOWLER ROAD, OTWAY, TE AROHA, 3392 | Eastern | SPRINGDALE | 2024-12-19 | 9:30 | 2024-12-19 | 14:27 | 0.031052 | 0.00010484 | 38 | 11255 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | PQI -Upgrade and relocate HV transformer fuses and P/M TX TC2239 to 11/100/3 to replacement Pole C1031. | .
1210 |  | JE24044995 | WHAKAMARAMA | Eastern | WHAKAMARAMA | 2024-12-19 | 8:31 | 2024-12-19 | 15:38 | 0.11378 | 0.0003228 | 117 | 41240 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace 33kV pole 205559 with a new 15.5m concrete busck, replace HV arm on Pole 209833, 209842, 209877 and 209878 | .
1211 |  | JE24045602 | 111 LINDEMANN ROAD, TAHAWAI, 3170 | Eastern | LINDERMANN RD | 2024-12-19 | 16:08 | 2024-12-19 | 16:12 | 7.0629e-05 | 1.6554e-05 | 6 | 26 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: Transformer not on Neutral Tap "2" it was on "3"Lowered Voltage Now 242V Loop tests completed: Test results: Voltage at TX: 242V Voltage at house: 242V Have all connections been checked? Yes PQI Ref #: Additional Info: Lowered to Neutral Tap, Voltage now 242V | .
1212 |  | JE24046381 | ALEXANDRA AVE | Eastern | ALEXANDRA AVE | 2024-12-19 | 19:57 | 2024-12-19 | 20:37 | 0.010746 | 0.00027314 | 99 | 3895 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Switch gear 9596 for CFCF | .
1213 |  | JE24046502 | 607 CAMERON ROAD, TAURANGA SOUTH, TAURANGA, 3112 | Eastern | 10TH AVE | 2024-12-19 | 6:00 | 2024-12-19 | 8:21 | 0.0011658 | 8.2769e-06 | 3 | 423 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To liven cable between SK5-034 and SK5-153 | .
1214 |  | JE24046551 | 985 MANAIA ROAD,KAPUNI,HAWERA | Western | AUROA | 2024-12-19 | 5:52 | 2024-12-19 | 7:20 | 0.0002407 | 2.759e-06 | 1 | 87 | Unplanned | WILDLIFE - BIRD | Awaiting AI Team Fuses Location: 8900 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 0719 Cause: unknown bird Weather (wind/rain): wind little rain Follow up required (select advisory)? sent email to AI team to add customer to K1053 so verified job can be made | .
1215 |  | JE24046554 | 1 TIROHANGA ROAD,MATAKANA ISLAND,TAURANGA | Eastern | MATAKANA RD | 2024-12-19 | 6:04 | 2024-12-19 | 10:15 | 0.0132 | 5.242e-05 | 19 | 4784 | Unplanned | WILDLIFE - BIRD | Fuses Location: SB3-004 No. Fuses: 2 Fuse Amp Size: 15 TIME CLOSED: 10:15 Cause: Bird Strike Weather (wind/rain): Calm 10km Breeze N.W Follow up required (select advisory)? | .
1216 |  | JE24046555 | 1198 JUNCTION ROAD,EGMONT VILLAGE,INGLEWOOD | Western | JUNCTION RD | 2024-12-19 | 6:20 | 2024-12-19 | 7:48 | 0.0024472 | 2.759e-05 | 10 | 887 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: 6571 No. Fuses: 2 Fuse Amp Size: 15amp TIME CLOSED: 07:48 Cause: Wind Weather (wind/rain): wind Follow up required (select advisory)? | .
1217 |  | JE24046559 | 47 KOPIKOPIKO ROAD,PAHIATUA,PAHIATUA | Western | MANGAMAIRE | 2024-12-19 | 7:07 | 2024-12-19 | 9:07 | 0.010562 | 8.8287e-05 | 32 | 3828 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Floating conductor at Pole P45613 Replace cross arm, and insulators. | .
1218 |  | JE24046633 | 243 DOUGHERTY ROAD, EKETAHUNA, 4995 | Western | MANGAMAIRE | 2024-12-19 | 12:45 | 2024-12-19 | 13:22 | 0.0031389 | 8.5528e-05 | 31 | 1138 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Replace broken insulators and cross arm at Pole P11138 | .
1219 |  | JE24046655 | unknown KAHUTARA ROAD,Kahutara,Rural | Western | DAIRY FACTORY | 2024-12-19 | 13:14 | 2024-12-19 | 14:52 | 0.0002726 | 2.759e-06 | 1 | 99 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T1885 No. Fuses: 2 Fuse Amp Size: 3a TIME CLOSED: 1452 Cause: lightening Weather (wind/rain): windy Follow up required (select advisory)? Restored | .
1220 |  | JE24046739 | sub_OMO | Eastern | WHAKAMARAMA | 2024-12-19 | 21:43 | 2024-12-20 | 11:45 | 0.4846 | 0.0017713 | 322 | 175647 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: Recloser 9560 Protection flags (nil where none): Phase B-OC CAUSE: Car Versus Pole Location: Pole 210112 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Replaced pole 210112 and Transformer TD2-024 Recloser 9560 lost comms during the shut so had to be closed on site Number of part Power jobs called in Blown Jumper found at Pole 263959 Isolated at ABS SD2-007 & Links 13134/6. With Back feed installed Via Gas/Sw IP717 Transformer TD2-024 Isolated for LV repairs to Allow HV to be Restored Power Restored 11:45 | .
1221 |  | JE24043171 | 143 WATERSHED ROAD, BUNNYTHORPE, PALMERSTON NORTH, 4470 | Western | POHANGINA | 2024-12-18 | 8:31 | 2024-12-18 | 13:33 | 0.089261 | 0.00029521 | 107 | 32353 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace cross-arms, stays and earths between P17086 and P17066 | .
1222 |  | JE24043204 | 81 CLIFTON GROVE ROAD, ADMIRAL HILL, MASTERTON, 5883 | Western | LONGBUSH | 2024-12-18 | 9:00 | 2024-12-18 | 14:14 | 0.042389 | 0.00013519 | 49 | 15364 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles and hardware past S333 | .
1223 |  | JE24043241 | 120 LOVEGROVE ROAD, TE AROHA, TE AROHA, 3393 | Eastern | LOVEGROVE RD | 2024-12-18 | 8:30 | 2024-12-18 | 13:54 | 0.048171 | 0.00014898 | 54 | 17460 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re-conductor HV (Iodine) conductor from Pole C13154 to Pole C13160 | .
1224 |  | JE24043258 | 27 MARAETAI ROAD, TOKOROA, TOKOROA, 3420 | Eastern | DALMENY ST | 2024-12-18 | 9:21 | 2024-12-18 | 13:08 | 0.045625 | 0.0002014 | 73 | 16537 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Upgrade 11kV Cable Between IC3028 & 9652/3 | .
1225 |  | JE24043293 | 859 HALCOMBE ROAD, HALCOMBE, FEILDING, 4775 | Western | MT STEWART | 2024-12-18 | 10:30 | 2024-12-18 | 12:18 | 0.0065421 | 6.0697e-05 | 22 | 2371 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Collect oil sample from regulator 10112 | .
1226 |  | JE24043298 | 1310 WAIHI VALLEY ROAD, PONGAROA, PONGAROA, 4990 | Western | HOROEKA | 2024-12-18 | 9:46 | 2024-12-18 | 15:16 | 0.061927 | 0.00018761 | 68 | 22446 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace 11kv pole P06283 | .
1227 |  | JE24043318 | 94 GREY STREET, TAURANGA, TAURANGA, 3110 | Eastern | SPRING ST | 2024-12-18 | 21:00 | 2024-12-18 | 23:42 | 0.0097874 | 6.0697e-05 | 22 | 3548 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To repair leak and top up oil on TL4-013 | .
1228 |  | JE24043531 | 54 VILES ROAD, WESTERN LAKE, FEATHERSTON, 5773 | Western | REVANS ST | 2024-12-18 | 9:31 | 2024-12-18 | 13:18 | 0.0075314 | 3.3108e-05 | 12 | 2730 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Change 11kv arms from 7261 to end of line , install HV fuses (11500) @ 798574 | .
1229 |  | JE24044698 | 2805 MOUNTAIN ROAD, MIDHIRST, STRATFORD, 4394 | Western | CLOTON RD NORTH | 2024-12-18 | 9:16 | 2024-12-18 | 15:45 | 0.13128 | 0.0005849 | 159 | 47582 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace ABS 5536 and pole for new double 11m rectify defects pole 761183 and 761181 croydon road replace Hv xarms along Rutland Road | .
1230 |  | JE24045950 | 47 CHERRYWOOD DRIVE, OTUMOETAI, TAURANGA, 3110 | Eastern | CHERRYWOOD DRIVE | 2024-12-18 | 22:34 | 2024-12-18 | 23:04 | 0.0013039 | 4.4143e-05 | 16 | 473 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Connect new cable to SD4-609. Connect new cable to TX TC4-330. Change over temp generator at TC4-330. | .
1231 |  | JE24045990 | 123 PROSPECT ROAD, WHANGAMOMONA, STRATFORD, 4396 | Western | STRATHMORE | 2024-12-18 | 9:17 | 2024-12-18 | 15:23 | 0.0030258 | 8.2769e-06 | 3 | 1097 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace hv pin arm at pole 708766 & 708768 | .
1232 |  | JE24045992 | 59 WHANGAMOMONA ROAD, WHANGAMOMONA, STRATFORD, 4396 | Western | STRATHMORE | 2024-12-18 | 9:16 | 2024-12-18 | 15:23 | 0.014156 | 3.8625e-05 | 14 | 5131 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace lv arms at pole 708819. replace hv arms at pole 708820 | .
1233 |  | JE24046007 | 319 MANGARE ROAD, WHANGAMOMONA, STRATFORD, 4396 | Western | STRATHMORE | 2024-12-18 | 9:15 | 2024-12-18 | 17:21 | 0.22821 | 0.00059042 | 214 | 82715 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace hv arm at pole 709075 replace insulators at pole 708885 | .
1234 |  | JE24046251 | unknown HAMUA HUKANUI ROAD,Eketahuna,Eketahuna | Western | MANGAMAIRE | 2024-12-18 | 9:03 | 2024-12-18 | 10:01 | 0.0020569 | 3.5867e-05 | 13 | 746 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Faultman found that the earthing straps have rusted away and are just hanging, crew will return in morning to replace cable clamps and reconnect earthing. 18/12/24 - Line was isolated at Fuses S21 to replace cable clamps and reconnect the earthing. | .
1235 |  | JE24046255 | 412 PAREWANUI ROAD, BULLS, BULLS, 4894 | Western | PAREWANUI | 2024-12-18 | 10:46 | 2024-12-18 | 12:18 | 0.00075871 | 8.2769e-06 | 3 | 275 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace defected 11kV xarm on pole 809350 raised by Helicopter Topography | .
1236 |  | JE24046261 | 22 MURIMOTU ROAD, HUNTERVILLE, HUNTERVILLE, 4785 | Western | MANGAWEKA | 2024-12-18 | 10:35 | 2024-12-18 | 12:43 | 0.018275 | 0.00014347 | 52 | 6624 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Defected 11KV X-Arm on pole 806677 raised by Helicopter Topography | .
1237 |  | JE24046263 | 409 TOKOMARU WEST ROAD, BRUNSWICK, WANGANUI, 4571 | Western | WESTMERE PEAT ST | 2024-12-18 | 10:24 | 2024-12-18 | 14:30 | 0.095632 | 0.00038901 | 141 | 34662 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Repair Defects at poles 784049, 784014, 781988, 782892 & 784375 & 454486 for Helicopter Topography | .
1238 |  | JE24046394 | 791 BALLANCE VALLEY ROAD,BALLANCE,PAHIATUA | Western | MANGATAINOKA | 2024-12-18 | 9:54 | 2024-12-18 | 11:06 | 0.00039457 | 5.5179e-06 | 2 | 143 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: t7/105 No. Fuses: 1 Fuse Amp Size: 3 TIME CLOSED: 1105 Cause: Lightening Weather (wind/rain): not bad Follow up required (select advisory)? 2R not required | .
1239 |  | JE24046396 | 2105 WIREMU ROAD,NEWALL,NEW PLYMOUTH | Western | PARIHAKA | 2024-12-18 | 9:57 | 2024-12-18 | 13:21 | 0.065405 | 0.00062077 | 225 | 23706 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 12270/2 Protection flags (nil where none): E/F B Ø CAUSE: Broken binder Location: Pole 704958 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4, cursory patrolled. Weather (wind/rain): Windy LFI (Y/N + Comments): Yes incorrect operation. Follow up Required (select advisory)? Yes LFI may be incorrectly installed on the scada tile or field Additional fault restoration comments: Broken binder and conductor on cross arm. The LFI indication was indicating past ABS 6431 but the fault was past ABS 6430. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1240 |  | JE24046422 | unknown DOMAIN ROAD,Kairua,Rural | Eastern | BLACK STUMP | 2024-12-18 | 11:48 | 2024-12-18 | 17:41 | 0.025908 | 0.00034763 | 126 | 9390 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV Sw/Gear 13625/1 Protection flags (nil where none): A,B,C E/F CAUSE: Tree fell through Lines @ Pole 220881 Namu Conductor Location: Pole 220881 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Fault Rung in. Weather (wind/rain): Windy LFI (Y/N + Comments): Required!!! Follow up Required (select advisory)? Additional fault restoration comments: We Need permanent Locators @ ABS SD5-182 Site!!! Numerous faults in this Location. Franklin Trees Cut trees away, Site now Clear. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1241 |  | JE24046431 | 1243 DEVON ROAD,SENTRY HILL,NEW PLYMOUTH | Western | DEVON RD | 2024-12-18 | 12:35 | 2024-12-18 | 14:01 | 0.044678 | 0.0010015 | 363 | 16194 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 12214/2 Protection flags (nil where none): E/F C Ø CAUSE: Unknown, lines patrolled. Location: Unknown Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F1, cursory patrolled. Weather (wind/rain): Windy LFI (Y/N + Comments): Yes Follow up Required (select advisory)? No Additional fault restoration comments: Network patrolled past Sw/Gear 12778/3 and no visible fault cause could be found. Rec 12214 had a comms fail and could have halved the SAIDI if i could have closed the recloser. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1242 |  | JE24046439 | 11 TOWNSEND ROAD,HIKUTAIA,PAEROA | Eastern | PURIRI | 2024-12-18 | 13:25 | 2024-12-18 | 14:26 | 0.00050042 | 8.2769e-06 | 3 | 181 | Unplanned | WILDLIFE - BIRD | Fuses Location: FP2033 No. Fuses: 2 Fuse Amp Size: 2 AMP TIME CLOSED: 14:25PM Cause: Bird strike Weather (wind/rain): Calm Follow up required (select advisory)? | .
1243 |  | JE24046459 | 215 REID LINE EAST, AORANGI, FEILDING | Western | BUNNYTHORPE | 2024-12-18 | 15:05 | 2024-12-18 | 15:31 | 0.00014107 | 5.5179e-06 | 2 | 51 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Job was logged at Tfr 7487P but job was at Tfr T2/236. Faultman isolated Tfr T2/236 for safety, to re-attach neutral jumper away from the HV lines on Tfr T2/236. | .
1244 |  | JE24046510 | 155 ,, | Eastern | BARRETT RD | 2024-12-18 | 22:14 | 2024-12-19 | 3:40 | 0.0026988 | 8.2769e-06 | 3 | 978 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: Fuses SC2-065 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 20:35 Cause: Faulty Transformer Weather (wind/rain): Calm Follow up required (select advisory)? Yes Reload Reliven Failed, Spur line tripped again when replacing Transformer Fuses. Isolated Transformer again at Fuses SC2-065 and replaced Transformer TC2-144. Power restored 03:40Hrs | .
1245 |  | JE24046513 | 1231 BALL ROAD,HURLEYVILLE,PATEA | Western | KAKARAMEA | 2024-12-18 | 20:20 | 2024-12-18 | 23:03 | 0.0080465 | 0.0001545 | 41 | 2917 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Burnt out center contact on ABS LI782, ABS LI782 Opened and back feed from ABS LI790 to enable full voltage Outage required to replace faulty parts on ABS LI782, faultman organising bucket truck and required parts Isolated at ABS LI790 & LI707 ABS Repaired, Full power restored | .
1246 |  | JE24046527 | 422 DURHAM ROAD UPPER,NORFOLK,INGLEWOOD | Western | MOUNTAIN RD | 2024-12-18 | 19:06 | 2024-12-18 | 20:27 | 0.00088914 | 1.1036e-05 | 4 | 322 | Unplanned | WILDLIFE - BIRD | Fuses Location: 12362 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 20:26 Cause: Bird strike at Pole 761882 Weather (wind/rain): windy Follow up required (select advisory)?n Line patrolled | .
1247 |  | JE24046544 | unknown WHAREKAHO ROAD,Wharekaho,Rural | Eastern | KUAOTUNU | 2024-12-18 | 22:16 | 2024-12-18 | 22:18 | 0.0091034 | 0.0047675 | 1728 | 3300 | Unplanned | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | Voltage & Device ID: Recloser 9226 Protection flags (nil where none): Phase B,C -OC Weather (wind/rain): Calm Follow up required (select advisory): No LFI Activation: Y/N | .
1248 |  | JE24042797 | TAISUB-CGLEN 66KV | Eastern | TAISUB-CGLEN 66KV | 2024-12-17 | 13:44 | 2024-12-17 | 14:46 | 0.11538 | 0.027882 | 2352 | 41822 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Coromandel Generator Project: Stage A - Isolate Whangapoua generator 11kV switchboard to allow dead bus testing of generator Stage B - Unplanned Grid to Island transition and resynch (simulate 66kV outage while running Grid tied), Stage C - Island start, run and resynch (Coromandel Sub outage until generators on load), Please refer to attached switching methodology & commissioning brief. | .
1249 |  | JE24043113 | 476 KOPIKOPIKO ROAD, EKETAHUNA, PAHIATUA, 4988 | Western | MANGAMAIRE | 2024-12-17 | 9:31 | 2024-12-17 | 11:49 | 0.012223 | 8.8287e-05 | 32 | 4430 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace red tagged pole P43189 | .
1250 |  | JE24043132 | LINDERMANN RD | Eastern | LINDERMANN RD | 2024-12-17 | 8:53 | 2024-12-17 | 15:32 | 0.063824 | 0.00016002 | 58 | 23133 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv/400vt cross arms @ poles 204485,204486,204487,204489 & 204490. Replace 11kv pole 204488.Isolation point @ SB1-041. | .
1251 |  | JE24043164 | 358 ALLEN ROAD, OHANGAI, HAWERA, 4672 | Western | WHAKAMARA | 2024-12-17 | 9:10 | 2024-12-17 | 15:35 | 0.0053032 | 1.3795e-05 | 5 | 1922 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace pole 725990 with new tx structure double 11m pole. relocate tx W2335 to pole 725990. replace hv pin arm at pole 725989. remove all redundant lines & hardware past pole 725990 | .
1252 |  | JE24043165 | ASHHURST | Western | ASHHURST | 2024-12-17 | 11:05 | 2024-12-17 | 11:22 | 0.00066371 | 3.8625e-05 | 14 | 241 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | install buck am on transformer T2/497. Install arm brace bolt at P41183. | .
1253 |  | JE24043341 | 799 TARATA ROAD, KAIMATA, INGLEWOOD, 4387 | Western | KOHETE RD | 2024-12-17 | 10:17 | 2024-12-17 | 17:00 | 0.010006 | 2.4831e-05 | 9 | 3627 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace crossarms @ poles 760001,760002,760003,760004,760015,760017,760018,760019,760020,760021 | .
1254 |  | JE24043545 | 2936 WHITE ROCK ROAD, TUTURUMURI, MARTINBOROUGH, 5782 | Western | TUTURUMURI | 2024-12-17 | 8:45 | 2024-12-17 | 13:46 | 0.024067 | 8.001e-05 | 29 | 8723 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace multiple defects past C633/2 | .
1255 |  | JE24046074 | 36 MANGATANGI ROAD,WAVERLEY,WAVERLEY | Western | WAVERLEY | 2024-12-17 | 3:02 | 2024-12-17 | 6:19 | 0.14322 | 0.0015367 | 557 | 51909 | Unplanned | LIGHTNING - LIGHTNING STRIKE | CAUSE: Line down due to lightning strike Location: Pole 772019 Isolation: 4809/6 & O98 Backfeeds: Via ABS 499 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): Heavy Rain / Lightning LFI (Y/N + Comments): None Installed Follow up Required (select advisory)? Additional fault restoration comments: FM found low voltages on Tx X307 indicating HV fault. Patrolled back to find HV line down. HV line repaired SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1256 |  | JE24046080 | unknown unknown,Alfredton,Rural | Western | CASTLEHILL | 2024-12-17 | 5:34 | 2024-12-17 | 8:22 | 0.0018499 | 1.1036e-05 | 4 | 671 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: t9/372 No. Fuses: 3 Fuse Amp Size: 2 TIME CLOSED: 0821 Cause: lightening Weather (wind/rain): rain Follow up required (select advisory)? | .
1257 |  | JE24046082 | 26 LENIHAN DRIVE,TE PUKE,TE PUKE | Eastern | MANGOREWA | 2024-12-17 | 5:40 | 2024-12-17 | 11:27 | 0.13582 | 0.0013353 | 484 | 49228 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV sec 9689 Tripped TPV 11kV CB 2 A/R Protection flags (nil where none): A,B,C O/C CAUSE: Ducks Location: Pole 230216 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: Cursory Weather (wind/rain): Rain LFI (Y/N + Comments): Yes Poles 230164 & 221755 Follow up Required (select advisory)? No Additional fault restoration comments: Te Puke CB 2 supporting PGA CB 1& 6 due to sub station upgrade Line spatrolled and sectionalised . Lines down repaired under access permit. Power restored 11:27. Caused by bird strike, ducks. | .
1258 |  | JE24046083 | unknown CASTLE HILL ROAD,Tinui,Rural | Western | CASTLEHILL | 2024-12-17 | 5:51 | 2024-12-17 | 7:38 | 0.00059094 | 5.5179e-06 | 2 | 214 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: t9/382 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 0738 Cause: lightening Weather (wind/rain): rain Follow up required (select advisory)? | .
1259 |  | JE24046090 | 88 SEDDON ROAD,WAITOA,TE AROHA | Eastern | NGARUA | 2024-12-17 | 9:41 | 2024-12-18 | 0:31 | 0.012275 | 1.3795e-05 | 5 | 4449 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: Fuses FP1814 Protection flags (nil where none): NIL CAUSE: Tree on Lines Location: Pole C2622 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): None Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): None Follow up Required (select advisory)? No Additional fault restoration comments: Replaced 1 x11kV pole and two 400V poles and repaired lines Inpsected each premises for traces of line clash, each installtion was fine and no sign of line clash or damage | .
1260 |  | JE24046091 | 327 KAKA AMU ROAD,RANGITUMAU,MASTERTON | Western | OXFORD ST | 2024-12-17 | 6:40 | 2024-12-17 | 8:11 | 0.00050394 | 5.5179e-06 | 2 | 183 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: t2584 No. Fuses: 3 Fuse Amp Size: 2 TIME CLOSED: 0810 Cause: lightening Weather (wind/rain): overcast Follow up required (select advisory)? | .
1261 |  | JE24046093 | 357 TE MAIRE ROAD,KAHUTARA,FEATHERSTON | Western | DAIRY FACTORY | 2024-12-17 | 6:46 | 2024-12-17 | 8:29 | 0.00056676 | 5.5179e-06 | 2 | 205 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: fuses 7230 No. Fuses: 3 Fuse Amp Size: 3amp TIME CLOSED: 08:28 Cause: Lightning Weather (wind/rain): calm - drizzly Follow up required (select advisory)? | .
1262 |  | JE24046100 | 568 LEPPER ROAD UPPER,KAIMIRO,INGLEWOOD | Western | KAIPI RD | 2024-12-17 | 7:07 | 2024-12-17 | 9:19 | 0.023695 | 0.00031176 | 113 | 8588 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 8260/2 Protection flags (nil where none): O/C E/F C Ø CAUSE: Line down Location: 745901 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4, cursory patrolled. Weather (wind/rain): Strong wind LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Replaced HV pin and 2m 16mm² HD Cu conductor, 2 x MST sleeves and binder SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1263 |  | JE24046103 | unknown POHANGINA VALLEY EAST ROAD,Apiti,Rural | Western | APITI | 2024-12-17 | 7:29 | 2024-12-17 | 10:51 | 0.0016662 | 8.2769e-06 | 3 | 604 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: P59 No. Fuses: 1 Fuse Amp Size: 6amp TIME CLOSED: 10:50 Cause: lightning Weather (wind/rain): calm Follow up required (select advisory)? Also used 2R - tx T4/233 closed - 10:30am cause : lightning fuse : 1 x 3amp asset no : tx 4/52 cause : lightning time : 10:50 am fuse size : 2 x 3amp | .
1264 |  | JE24046115 | 836 TE ORE ORE BIDEFORD ROAD,BIDEFORD,MASTERTON | Western | BIDEFORD | 2024-12-17 | 8:17 | 2024-12-17 | 10:53 | 0.00086145 | 5.5179e-06 | 2 | 312 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 7763 No. Fuses: 2 Fuse Amp Size: 6amp TIME CLOSED: 10:52 Cause: lightning Weather (wind/rain): calm Follow up required (select advisory)? 2R used site : T901 cause : lightning size : 2amp No of fuses : 2 x 2amp weather : calm | .
1265 |  | JE24046116 | unknown RIDGE ROAD,Pohangina,Rural | Western | APITI | 2024-12-17 | 8:27 | 2024-12-17 | 14:15 | 0.0028837 | 8.2769e-06 | 3 | 1045 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Tfr T4/131 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 14:15 Cause: Lightning Weather (wind/rain): Rain Follow up required (select advisory)?N | .
1266 |  | JE24046118 | 334A MANGAKUKEKE ROAD,MANGAWEKA,MANGAWEKA | Western | MANGAWEKA | 2024-12-17 | 8:27 | 2024-12-17 | 11:11 | 0.0022537 | 1.3795e-05 | 5 | 817 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: X2982 No. Fuses: X2 Fuse Amp Size: 2AMP TIME CLOSED: 11:10 AM Cause: LIGHTNING Weather (wind/rain): Calm Follow up required (select advisory)? | .
1267 |  | JE24046120 | 242 STOPFORD ROAD,TE POI,MATAMATA | Eastern | TE POI | 2024-12-17 | 13:02 | 2024-12-17 | 16:16 | 0.0016038 | 8.2769e-06 | 3 | 581 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: TC2278 Fuses CAUSE: Lightning Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): NIL Circuit patrolled & type: NIL Weather (wind/rain): Fine Follow up required (select advisory)? NIL Additional fault restoration comments: Transformer Blown Replaced - Relivened at 16:15 | .
1268 |  | JE24046122 | unknown DORSETS ROAD,Rangitumau,Rural | Western | OXFORD ST | 2024-12-17 | 8:36 | 2024-12-17 | 8:48 | 0.0001307 | 1.1036e-05 | 4 | 47 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: t2670 No. Fuses: 3 Fuse Amp Size: 3 TIME CLOSED: 0847 Cause: lightening Weather (wind/rain): overcast Follow up required (select advisory)? | .
1269 |  | JE24046126 | 203 KAKA AMU ROAD,RANGITUMAU,MASTERTON | Western | OXFORD ST | 2024-12-17 | 8:46 | 2024-12-17 | 9:23 | 0.00010267 | 2.759e-06 | 1 | 37 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: t3026 No. Fuses: 3 Fuse Amp Size: 2 TIME CLOSED: 0923 Cause: lightening Weather (wind/rain): overcast Follow up required (select advisory)? | .
1270 |  | JE24046133 | 934 COONOOR ROAD,PAHIATUA,PAHIATUA | Western | COONOOR | 2024-12-17 | 8:56 | 2024-12-17 | 10:45 | 0.00054759 | 5.5179e-06 | 2 | 198 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T7/392 No. Fuses:2 Fuse Amp Size: 2AMP TIME CLOSED: 10:25 AM Cause: LIGHTNING Weather (wind/rain): CALM Follow up required (select advisory)? 2R USED advised also closed in links at T7/391 | .
1271 |  | JE24046141 | unknown unknown,Turangaomoana,Rural | Eastern | MOWBRAY RD | 2024-12-17 | 21:00 | 2024-12-17 | 23:30 | 0.00041417 | 2.759e-06 | 1 | 150 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Unbalanced phase 242V 242V 264V Isolated at the TRF LV. Farmer ok with power off. to be attended later. Suspect Transformer burnt to be replaced . Caused by lightning. Transformer Replaced - Power Restored 23:35 | .
1272 |  | JE24046156 | 431 KAKA AMU ROAD,RANGITUMAU,MASTERTON | Western | OXFORD ST | 2024-12-17 | 6:59 | 2024-12-17 | 8:32 | 0.0015434 | 1.6554e-05 | 6 | 559 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: t550 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 0832 Cause: lightening Weather (wind/rain): overcast Follow up required (select advisory)? See child jobs for the below Fuses Location: t2016 No. Fuses: 1 Fuse Amp Size: 2 TIME CLOSED: 0833 Cause: lightening Weather (wind/rain): overcast Follow up required (select advisory)? Fuses Location: t2395 No. Fuses: 1 Fuse Amp Size: 2 TIME CLOSED: 0906 Cause: lightening Weather (wind/rain): overcast Follow up required (select advisory)? | .
1273 |  | JE24046173 | unknown unknown ,Ocean Beach,Rural | Western | PIRINOA | 2024-12-17 | 14:30 | 2024-12-18 | 7:26 | 0.0028011 | 2.759e-06 | 1 | 1015 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Faultman found cable end had burnt off at Fuses 7290, line was isolated at Fuses 7290. Cable crew will return to and in piece of new cable and re-terminate the cable. | .
1274 |  | JE24046183 | 1140 OHANGAI ROAD,OHANGAI,HAWERA | Western | MEREMERE | 2024-12-17 | 10:41 | 2024-12-17 | 13:43 | 0.01975 | 0.00029797 | 108 | 7158 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 12080/2 Protection flags (nil where none): E/F A Ø CAUSE: Floating conductor Location: Pole 842518 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4, Cursory patrolled Weather (wind/rain): Strong wind LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Floating conductor found at Pole 842518 Replaced 3 x binders SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1275 |  | JE24046188 | 331 LIMESTONE ROAD,APITI,KIMBOLTON | Western | APITI | 2024-12-17 | 16:10 | 2024-12-17 | 20:18 | 0.0013661 | 5.5179e-06 | 2 | 495 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: Tfr T4/264 CAUSE: Lightning Temp generation (stage details when used): N PERFORMANCE DETAIL DNO (number or state no): N Circuit patrolled & type: cursory Weather (wind/rain): Rain Follow up required (select advisory)?N Additional fault restoration comments: TX T4/264 is going to be replaced by Craig Evans, damaged by lighting Transformer T4/264 Replaced Power restored | .
1276 |  | JE24046195 | FEEDER FAULT - TE ORE ORE - WERAITI CB830 | Western | WERAITI | 2024-12-17 | 11:17 | 2024-12-17 | 14:03 | 0.081847 | 0.0012471 | 348 | 29666 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB C830 Protection flags (nil where none): C ph O/C & E/F CAUSE: Tree touching lines in wind Location: 827644 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: Cursory Weather (wind/rain): V. Windy LFI (Y/N + Comments): N Follow up Required (select advisory)? N Additional fault restoration comments: Line was patrolled and Faultman found tree touching line in the heavy winds, lines were isolated at ABS S64, there was a tree contractor in area and Faultman asked them to fell the tree between poles 827644 & 827645. | .
1277 |  | JE24046199 | 809 RANGATIRA ROAD,HUNTERVILLE,MARTON | Western | PUTORINO | 2024-12-17 | 11:23 | 2024-12-17 | 19:35 | 0.024667 | 0.00014347 | 52 | 8941 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 4246 Protection flags (nil where none): A Ph O/C E/F CAUSE: Bird strike Location: 806904 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Windy LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Line down caused by Magpie Isolated at Fuses 4078 Line Repaired SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1278 |  | JE24046209 | 830 VALLEY ROAD,ASHHURST,FEILDING | Western | POHANGINA | 2024-12-17 | 11:48 | 2024-12-17 | 13:30 | 0.00028158 | 2.759e-06 | 1 | 102 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T 4/326 No. Fuses: 2 Fuse Amp Size: 3amp TIME CLOSED: 13:15 Cause: lightning Weather (wind/rain): wind Follow up required (select advisory)? | .
1279 |  | JE24046217 | 5 BONNIEGLEN ROAD,OMANAWA,TAURANGA | Eastern | KEENAN RD | 2024-12-17 | 13:20 | 2024-12-17 | 17:50 | 0.0044679 | 1.6554e-05 | 6 | 1619 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faulty Transformer TE3-137 Replaced under Access Permit. Power restored 17:50 | .
1280 |  | JE24046226 | 2934 PAHIATUA PONGAROA ROAD,MAKURI,PAHIATUA | Western | COONOOR | 2024-12-17 | 12:33 | 2024-12-17 | 13:20 | 0.00025754 | 5.5179e-06 | 2 | 93 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T7/367 No. Fuses: 2 Fuse Amp Size: 2amp TIME CLOSED: 13:20 Cause: lightning Weather (wind/rain): Follow up required (select advisory)? | .
1281 |  | JE24046243 | 364 BENNER ROAD,PUKEHINA,TE PUKE | Eastern | ROTOEHU | 2024-12-17 | 16:10 | 2024-12-17 | 18:23 | 0.0010993 | 8.2769e-06 | 3 | 398 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: Fuses SF7-043 Protection flags (nil where none): NIL CAUSE: Trees through Lines Location: Pole 422376 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): None Circuit patrolled and type: Cursory Weather (wind/rain): Windy LFI (Y/N + Comments): Yes at 422273 Follow up Required (select advisory)? Additional fault restoration comments: Isolated lines and removed trees and repaired lines. | .
1282 |  | JE24046262 | unknown unknown ,Kaitawa,Pahiatua | Western | COONOOR | 2024-12-17 | 15:59 | 2024-12-17 | 17:38 | 0.00082452 | 8.2769e-06 | 3 | 299 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: Tfr T7/304 CAUSE: Lightning Temp generation (stage details when used): N PERFORMANCE DETAIL DNO (number or state no): N Circuit patrolled & type: cursory Weather (wind/rain): Lightning Follow up required (select advisory)?N Additional fault restoration comments: TFR Replaced LV Isolated before livening of TFR T7/304, Testing carried out, no faults found on network equipment, TFR T7/304 400V Fuses closed at 19:12, Full power restored | .
1283 |  | JE24046275 | 1413 SH 3,WAVERLEY,WAVERLEY | Western | WAITOTARA | 2024-12-17 | 15:24 | 2024-12-17 | 17:31 | 0.00035036 | 2.759e-06 | 1 | 127 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: TX 4542W No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 17:30 Cause: LIGHTNING Weather (wind/rain): WINDY Follow up required (select advisory)? FULL POWER | .
1284 |  | JE24046282 | 806 NIREAHA ROAD,EKETAHUNA,EKETAHUNA | Western | HUKANUI | 2024-12-17 | 15:56 | 2024-12-17 | 17:39 | 0.0011434 | 1.1036e-05 | 4 | 414 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: TX T8/201 No. Fuses: 2 Fuse Amp Size: 2A PLUS CARRIERS TIME CLOSED: 17:39 Cause: LIGHTNING Weather (wind/rain): WINDY Follow up required (select advisory)? FULL POWER | .
1285 |  | JE24046308 | 327 HEREFORD PARK ROAD,PUKEHINA,TE PUKE | Eastern | ROTOEHU | 2024-12-17 | 21:36 | 2024-12-17 | 22:16 | 0.00033135 | 8.2769e-06 | 3 | 120 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: Fused ABS SF7-029 No. Fuses: 3 Fuse Amp Size: 20A TIME CLOSED: 22:16 Cause: Line Clash Heavy Winds Weather (wind/rain): Windy Follow up required (select advisory)? NIL | .
1286 |  | JE24046325 | 46 MANGAMAHU ROAD,FORDELL,WANGANUI | Western | FORDELL | 2024-12-17 | 16:26 | 2024-12-17 | 19:46 | 0.0016501 | 8.2769e-06 | 3 | 598 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: 940 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 1945 Cause: WIND Weather (wind/rain): Follow up required (select advisory)? RESTORED | .
1287 |  | JE24041394 | SPRINGDALE | Eastern | SPRINGDALE | 2024-12-16 | 10:06 | 2024-12-16 | 10:50 | 0.0002461 | 5.5179e-06 | 2 | 89 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace defect pole C13959 Only replaced cross arm not the whole pole | .
1288 |  | JE24042024 | 120 LOVEGROVE ROAD, TE AROHA, TE AROHA, 3393 | Eastern | TE AROHA BOROUGH | 2024-12-16 | 9:01 | 2024-12-16 | 14:03 | 0.045008 | 0.00014898 | 54 | 16313 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Poles C348, C362, C13159, C361, C363, C364. Replace Pole and ABS at Pole C13160 and ABS IC540. Run new Lv conductor between Poles C348 and C364. | .
1289 |  | JE24042908 | 26 HULL ROAD, MOUNT MAUNGANUI, TAURANGA, 3116 | Eastern | PORTSIDE | 2024-12-16 | 10:11 | 2024-12-16 | 16:02 | 0.001937 | 5.5179e-06 | 2 | 702 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace TX TC4-217 due to red defect | .
1290 |  | JE24042912 | 16 ADMIRAL PLACE, TAKARO, PALMERSTON NORTH, 4412 | Western | TREMAINE AVE | 2024-12-16 | 23:41 | 2024-12-17 | 2:52 | 0.023709 | 0.00012415 | 45 | 8594 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Perform oil maintenance at FS140/357/358. | .
1291 |  | JE24042932 | 37 ST ANDREWS DRIVE, TOKOROA, TOKOROA, 3420 | Eastern | DALMENY ST | 2024-12-16 | 9:00 | 2024-12-16 | 9:55 | 0.011232 | 0.0002014 | 73 | 4071 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To carry out oil repair works on TC3207 and top up oil | .
1292 |  | JE24042938 | 1549 TE AROHA ROAD, GORDON, MATAMATA, 3471 | Eastern | GORDON | 2024-12-16 | 9:11 | 2024-12-16 | 10:27 | 0.0012664 | 1.6554e-05 | 6 | 459 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace HV pin pole F12802 and Replace HV xarm on Pole F12804. Job not done due to lightning in the vicinity and heavy rain. | .
1293 |  | JE24042939 | 274 MAKOMAKO ROAD, BALLANCE, PAHIATUA, 4983 | Western | MANGATAINOKA | 2024-12-16 | 9:33 | 2024-12-16 | 13:12 | 0.039313 | 0.00017933 | 65 | 14249 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace 11kV poles P16644 & P16651 | .
1294 |  | JE24042943 | 99 MAIN ROAD, TOKOROA, TOKOROA, 3420 | Eastern | ASHWORTH ST | 2024-12-16 | 23:10 | 2024-12-17 | 2:24 | 0.0005357 | 2.759e-06 | 1 | 194 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To carry out oil leak repair and top up oil on TC5665 | .
1295 |  | JE24043394 | 240 WARNER ROAD, OROPI, TAURANGA, 3173 | Eastern | WAIMAPU | 2024-12-16 | 8:47 | 2024-12-16 | 15:00 | 0.025755 | 6.8974e-05 | 25 | 9335 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace crossarms 211248 to 211250 (TE4-169) | .
1296 |  | JE24043552 | 15 KITCHENER STREET, LANSDOWNE, MASTERTON, 5810 | Western | GORDON ST | 2024-12-16 | 9:16 | 2024-12-16 | 11:26 | 0.12142 | 0.00093253 | 338 | 44008 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove ABS S91 from network | .
1297 |  | JE24045093 | 2168 TE MATAI ROAD, TE PUKE, 3188 | Eastern | TE MATAI RD | 2024-12-16 | 13:00 | 2024-12-16 | 13:20 | 5.5547e-05 | 2.759e-06 | 1 | 20 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Checked for safety found no immediate safety issue, needs power off to repair but dairy farm couldn't go off right away as middle of milking will return latter in week on 2r Re clamped saddle CLAMP onto cross and restored power. Power Off -13:00 Power on 13:20 | .
1298 |  | JE24045564 | 23 UREKAWA ROAD, PATEA, PATEA, 4597 | Western | PORTLAND QUAY | 2024-12-16 | 8:39 | 2024-12-16 | 10:26 | 0.0023694 | 2.2072e-05 | 8 | 859 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace deteriorated xarm at pole 727411 | .
1299 |  | JE24045598 | 1058A UPPER KAHAROA ROAD, PATEA, PATEA, 4597 | Western | PORTLAND QUAY | 2024-12-16 | 11:01 | 2024-12-16 | 12:27 | 0.00095718 | 1.1036e-05 | 4 | 347 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace crossarm at pole 727107 | .
1300 |  | JE24045682 | 111 PARSONS ROAD, PATEA, PATEA, 4597 | Western | OTAUTU | 2024-12-16 | 9:31 | 2024-12-16 | 15:21 | 0.009655 | 2.759e-05 | 10 | 3500 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace pole 727769 and new stay | .
1301 |  | JE24045685 | 647 OTAUTO ROAD, PATEA, PATEA, 4597 | Western | PORTLAND QUAY | 2024-12-16 | 10:46 | 2024-12-16 | 13:51 | 0.0091873 | 4.9661e-05 | 18 | 3330 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace hv & lv pin arm at pole 727621. remove redundant lv term arm | .
1302 |  | JE24045687 | 163 PIPIRIKI RAETIHI ROAD, RAETIHI, RAETIHI, 4694 | Western | RAETIHI | 2024-12-16 | 11:05 | 2024-12-16 | 13:54 | 0.10829 | 0.00064008 | 232 | 39251 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11KV X-arms & Binders at 777284, 373113, 777896, 777256 raised by Helicopter Topography | .
1303 |  | JE24045742 | 5421 MASTERTON CASTLEPOINT ROAD, TINUI, MASTERTON, 5889 | Western | CASTLEPOINT | 2024-12-16 | 9:02 | 2024-12-16 | 15:14 | 0.075573 | 0.0014374 | 315 | 27392 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv pole 838619 with strain pole. Replace 11kv arm at pole 838620. Install new 11kV pole to fix low lines between 838619 & 838620 | .
1304 |  | JE24045881 | 582 ONGO ROAD,HUNTERVILLE,HUNTERVILLE | Western | HUNTERVILLE 22KV | 2024-12-16 | 5:52 | 2024-12-16 | 8:00 | 0.0085273 | 6.6215e-05 | 24 | 3091 | Unplanned | WILDLIFE - BIRD | Fuses Location: 997 No. Fuses: 2 Fuse Amp Size: 10 amp TIME CLOSED: 8am Cause: Bird strike Weather (wind/rain): calm Follow up required (select advisory)? | .
1305 |  | JE24045914 | FEEDER FAULT - PUTARURU SUB - LICHFIELD - REC13232 | Eastern | LICHFIELD | 2024-12-16 | 9:41 | 2024-12-16 | 22:34 | 0.066894 | 0.00054352 | 101 | 24246 | Unplanned | LIGHTNING - LIGHTNING STRIKE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 13232/2 Protection flags (nil where none): E/F CAUSE: Lightning strike Location: TC4336 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4, operational patrol Weather (wind/rain): Lightning/ rain LFI (Y/N + Comments): Yes past ABS 919, 2 x Ø Follow up Required (select advisory)? No Additional fault restoration comments: Fault man instructed to open all fuses so as to liven the main line and to liven each transformer and test voltage, only found TC4336 & TC1473 blown Outage at Transformer TC4336 - Fuses Closed at 19:39 Outage at Transformer TC 1473 - Fuses Closed at 22:33 | .
1306 |  | JE24045918 | 461 OTAMARAKAU VALLEY ROAD,PUKEHINA,TE PUKE | Eastern | MANGOREWA | 2024-12-16 | 9:45 | 2024-12-16 | 10:40 | 0.00030487 | 5.5179e-06 | 2 | 111 | Unplanned | WILDLIFE - BIRD | Fuses Location: fuses SF8-008 No. Fuses: 2 Fuse Amp Size: 8A TIME CLOSED: 10:40 Cause: Birds Weather (wind/rain): Rain Follow up required (select advisory)?No | .
1307 |  | JE24046010 | unknown WESTMERE ROAD,Wainuioru,Rural | Western | WERAITI | 2024-12-16 | 16:47 | 2024-12-16 | 17:16 | 0.0083593 | 0.00028693 | 104 | 3030 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | ETA 30 min Check on closure JE24046014 Burnt out fuse to Reg T1482/2, Isolated at ABS S64, Isolated and Bypassed Reg T1482/2, Re-Livened ABS S64 New Regulator Fuses have to be ordered - 2R to be left open Regulators do not have an external indication of neutral tap position. Crew will apply for a planned outage in the new year to replace the Fuses and restore the regulators to service. DNO 2412017 | .
1308 |  | JE24046020 | 463A OTAUTO ROAD,PATEA,PATEA | Western | OTAUTU | 2024-12-16 | 17:20 | 2024-12-16 | 23:34 | 0.0020597 | 5.5179e-06 | 2 | 747 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: Fuses 6445 CAUSE: Faulty Transformer 5088E. Aged Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: Weather (wind/rain): Calm Follow up required (select advisory)? Additional fault restoration comments: Replaced 10/11/3ph Tranny with a 15/11/3ph & replaced 3x 2A HV fuse links | .
1309 |  | JE24046021 | 4 SOMERSET ROAD,CLAREVILLE,CARTERTON | Western | SOMERSET RD | 2024-12-16 | 15:48 | 2024-12-16 | 18:55 | 0.059919 | 0.00077251 | 280 | 21718 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB C831 Protection flags (nil where none): E/F CAUSE: Lines down Location: between Poles 824417 & 824418 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): NIL Circuit patrolled and type: Cursory Patrol Weather (wind/rain): Fine Windy LFI (Y/N + Comments): NIL Follow up Required (select advisory)? NIL Additional fault restoration comments: Isolated at CB C831 & ABS S343, back feed put in place via GLA C944, line has broken mid span, unknown cause | .
1310 |  | JE24046031 | 1016 STATE HIGHWAY 3, WAVERLEY, 4591 | Western | RANGIKURA | 2024-12-16 | 17:18 | 2024-12-16 | 21:16 | 0.018427 | 0.00018761 | 68 | 6679 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV, Rec 1112 Protection flags (nil where none): E/F, B phase CAUSE: Truck v Pole Location: 771443 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Calm LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Rec 1112 A/R. Call of Truck v Pole came in so Operator opened Rec 1112 for safety. Rec 1112 relivened on fault being isolated at Fuses 2898. NDR to follow. Pole Block may still need to be installed. Pole was moved but otherwise undamaged. HV & LV lines were restrained. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1311 |  | JE24046043 | 806 KAHUTARA ROAD,KAHUTARA,FEATHERSTON | Western | DAIRY FACTORY | 2024-12-16 | 21:14 | 2024-12-16 | 22:59 | 0.00028969 | 2.759e-06 | 1 | 105 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Transformer T1003 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 22:58 Cause: Lightning Weather (wind/rain): Light Rain Follow up required (select advisory)? NIL | .
1312 |  | JE24046044 | 392 TE MAIRE ROAD,KAHUTARA,FEATHERSTON | Western | DAIRY FACTORY | 2024-12-16 | 21:17 | 2024-12-16 | 22:23 | 0.00036352 | 5.5179e-06 | 2 | 132 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Transformer T2832 No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 22:22 Cause: Lightning Weather (wind/rain): Light Rain Follow up required (select advisory)? NIL | .
1313 |  | JE24046046 | 580 KAHUTARA ROAD,KAHUTARA,FEATHERSTON | Western | DAIRY FACTORY | 2024-12-16 | 21:22 | 2024-12-16 | 23:25 | 0.00033901 | 2.759e-06 | 1 | 123 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Transformer T2831 No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 23:25 Cause: Lightning Weather (wind/rain): rain Follow up required (select advisory)? nil | .
1314 |  | JE24046052 | 37 BLAKES ROAD,MOUNT HOLDSWORTH,CARTERTON | Western | HOLDSWORTH | 2024-12-16 | 23:06 | 2024-12-17 | 1:41 | 0.00085487 | 5.5179e-06 | 2 | 310 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Transformer T1164 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 01:41 Cause: Lightning Weather (wind/rain): Fine Follow up required (select advisory)? NIL | .
1315 |  | JE24046058 | 398 DORSETS ROAD,RANGITUMAU,MASTERTON | Western | OXFORD ST | 2024-12-16 | 23:28 | 2024-12-17 | 2:25 | 0.00097818 | 5.5179e-06 | 2 | 355 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Transformer T551 No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: Nil Cause: Lightning Weather (wind/rain): Rain, Wind Fog Follow up required (select advisory)? Fuses Location: Fuses 7481 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 02:25 Cause: Lightning Weather (wind/rain): Rain, Wind Fog Follow up required (select advisory)? | .
1316 |  | JE24046061 | 18 KAUARAPAOA ROAD,BRUNSWICK,WANGANUI | Western | MAKIRIKIRI | 2024-12-16 | 23:34 | 2024-12-17 | 21:40 | 0.082592 | 0.00033383 | 39 | 29936 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 2995 Protection flags (nil where none): O/C, B-C phase CAUSE: Branch on lines Location: 784998 - 784999, 851760 - 852803, 851779 - 784984 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: Cursory Weather (wind/rain): Light Rain / Windy LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Line was isolated at Links 2650, patrolled at day light, Faultman found branch over lines between poles 784998 - 784999, 851760 - 852803 & 851779 - 784984, branch's where removed with hot line sticks, Full power restored | .
1317 |  | JE24045852 | 67 WHANGAEHU BEACH ROAD,WHANGAEHU,WANGANUI | Western | FORDELL | 2024-12-15 | 13:33 | 2024-12-15 | 14:55 | 0.00067724 | 8.2769e-06 | 3 | 245 | Unplanned | WILDLIFE - BIRD | Fuses Location: 16041 No. Fuses: 2 Fuse Amp Size: 2 TIME CLOSED: 14:55 Cause: Bird strike Weather (wind/rain): calm Follow up required (select advisory)?n Line Patrolled | .
1318 |  | JE24045863 | 298 BEDFORD ROAD NORTH,KAIMIRO,INGLEWOOD | Western | MOUNTAIN RD | 2024-12-15 | 18:00 | 2024-12-15 | 20:16 | 0.0048599 | 3.5867e-05 | 13 | 1762 | Unplanned | WILDLIFE - BIRD | Line down past Pole 461268 Cause: Bird Strike Isolated at Fuses 5547 Line repaired, Full power restored Replaced 5mtrs of conductor & 2 sleeves Weather: Calm | .
1319 |  | JE24045866 | 465 NO 4 ROAD, TE PUKE | Eastern | NO 3 ROAD | 2024-12-15 | 22:06 | 2024-12-16 | 12:42 | 0.021749 | 2.4831e-05 | 9 | 7883 | Unplanned | VEGETATION - OUTSIDE ZONE | Tree through Lines Fuse/SW 13145/2 Tripped Isolated at Fuse/Sw 13145/2 Access issues to site Customer Contacted and happy with power to remain off till morning FM to return in morning REGULATORY INFORMATION Voltage & Device ID: Fuse /Sw 13145/2 Protection flags (nil where none): None CAUSE: Trees through lines Location: Pole 269279 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Rain LFI (Y/N + Comments): Nil Follow up Required (select advisory)? No Additional fault restoration comments: Trees removed, straightened and put a block on pole 269279.Replaced conductor and lines repaired under Access Permit,. Replaced 3 x15A Safe Link Fuses at Fuse/Sw 13142/2. Full Power restored 12:42Hrs SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): No Circuit that tripped: N/A DTF (KM):N/A | .
1320 |  | JE24045873 | 109 KIRIHAU ROAD,KORU,NEW PLYMOUTH | Western | PIONEER RD | 2024-12-15 | 21:47 | 2024-12-15 | 23:01 | 0.0034647 | 4.6902e-05 | 17 | 1256 | Unplanned | WILDLIFE - BIRD | Fuses Location: 6466 No. Fuses: 2 Fuse Amp Size: 8 Amp TIME CLOSED: 23:00 hrs Cause: Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? | .
1321 |  | JE24045876 | unknown KAHUTARA ROAD,Pirinoa,Rural | Western | KUMENGA | 2024-12-15 | 22:26 | 2024-12-16 | 0:58 | 0.0021015 | 1.3795e-05 | 5 | 762 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 7347 No. Fuses: 2 Fuse Amp Size: 20 Amp plus carrier TIME CLOSED: 00:57 Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)? N | .
1322 |  | JE24044645 | 210 BEACH ROAD, THAMES, THAMES, 3500 | Eastern | A & G PRICE | 2024-12-14 | 7:25 | 2024-12-14 | 14:11 | 0.0011205 | 2.759e-06 | 1 | 406 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Service CB11 at Thames Sub, then put into Circuit Earth so Northpower can can a Switch (CB) on A & G Price Sub. Plus Service CB16 Buscoupler at Thames Sub | .
1323 |  | JE24044684 | 2977 TE WHARAU ROAD, TE WHARAU, MASTERTON, 5883 | Western | WESTMERE GLADSTONE | 2024-12-14 | 10:01 | 2024-12-14 | 12:17 | 0.0022618 | 1.6554e-05 | 6 | 820 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv pole 834001 | .
1324 |  | JE24045689 | 69 PARAITE ROAD, BELL BLOCK, NEW PLYMOUTH, 4312 | Western | DE HAVILLAND SOUTH | 2024-12-14 | 8:30 | 2024-12-14 | 10:42 | 0.00036262 | 2.759e-06 | 1 | 131 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | DNO 2412008 for Safelink 8868. Replacing with like-4-like unit. | .
1325 |  | JE24045754 | 607 CAMERON ROAD, TAURANGA SOUTH, TAURANGA, 3112 | Eastern | 10TH AVE | 2024-12-14 | 7:10 | 2024-12-14 | 8:30 | 0.00066367 | 8.2769e-06 | 3 | 241 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To remove faulty cable between SK5-034 and SK5-153 so that equipment can be used to locate exact fault location in cable. Outage to remove cable from switchgear at each end for testing. Network outage is for testing and fault identification, once cable disconnected and covers on supply to be restored to TK5-026. Hole left in network between SK5-034 & SK5-153. | .
1326 |  | JE24045771 | 347 WAITARA ROAD,HUIRANGI,WAITARA | Western | TIKORANGI 33kV | 2024-12-14 | 6:04 | 2024-12-14 | 6:12 | 0.0035986 | 0.00047454 | 172 | 1304 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 33kV, CB 1342 & CB 210 Protection flags (nil where none): E/F CAUSE: Unk Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Yes / Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): Yes, indicate fault past ABS 166 Follow up Required (select advisory)? Protection review as MCK CB 191 should have cleared this fault instead it was cleared by HUI CB 1342 Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Mangahewa, MCK, ING, MOK Generation Circuit that tripped: CB 1342 DTF (KM): N/A | .
1327 |  | JE24045780 | 65 PARRIS STREET,WAITARA,WAITARA | Western | BLAKE ST | 2024-12-14 | 10:17 | 2024-12-14 | 12:40 | 0.030121 | 0.00020968 | 76 | 10917 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Location: Transformer 3556T Cause: Faulted Termination onto Transformer 3556T due to Oxidisation. Isolation: ABS 5070 What was replaced? Replaced Crimp Lug & Heat Shrinks Also replaced padlock at ABS 5070 as it would not open Is 2R required? Yes Weather: Calm Additional Info: | .
1328 |  | JE24045787 | 91 WAIMEA DRIVE,TE PUKE,TE PUKE | Eastern | TE MATAI RD | 2024-12-14 | 12:31 | 2024-12-14 | 12:48 | 0.00033218 | 1.9313e-05 | 7 | 120 | Unplanned | WILDLIFE - OTHER | Fuses Location: SF5-027 - L1 No. Fuses: 3 Fuse Amp Size: 16A TIME CLOSED: 12:48 Cause: Mouse Across Live Bus and Metal Box Weather (wind/rain): Fine Follow up required (select advisory)? NIL Full Power Restored | .
1329 |  | JE24045805 | BARRETT RD | Eastern | BARRETT RD | 2024-12-14 | 12:54 | 2024-12-14 | 13:01 | 3.7154e-05 | 5.5179e-06 | 2 | 13 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Removal Of Generators From Transformer TC3-119 & TC3-105 - Relived at 13:00 E00170 14/12/24 0800-1500 | .
1330 |  | JE24045806 | BARRETT RD | Eastern | BARRETT RD | 2024-12-14 | 12:53 | 2024-12-14 | 13:01 | 8.2769e-05 | 1.1036e-05 | 4 | 30 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Removal Of Generators From Transformer TC3-119 & TC3-105 - Relived at 13:00 E00170 14/12/24 0800-1500 | .
1331 |  | JE24045820 | 522 PAKARAKA ROAD,TAPAPA,TIRAU | Eastern | RANGITANUKU RD | 2024-12-14 | 16:22 | 2024-12-18 | 13:15 | 0.01699 | 1.3795e-05 | 5 | 6158 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Reclosure 9902/2 Protection flags (nil where none): Found Tripped not controlled via SCADA CAUSE: Unknown Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Fuses FC2128 & FC2105 Opened Tagged Line past Fuses FC2105 no longer in uses Line past Fuses FC2128 through forestry block, too be flown on Monday Recloser closed 18:48. Line Patrolled with a Helicopter nothing found, Relivened 18/12/24 @ 13:15 All OK 2R - Left open SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1332 |  | JE24045821 | 341 WHAKATOMOTOMO ROAD,PIRINOA,FEATHERSTON | Western | BURNSIDE | 2024-12-14 | 16:53 | 2024-12-15 | 0:37 | 0.0051195 | 1.1036e-05 | 4 | 1856 | Unplanned | VEGETATION - OUTSIDE ZONE | Found Tree Through lines at Pole 797633 Isolated at Fuses 8160 Tree Cleared, Transformer structure replaced and lines repaired | .
1333 |  | JE24037802 | 16 MANGATEPARU LOOP ROAD, MANGATEPARU, MORRINSVILLE, 3375 | Eastern | HORRELLS RD | 2024-12-13 | 9:15 | 2024-12-13 | 14:34 | 0.043141 | 0.00013519 | 49 | 15637 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Pole I13774: Replace existing pole with a 12.5m Busck Level 1: Install a Top mounted ENTEC Load Break Switch. Surge arrestors to be fitted on both sides of the switch Level 2: B2Â²/T2 Install 3 x swing links on the side towards pole I0114 Level 3: b3Â²/p2 Remove existing stay wire + screw anchor All 11kV current carrying leads are to be 95mmÂ² Cu PVC | .
1334 |  | JE24042297 | OTAMARAKAU | Eastern | OTAMARAKAU | 2024-12-13 | 9:16 | 2024-12-13 | 15:20 | 0.1187 | 0.00032556 | 118 | 43023 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace x-arms on pole 227408 & replace L.V poles 227415 & 227416 = Red defect - PTP 22 | .
1335 |  | JE24042388 | 188 HINUERA ROAD, MATAMATA, MATAMATA, 3472 | Eastern | FIRTH ST | 2024-12-13 | 14:30 | 2024-12-13 | 15:56 | 0.0076181 | 0.00055455 | 201 | 2761 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Disconnect Switch 14150 from O/H line on BRN 3 and BRN9. Remove 11kv arm & ABS 14150 using GB-30. At Pole 496071 install ENTEC Sectionaliser 14912 on South side in Open position. Install new fuse arm and links in open position. Connect ENTEC to bottom of links 14912/6 to OH line on North Side. (BRN3). | .
1336 |  | JE24042818 | WHAKAMARAMA | Eastern | WHAKAMARAMA | 2024-12-13 | 8:44 | 2024-12-13 | 12:58 | 0.047038 | 0.00018485 | 67 | 17049 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace HV arm on Pole 209945 | .
1337 |  | JE24042824 | 24 FARMER ROAD, WAITOA, WAITOA, 3310 | Eastern | TATUANUI | 2024-12-13 | 9:00 | 2024-12-13 | 14:14 | 0.039798 | 0.00012691 | 46 | 14425 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace TC5014 200kVA GMT | .
1338 |  | JE24042879 | 23 FAIRVIEW ROAD, KATIKATI, KATIKATI, 3129 | Eastern | MIDDLEBROOK | 2024-12-13 | 2:33 | 2024-12-13 | 5:08 | 0.062174 | 0.00040281 | 146 | 22535 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Linkbox maintenance at TB2-013 | .
1339 |  | JE24042891 | BARRETT RD | Eastern | BARRETT RD | 2024-12-13 | 8:52 | 2024-12-13 | 14:47 | 0.050012 | 0.00014071 | 51 | 18127 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace HV and LV arms on poles 209232, 209233, 209234, 209695 and 209690 and remove temporary ABS TEMP63 on Pole 493881 using GB-40 | .
1340 |  | JE24043117 | 162 REYNOLDS ROAD, RATANA, WANGANUI, 4581 | Western | TURAKINA | 2024-12-13 | 8:31 | 2024-12-13 | 14:24 | 0.017543 | 4.9661e-05 | 18 | 6359 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | HV reconductoring from and including pole 794703 to 794717.Remove TEMP ABS TEMP124(at pole 794710) | .
1341 |  | JE24043158 | 2111A KAHUTARA ROAD, PIRINOA, FEATHERSTON, 5772 | Western | KUMENGA | 2024-12-13 | 9:14 | 2024-12-13 | 14:38 | 0.065077 | 0.00020416 | 74 | 23587 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace ABS S588 with front mounted automated Entec switch S588/2 & Links/4 Note: New Entec & links installed & in service. SCADA commissioning still to be completed | .
1342 |  | JE24043195 | 242 DORSET ROAD, HILLSBOROUGH, NEW PLYMOUTH, 4372 | Western | KATERE 5 | 2024-12-13 | 8:45 | 2024-12-13 | 15:21 | 0.14339 | 0.00036694 | 133 | 51972 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Abs pole 181 with new Recloser 12739/2, bypass ABS 12739/1 and solid links 12739/6, 12739/4. Replace ABS 179 with new sectionaliser 12743/2 and solid links 12743/4 | .
1343 |  | JE24045462 | 292 UPPER KAHUI ROAD, RAHOTU, OPUNAKE, 4684 | Western | NGARIKI RD | 2024-12-13 | 9:30 | 2024-12-13 | 12:08 | 0.010857 | 6.8974e-05 | 25 | 3935 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT. Pole 711686, replace HV crossarm due to badly deteriorated. | .
1344 |  | JE24045641 | 598 4 ,UPOKONGARO,WANGANUI | Western | MAKIRIKIRI | 2024-12-13 | 2:43 | 2024-12-13 | 14:35 | 0.19779 | 0.00062628 | 145 | 71690 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 575 Protection flags (nil where none): A & B ph E/F CAUSE: Tree through lines Location: 784715 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: cursory Weather (wind/rain): LFI (Y/N + Comments): N Follow up Required (select advisory)? N Additional fault restoration comments: Line was isolated at ABS 1493 & Links 1013 so a temp line break was made at pole 784716, as will need tree contractors in to cut away the tree so lines can be repaired. Trees cut, lines repaired beyond Pole 784715. Then isolated again at ABS 1493 & Links 1013 so as to close temp line break. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1345 |  | JE24045692 | unknown HOMEWOOD ROAD,Homewood,Rural | Western | BLAIRLOGIE | 2024-12-13 | 11:03 | 2024-12-13 | 14:56 | 0.00064116 | 2.759e-06 | 1 | 232 | Unplanned | WILDLIFE - BIRD | Fuses Location: 8164 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 14:55 Cause: Bird Strike Weather (wind/rain):Calm - Follow up required (select advisory)?n | .
1346 |  | JE24045746 | 3 PALAZZO DRIVE,PAPAMOA BEACH,TAURANGA | Eastern | PALM SPRINGS | 2024-12-13 | 16:18 | 2024-12-17 | 11:42 | 0.13499 | 0.0012498 | 295 | 48929 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Fuses in Fuse/Sw S6167 found blown Isolated at TP735 11kV Cable Connection, Failed Transformer TP735 Generation connected to transformer TP735 at 20:15 13/12/24. Customer in 26 Santa Cruize Dr complaining of noise from Generation. 17/12/24 Generator removed 09:00Hrs from Transformer TP735 Cable break closed and Transformer TP735 replaced. Full power restored 11:41Hrs | .
1347 |  | JE24045759 | 201 WHANGAEHU BEACH RD,WHANGAEHU,WANGANUI | Western | FORDELL | 2024-12-13 | 18:39 | 2024-12-13 | 19:34 | 0.00015383 | 2.759e-06 | 1 | 56 | Unplanned | HUMAN ERROR - POTENTIAL WORKMANSHIP | Fuses Location: Fuses 4550 No. Fuses: 3 Fuse Amp Size: 8A and 1 x barrel TIME CLOSED: 1934 Cause: Fuses were 3A for a 100kVA Tfr so too small Weather (wind/rain): Fine Follow up required (select advisory)? | .
1348 |  | JE24045765 | 593 BIRD ROAD,PUKENGAHU,STRATFORD | Western | ORIGIN 2 | 2024-12-13 | 23:46 | 2024-12-14 | 1:12 | 0.00047631 | 5.5179e-06 | 2 | 173 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: CB 3 Protection flags (nil where none): B phase EF CAUSE: Unknown Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): fine LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: No fault found | .
1349 |  | JE24042643 | 13 KATTERNS STREET, KATIKATI, KATIKATI, 3129 | Eastern | TETLEY ROAD | 2024-12-12 | 23:26 | 2024-12-13 | 1:50 | 0.030726 | 0.00021244 | 77 | 11137 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Linkbox maintenance at TB2-126 | .
1350 |  | JE24042657 | 814 WHITE ROCK ROAD, RUAKOKOPUTUNA, MARTINBOROUGH, 5782 | Western | DYERVILLE | 2024-12-12 | 9:46 | 2024-12-12 | 12:39 | 0.011918 | 6.8974e-05 | 25 | 4320 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install and SCADA Test fuse saver 11414. Links 11414/4 were installed during a fault a few days ago so the outagearea was able to be reduced. Advised crew that it is better to contact planning when this happens so they can amend advertising rather than contacting control to change switching on the day of work. | .
1351 |  | JE24042723 | 255 OCEANBEACH ROAD, MOUNT MAUNGANUI, TAURANGA, 3116 | Eastern | GOLF RD | 2024-12-12 | 8:56 | 2024-12-12 | 12:35 | 0.032079 | 0.00014623 | 53 | 11627 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | AP: Pole 321209 Connect load side of ENTEC LBS Top Mount Sectionaliser 14897 to HV OH Line, leave in Open position LLP: Remove Temporary In-Line Links TEMP67 between poles 214499 & 214500 GB-T01, GB-T02, GB-34, GB-36, GB-40 12/12/2024 Links TEMP67 not removed due to Rain, Sectionaliser not put into Service | .
1352 |  | JE24042741 | 6 ANCHOR PLACE, TOKOROA, TOKOROA, 3420 | Eastern | CAMPBELL ST | 2024-12-12 | 9:16 | 2024-12-12 | 11:29 | 0.00073655 | 5.5179e-06 | 2 | 267 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To carry out oil repair works on TC776 and top up oil. | .
1353 |  | JE24042772 | 165 ANDREWS ROAD, OTWAY, TE AROHA, 3393 | Eastern | SPRINGDALE | 2024-12-12 | 9:30 | 2024-12-12 | 15:06 | 0.034288 | 0.00010208 | 37 | 12428 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace defect poles and arms at poles C1088, C1093, C1080, C1084 | .
1354 |  | JE24042775 | 654 3, KAI IWI, WANGANUI, 4574 | Western | WESTMERE PEAT ST | 2024-12-12 | 9:01 | 2024-12-12 | 13:07 | 0.0054215 | 2.2072e-05 | 8 | 1965 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Defected poles 782826, 782827 & 11KV X-arms on poles 782822 & 782823 | .
1355 |  | JE24042776 | LINDERMANN RD | Eastern | LINDERMANN RD | 2024-12-12 | 9:20 | 2024-12-12 | 14:44 | 0.059113 | 0.00018209 | 66 | 21426 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV/400V crossarms @ poles 204573, 204574, 204575, 204578, 204579 & 204581. | .
1356 |  | JE24042778 | 65 ALLEN ROAD, OHANGAI, HAWERA, 4672 | Western | WHAKAMARA | 2024-12-12 | 8:46 | 2024-12-12 | 14:02 | 0.041857 | 0.00013243 | 48 | 15171 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace ABS pole 729361 & DNO abs WH229. replace hv pin arm at pole 729300. install new 11kv fuses 12798 and replace hv xarms at pole 725984. no existing fuses for spur line. | .
1357 |  | JE24042780 | 147 MILLERS ROAD, KOPUARANGA, MASTERTON, 5882 | Western | OXFORD ST | 2024-12-12 | 9:16 | 2024-12-12 | 12:43 | 0.015442 | 7.4492e-05 | 27 | 5597 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Change 11KV arms & poles between S94 & S123 | .
1358 |  | JE24042785 | 946 BRISTOL ROAD, WAITUI, INGLEWOOD, 4388 | Western | BRISTOL RD | 2024-12-12 | 9:50 | 2024-12-12 | 14:10 | 0.0086113 | 3.3108e-05 | 12 | 3121 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Vegetation clearance in between poles 759771 - 759774 | .
1359 |  | JE24043240 | 562 COLVILLE ROAD, COROMANDEL, COROMANDEL, 3584 | Eastern | COLVILLE | 2024-12-12 | 9:15 | 2024-12-12 | 12:47 | 0.36188 | 0.0017078 | 619 | 131166 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace 11kV pole V0980. To cut trees at pole V2122. HV restore with LV links open at Transformer TC1241 LV permit to complete work Power restored 14:20 | .
1360 |  | JE24043297 | 424 MOTUKAWA ROAD, TARATA, INGLEWOOD, 4387 | Western | KOHETE RD | 2024-12-12 | 9:00 | 2024-12-12 | 15:31 | 0.015082 | 3.8625e-05 | 14 | 5467 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Upgrade existing 30kVa duel Tx at poles 760211,760214. Replace arms between poles 760205 and 760215 | .
1361 |  | JE24044715 | 1156 25, PIPIROA, THAMES, 3576 | Eastern | HAURAKI RD | 2024-12-12 | 10:01 | 2024-12-12 | 10:57 | 0.014386 | 0.00025658 | 93 | 5214 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace hv binder at pole O3616 due to red defect ptp | .
1362 |  | JE24045503 | 2009 STATE HIGHWAY 2,PUKEHINA,TE PUKE | Eastern | OTAMARAKAU | 2024-12-12 | 11:26 | 2024-12-12 | 12:56 | 0.0013741 | 1.9313e-05 | 7 | 498 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: S5947 No. Fuses: 2 Fuse Amp Size: Failed Isolated at Fuses S5947 Lightning Arresters cut away at Fuses S5948 Fuses S5948 Open for livening from Fuses S5947 12:30 Fuses S5948 Closed 12:55 Further repairs required at pole with Fuses S5948 FM to Defect Cable crutch Pole has no Number 2R - Required for switching | .
1363 |  | JE24045523 | 150 OPOUTERE ROAD,OPOUTERE,WHANGAMATA | Eastern | OPOUTERE | 2024-12-12 | 9:38 | 2024-12-12 | 16:05 | 0.15468 | 0.00040005 | 145 | 56064 | Unplanned | VEGETATION - OUTSIDE ZONE | Branch found contacting lines at Pole R13037 FM unable to brake branch Waiting for Tree Trimming company (3 hours away) Isolated at ABS 13403/1 & Links 13403/6 Control of Network handed over due to Comms issues 13:08 Control of Network returned 15:58 Confirmed branch Removed Power Restored 16:04 | .
1364 |  | JE24045544 | 81 EDGECUMBE ROAD,TAURANGA,TAURANGA | Eastern | 13TH AVE | 2024-12-12 | 11:51 | 2024-12-12 | 13:00 | 0.12333 | 0.0026348 | 955 | 44702 | Unplanned | THIRD PARTY INTERFERENCE - DIG IN | REGULATORY INFORMATION Voltage & Device ID: 11kV CB3 Protection flags (nil where none): B Ph O/C, E/F CAUSE: Cable Strike Location: 673 Camron Rd Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): 2412011 Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): N Follow up Required (select advisory)? Additional fault restoration comments: No Active LFI's Back Feed installed via Automated Sw/Gear SK5-084 up to Sw/Gear 9826/1 Damaged Cable Isolated between Sw/Gears 9767/1 & S4710 FM to supply NDR SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1365 |  | JE24045550 | 170 RAMA ROAD,KAUPOKONUI,HAWERA | Western | AUROA | 2024-12-12 | 13:26 | 2024-12-12 | 16:11 | 0.0022778 | 1.3795e-05 | 5 | 826 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | ETA fire FM onsite now 13:05 This was not at Transformer M1300 it was at transformer 5608E Isolated at Fuses 8977 Replaced Pole after being hit By Tanker Did not Make another Job When Fuses were opened in E Map | .
1366 |  | JE24045603 | unknown PAHAUTEA ROAD,Kahutara,Rural | Western | DAIRY FACTORY | 2024-12-12 | 17:11 | 2024-12-12 | 22:03 | 0.039751 | 0.00048006 | 88 | 14408 | Unplanned | THIRD PARTY INTERFERENCE - OVERHEAD CONTACT | REGULATORY INFORMATION Voltage & Device ID: 11kV Lines Pulled down @ Pole 812985 Protection flags (nil where none): A,B,C Fault CAUSE: Digger Pulled Lines Down @ Pole 812985 Location: Pole 812985 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Fine LFI (Y/N + Comments): Nil Follow up Required (select advisory)? Additional fault restoration comments: 11kV Lines Pulled down @ Pole 812985 by Digger Ben Johnson has Details. NDR TLB @ pole 812983 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1367 |  | JE24045607 | 640B MORRINSVILLE-WALTON ROAD,MORRINSVILLE,MORRINSVILLE | Eastern | KIWITAHI | 2024-12-12 | 17:14 | 2024-12-13 | 2:04 | 0.20439 | 0.00097667 | 238 | 74083 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV Pole I1457 Car V Pole , Pole I1461 & I1462 Failed 7/16Cu Wires with Fault Current Protection flags (nil where none): CAUSE: Pole I1457 Car V Pole , Pole I1461 & I1462 Failed 7/16Cu Wires with Fault Current , 2 x Worksites Location: Pole I1457 Car V Pole , Pole I1461 & I1462 Failed 7/16Cu Wires with Fault Current Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Curse Weather (wind/rain): Windy LFI (Y/N + Comments): Nil Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1368 |  | JE24045608 | unknown LOWER WAIAU ROAD,Waverley,Waverley | Western | WAITOTARA | 2024-12-12 | 15:13 | 2024-12-12 | 17:33 | 0.012344 | 8.8287e-05 | 32 | 4474 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 2719 No. Fuses: 2 Fuse Amp Size: 30A TIME CLOSED: 1732 Cause: Unknown Weather (wind/rain): Calm, raining Follow up required (select advisory)? | .
1369 |  | JE24045623 | 50 ELEVENTH AVENUE,TAURANGA,TAURANGA | Eastern | 10TH AVE | 2024-12-12 | 19:29 | 2024-12-12 | 22:45 | 0.38206 | 0.003686 | 1137 | 138479 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Cable Failed @ Sw/G SK5-034 to Sw/G SK5-153 Protection flags (nil where none): CB 1 Flags A,C, E/F Ground O/C. GMCB 13471 Flags A,B, Fault, E/F CAUSE: : 11kV Cable Failed @ Sw/G SK5-034 to Sw/G SK5-153 Location: : 11kV Cable Failed @ Sw/G SK5-034 to Sw/G SK5-153 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): 2412012 Circuit patrolled and type: Cable Fault Sectioning procedure used, Plus Long & Crawford Sw/Gear along 11th Av, SK5-040, SK5-034, sites CB 1 opened to allow switching Safely. Rather than 10Min wait time procedure. Weather (wind/rain): Fine LFI (Y/N + Comments): Nil Operations Follow up Required (select advisory)? Protection for GMCB 13471 Additional fault restoration comments: GMCB 13471/1 Protection Operated Flags A,B, Fault, E/F ????" DNO number: : 2412012. | .
1370 |  | JE24045632 | 8 NEWTON STREET, MOUNT MAUNGANUI, TAURANGA, 3116 | Eastern | NEWTON ST | 2024-12-12 | 23:31 | 2024-12-13 | 1:57 | 0.023796 | 0.00016278 | 59 | 8625 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | . | .
1371 |  | JE24042069 | LINTON | Western | LINTON | 2024-12-11 | 9:00 | 2024-12-11 | 12:48 | 0.025763 | 0.00011312 | 41 | 9338 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re-sag conductors between poles P02904 to P28339, re-sag conductors between poles P03699 to P02923, straighten poles and re-sag conductors between poles P03695 to P27107, re-sag conductors between poles P03668 to P00320 | .
1372 |  | JE24042566 | 541 WHAKAMARA ROAD, MANUTAHI, HAWERA, 4672 | Western | WHAKAMARA | 2024-12-11 | 8:45 | 2024-12-11 | 15:11 | 0.032316 | 0.00035315 | 77 | 11713 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | create line break at pole 729548. replace pole 729676 and DNO ABS WH293. remove line break from pole 729548. | .
1373 |  | JE24042620 | 243 WAIHI ROAD, JUDEA, TAURANGA, 3110 | Eastern | WAIHI RD | 2024-12-11 | 23:31 | 2024-12-12 | 2:01 | 0.026121 | 0.00017381 | 63 | 9468 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9448/1/2/3 | .
1374 |  | JE24042622 | 58 OTARAOA ROAD, MOTUNUI, WAITARA, 4383 | Western | TIKORANGI | 2024-12-11 | 9:41 | 2024-12-11 | 11:30 | 0.010554 | 9.6564e-05 | 35 | 3826 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace defective 33kV xarm & insulators at pole 764110 | .
1375 |  | JE24042625 | 721 KAUKATEA VALLEY ROAD, OKOIA, WANGANUI, 4582 | Western | NO 3 LINE | 2024-12-11 | 8:44 | 2024-12-11 | 11:24 | 0.01811 | 0.00011312 | 41 | 6564 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Vegetation cutting between poles 792070 to 792071 | .
1376 |  | JE24042633 | 1233 OPAKI KAIPARORO ROAD, MAURICEVILLE, MASTERTON, 5882 | Western | MAURICEVILLE | 2024-12-11 | 9:36 | 2024-12-11 | 10:13 | 0.00051317 | 1.3795e-05 | 5 | 186 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To upgrade Transformer earths at T8/141 | .
1377 |  | JE24042639 | LINDERMANN RD | Eastern | LINDERMANN RD | 2024-12-11 | 9:31 | 2024-12-11 | 14:31 | 0.1144 | 0.00038074 | 138 | 41464 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv/400vt cross arms @ poles 204478,204479,204480 ,204482 ,204483 & 204484 Replace 11kv pole 204481. Isolation points @ ABS 14274 and SB1-079. | .
1378 |  | JE24042645 | 113 TE KOUMA ROAD, TE KOUMA, COROMANDEL, 3581 | Eastern | MANAIA COROMANDEL | 2024-12-11 | 9:54 | 2024-12-11 | 15:07 | 0.11565 | 0.0003697 | 134 | 41917 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV Pole V1149 as part of the Manaia FFT Project | .
1379 |  | JE24042649 | 11 AIRPORT ROAD, WHANGANUI AIRPORT, WANGANUI, 4501 | Western | MARANGAI | 2024-12-11 | 9:15 | 2024-12-11 | 14:41 | 0.038618 | 0.00011864 | 43 | 13997 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles & x-arms between 774073 - 774048 & 774061 | .
1380 |  | JE24042725 | 54 WHAREPOA ROAD, HIKUTAIA, PAEROA, 3674 | Eastern | BENNETT ST | 2024-12-11 | 9:02 | 2024-12-11 | 15:32 | 0.073323 | 0.00018761 | 68 | 26576 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV crossarms beyond sectionaliser 14787 | .
1381 |  | JE24042763 | 39 RATANA ROAD, RATANA, WANGANUI, 4581 | Western | TURAKINA | 2024-12-11 | 8:33 | 2024-12-11 | 13:35 | 0.011644 | 3.8625e-05 | 14 | 4220 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | HV reconductoring from and including pole 794742 to 794734 | .
1382 |  | JE24043263 | 172 BULLTOWN ROAD, WAIHI, WAIHI, 3610 | Eastern | WAIHI NORTH | 2024-12-11 | 9:16 | 2024-12-11 | 12:43 | 0.0034264 | 1.6554e-05 | 6 | 1242 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Tree trimming between poles P1111 - P12696 | .
1383 |  | JE24045088 | 159 BREAKWATER ROAD, MOTUROA, NEW PLYMOUTH, 4310 | Western | CENTENNIAL DR | 2024-12-11 | 15:31 | 2024-12-11 | 18:01 | 0.0016554 | 1.1036e-05 | 4 | 600 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace damaged pole 748780. pole damaged by vehicle. Required urgent replacement. Booking outage due to pole on private land (Port Taranaki). | .
1384 |  | JE24045369 | 6 LINCOLN STREET,MORRINSVILLE,MORRINSVILLE | Eastern | ALEXANDRA AVE | 2024-12-11 | 10:27 | 2024-12-11 | 14:25 | 0.060013 | 0.00027314 | 99 | 21752 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Fuse/Sw 9596/2 Cable Failed Protection flags (nil where none): CAUSE: Failed Cable from Fuse/sw 9596/2 Location: Temp generation (state details when used): Gen Installed @ TC5307 @ 13:35, Gen Set @ TC4675 installed 14:25 PERFORMANCE DETAIL DNO (number or state No): 2412010 Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1385 |  | JE24045383 | 1579B STATE HIGHWAY 53,MARTINBOROUGH,MARTINBOROUGH | Western | TAWAHA | 2024-12-11 | 16:31 | 2024-12-11 | 19:41 | 0.0015739 | 8.2769e-06 | 3 | 570 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: Transformer T2331 Fuses CAUSE: Broken LV Bushings at the transformer Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): N/A Circuit patrolled & type: Cursory Weather (wind/rain): calm Follow up required (select advisory)?No Additional fault restoration comments: Transformer replaced, power restored 19:40 | .
1386 |  | JE24045409 | 523D OTUMOETAI ROAD,OTUMOETAI,TAURANGA | Eastern | BEACH RD MATUA | 2024-12-11 | 11:21 | 2024-12-12 | 12:30 | 0.066628 | 4.4143e-05 | 16 | 24150 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Cable Failed from Fuse/Switch SC4-609 Protection flags (nil where none): CAUSE: Failed Cable Location: SC4-609 Temp generation (state details when used): Installed DTX TC4-330 @ 12:30 PERFORMANCE DETAIL DNO (number or state No): 2412009 Circuit patrolled and type: cursory Weather (wind/rain): fine LFI (Y/N + Comments): n/a Follow up Required (select advisory)? no Additional fault restoration comments: Update from Alvin 12/12/24 - Generator installed - work handed over to EIS to complete because Downer do not have resources, approx. 1 week worth of work, EIS will also restore network and remove generator. DNO 2412009, being managed by Michael Vickers, info provided by NOC Performance. | .
1387 |  | JE24045413 | 841B MT CURL ROAD, MARTON, 4788 | Western | MARTON | 2024-12-11 | 13:13 | 2024-12-11 | 14:29 | 0.0042056 | 5.5179e-05 | 20 | 1524 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | broken 11kv crossarm being repaired under 2R now Replaced 1 X crossarm at Pole 804516 Isolated at Fuses 744 | .
1388 |  | JE24045436 | unknown DAGGER ROAD,Kerepehi,Rural | Eastern | PATETONGA | 2024-12-11 | 9:36 | 2024-12-11 | 12:31 | 0.0024018 | 1.3795e-05 | 5 | 871 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: FC762 No. Fuses: 2 Fuse Amp Size: 25A TIME CLOSED: 1230 Cause: Possible bird strike Weather (wind/rain): fine Follow up required (select advisory)? yes 2 x trip in 2 days Restored | .
1389 |  | JE24045476 | 2148 SOLDIERS SETTLEMENT ROAD, FEATHERSTON | Western | SOUTH FEATHERSTON | 2024-12-11 | 21:30 | 2024-12-11 | 22:06 | 0.0046111 | 0.00012691 | 46 | 1671 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: CB C912 Protection flags (nil where none): None CAUSE: Deterioration Location: Pole 812408 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): None Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): None Follow up Required (select advisory)? No Additional fault restoration comments: Skewed cross arm at pole 812408. Isolated at ABS S566 and restrapped cross arm into place, bolted bracings SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1390 |  | JE24045481 | 3 CLOTEN ROAD,STRATFORD,STRATFORD | Western | CLOTON RD INDUSTRIAL | 2024-12-11 | 20:12 | 2024-12-12 | 0:24 | 0.085354 | 0.00094081 | 341 | 30937 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 8 Protection flags (nil where none): B & C ph O/C & E/F CAUSE: Bird Strike Location: 734393 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: N Weather (wind/rain): calm LFI (Y/N + Comments): N Follow up Required (select advisory)? N Additional fault restoration comments: Customer reported a big black bird hit the line - suspect a swan, line was isolated at ABS's 5828 & 5855. Faultman also replaced 1 x 20 amp hv fuses at transformer 2062T at 00:24. | .
1391 |  | JE24045490 | 33 HUGHES LINE,CLAREVILLE,CARTERTON | Western | CHESTER RD | 2024-12-11 | 22:03 | 2024-12-11 | 23:40 | 0.0013359 | 1.3795e-05 | 5 | 484 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 7655 No. Fuses: 2 Fuse Amp Size: 8A TIME CLOSED: 23:40 Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)?No | .
1392 |  | JE24045493 | unknown LOWER WAIAU ROAD,Waverley,Waverley | Western | WAITOTARA | 2024-12-11 | 22:36 | 2024-12-12 | 0:03 | 0.007643 | 8.8287e-05 | 32 | 2770 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 2719 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 00:02 Cause: unknown Weather (wind/rain): calm Follow up required (select advisory)?N | .
1393 |  | JE24042346 | 10 KOHETE ROAD, KAIMATA, INGLEWOOD, 4390 | Western | KOHETE RD | 2024-12-10 | 9:01 | 2024-12-10 | 18:01 | 0.092422 | 0.00017106 | 62 | 33499 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace arms @ pole 760044,843201,760119,760120,760121,760122,760164. Install temp ABS 146 and permanent ABS 12784 Close out NAPA 116264 aswell, this was advertised under this NAPA also Northpower had unforeseen issue with Network hardware, this has caused an over run of outage, Please explain from northpower required | .
1394 |  | JE24042350 | 909 RIMU ROAD, PONGAROA, PAHIATUA, 4989 | Western | TIRAUMEA | 2024-12-10 | 8:49 | 2024-12-10 | 15:41 | 0.0056848 | 1.3795e-05 | 5 | 2061 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Isolation for vegetation - Tree felling between 11kV poles: P27553 and P27267 | .
1395 |  | JE24042429 | 81 CLIFTON GROVE ROAD, ADMIRAL HILL, MASTERTON, 5883 | Western | LONGBUSH | 2024-12-10 | 9:01 | 2024-12-10 | 13:56 | 0.039939 | 0.00013519 | 49 | 14476 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles and hardware past S333 | .
1396 |  | JE24042448 | 223 REID LINE EAST, AORANGI, FEILDING, 4775 | Western | BUNNYTHORPE | 2024-12-10 | 9:30 | 2024-12-10 | 14:39 | 0.079973 | 0.00025934 | 94 | 28986 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace xarms on various locations beyond ABS E5 | .
1397 |  | JE24042459 | 1351 OPAKI KAIPARORO ROAD, MAURICEVILLE, MASTERTON, 5882 | Western | MAURICEVILLE | 2024-12-10 | 9:46 | 2024-12-10 | 12:11 | 0.022104 | 0.00015174 | 55 | 8012 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To install 11kv pole to get ground clearance . Between poles P45495 & P45497. | .
1398 |  | JE24042472 | TATUANUI | Eastern | TATUANUI | 2024-12-10 | 9:30 | 2024-12-10 | 13:55 | 0.023364 | 8.8287e-05 | 32 | 8468 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV xarms, hardware & fusing on poles K0249, K0257, K13510, K13502 & K0239. | .
1399 |  | JE24042562 | 82 REYNOLDS ROAD, RATANA, WANGANUI, 4581 | Western | TURAKINA | 2024-12-10 | 8:30 | 2024-12-10 | 12:31 | 0.0086199 | 3.5867e-05 | 13 | 3124 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | HV reconductoring from and including pole 794693 to 794703. | .
1400 |  | JE24042588 | 2221 TAIRUA WHITIANGA ROAD, KAIMARAMA, WHITIANGA, 3591 | Eastern | COROGLEN | 2024-12-10 | 9:46 | 2024-12-10 | 15:41 | 0.049895 | 0.00014071 | 51 | 18085 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace crossarms and hardware at various sites and resag OH lines between TX TC1504 & TP3864 | .
1401 |  | JE24045102 | 881 MAKAKAHI ROAD, MAKAKAHI, RAETIHI, 4696 | Western | RAETIHI | 2024-12-10 | 9:32 | 2024-12-10 | 13:29 | 0.017049 | 7.1733e-05 | 26 | 6179 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 6.6KV X-arms on pole 775490 raised by Helicopter Pole Top Topography | .
1402 |  | JE24045140 | 1236 RANGITIKEI LINE,NEWBURY,PALMERSTON NORTH | Western | TE ARAKURA | 2024-12-10 | 5:12 | 2024-12-10 | 7:41 | 0.00082062 | 5.5179e-06 | 2 | 297 | Unplanned | WILDLIFE - BIRD | Fuses Location: D88 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 0740 Cause: birds Weather (wind/rain): Good Follow up required (select advisory)? NO Restored | .
1403 |  | JE24045159 | unknown WHITE ROCK ROAD,Tuturumuri,Rural | Western | TUTURUMURI | 2024-12-10 | 12:30 | 2024-12-10 | 13:50 | 0.0011068 | 1.3795e-05 | 5 | 401 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faultman found a floating conductor on pole 371722 due to broken binder. Line was isolated at Fuses 7317 to rebind in conductor. | .
1404 |  | JE24045211 | unknown DAGGER ROAD,Kerepehi,Rural | Eastern | KAIHERE | 2024-12-10 | 10:51 | 2024-12-10 | 13:09 | 0.0019028 | 1.3795e-05 | 5 | 690 | Unplanned | WILDLIFE - BIRD | Fuses Location: FC762 No. Fuses: 2 Fuse Amp Size: 25A TIME CLOSED: 1309 Cause: Bird Weather (wind/rain): fine Follow up required (select advisory)? Restored , 2 r because of time | .
1405 |  | JE24045226 | 810 ,, | Western | LINTON | 2024-12-10 | 11:57 | 2024-12-10 | 18:13 | 0.094708 | 0.00070905 | 257 | 34327 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Called SMC for ETA Fire comms 2nd call for an eta - Urgent - ETA 10 minutes- fire comms notified. REGULATORY INFORMATION Voltage & Device ID: 11kV REC H131 Protection flags (nil where none): A, B, C ph O/C & E/F CAUSE: Car vs Pole Location: P03466 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: N Weather (wind/rain): windy LFI (Y/N + Comments): N Follow up Required (select advisory)? Additional fault restoration comments: Lines were isolated at ABS's H127 & H129 to replace pole hit by car and repair HV to LV line contact to customer. Only one customer was left of but they had solar / Batteries so weren't overly bothered . 928 Tennant Drive - Added to safety Tag register and emailed retailer 3 properties are live to the main switch but isolated have internal damage FM has Advised them off the path to reconnection 12 . Properties were inspected overall | .
1406 |  | JE24045348 | unknown SH 1 ,Hunterville,Rural | Western | HUNTERVILLE 22KV | 2024-12-10 | 21:40 | 2024-12-10 | 23:27 | 0.0064725 | 6.0697e-05 | 22 | 2346 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: 285 No. Fuses: 2 Fuse Amp Size: 8 TIME CLOSED: 23:27 Cause: unknown Weather (wind/rain): calm Follow up required (select advisory)?n Line patrolled | .
1407 |  | JE24041867 | 583 WAIHI BEACH ROAD, WAIHI BEACH, WAIHI, 3681 | Eastern | BEACH RD WAIHI BEACH | 2024-12-09 | 23:03 | 2024-12-10 | 13:36 | 0.052488 | 0.005002 | 1774 | 19024 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 33kV Crossarms between poles P13650 to CREWBH065 Waihi Beach Rd | .
1408 |  | JE24041905 | 120 LOVEGROVE ROAD, TE AROHA, TE AROHA, 3393 | Eastern | LOVEGROVE RD | 2024-12-09 | 9:00 | 2024-12-09 | 14:45 | 0.029464 | 8.5528e-05 | 31 | 10680 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Poles and hardware at 878344, C350, C351, C352. Replace Pole and hardware at Pole C13161 and transformer TC682. Run new Lv conductor between Poles 878344 and C352. | .
1409 |  | JE24042057 | 532 INAHA ROAD, OKAIAWA, HAWERA, 4678 | Western | OKAIAWA | 2024-12-09 | 9:30 | 2024-12-09 | 15:29 | 0.011878 | 3.3108e-05 | 12 | 4305 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 33kV pin arm at poles 720156, 720169 & 720180 and straighten & block poles 720171, 720170 & 720161. | .
1410 |  | JE24042064 | 125 RATANA ROAD, RATANA, WANGANUI, 4581 | Western | TURAKINA | 2024-12-09 | 8:36 | 2024-12-09 | 13:28 | 0.010471 | 3.5867e-05 | 13 | 3795 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | HV reconductoring from and including pole 794759 to 794742 | .
1411 |  | JE24042065 | BAINESSE | Western | BAINESSE | 2024-12-09 | 9:15 | 2024-12-09 | 14:29 | 0.062262 | 0.00019865 | 72 | 22567 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re-sag conductors between P03492 - P03494, Replace binders at P03470, Replace span conductor P03447 - P03467, Replace binder at P03440, Replace arms at P03427 and re-sag conductor between P03427 - P03428 | .
1412 |  | JE24042296 | 16 JANS TERRACE, OAKURA, OAKURA, 4314 | Western | OAKURA | 2024-12-09 | 8:53 | 2024-12-09 | 12:08 | 0.022609 | 0.00011588 | 42 | 8195 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Isolate TX 1837N at RMU 12767/2 to replace LV distribution Rack in TX. | .
1413 |  | JE24042312 | 111 MAIN ROAD, TOKOROA, TOKOROA, 3491 | Eastern | ASHWORTH ST | 2024-12-09 | 23:00 | 2024-12-10 | 3:07 | 0.0034016 | 3.3108e-05 | 12 | 1233 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To carry out oil leak repair and top up oil on TC3215 and clean up transformer TC3473 | .
1414 |  | JE24042323 | 25 CHARTWELL DRIVE, TOKOROA, TOKOROA, 3420 | Eastern | CAMPBELL ST | 2024-12-09 | 9:17 | 2024-12-09 | 10:40 | 0.010029 | 0.00012139 | 44 | 3635 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To carry out oil leak repair on TC3357 and clean up transformer | .
1415 |  | JE24042331 | 45 LION DRIVE, TOKOROA, TOKOROA, 3491 | Eastern | CAMPBELL ST | 2024-12-09 | 12:30 | 2024-12-09 | 13:06 | 0.00069107 | 1.9313e-05 | 7 | 250 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To carry out oil repair works on TC5619 and clean up transformer. | .
1416 |  | JE24044929 | unknown PAHIATUA PONGAROA ROAD,Pahiatua,Pahiatua | Western | COONOOR | 2024-12-09 | 1:47 | 2024-12-09 | 3:45 | 0.0287 | 0.00029245 | 106 | 10402 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV, Rec T42 Protection flags (nil where none): O/C, B-C phase CAUSE: multiple sites with tree & line problems Location: P46478 & P46484 & P46489 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: Operational Weather (wind/rain): Windy LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: FM has sectionalized and restored power. Section of line between T38 & V19 left isolated. Crew will need to return in daylight to patrol from T42 to the end of feeder. Feeder was patrolled at day light and the following problems were found. Faultman found multiple faults. Fault 1: At pole P46478 lines are low and swinging into trees. Fault 2: At pole P46484 & P46483 trees touching lines Fault 3: At pole P46489 the line gap between the single & 3 phase take off are to close less than a 100mm a part. Phil Barnes is going to put in a short notice NAPA application to have these problems sorted out. | .
1417 |  | JE24044935 | unknown WAIHI VALLEY ROAD,Pongaroa,Rural | Western | HOROEKA | 2024-12-09 | 5:28 | 2024-12-09 | 10:56 | 0.061522 | 0.00018761 | 68 | 22299 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC V5 Protection flags (nil where none): C ph O/C & E/F CAUSE: Deuteriation Location: P31368 & P00747 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: Cursory Weather (wind/rain): wind & rain LFI (Y/N + Comments): N Follow up Required (select advisory)? N Additional fault restoration comments: Faultman found lines had come down at pole P31368 and the fault currents brought down lines down at pole P00747.Faultman to talk with PM to have line re-conducted as is in very poor state. | .
1418 |  | JE24044940 | 10 KAHAROA ROAD,PATEA,PATEA | Western | OTAUTU | 2024-12-09 | 5:59 | 2024-12-09 | 8:58 | 0.0084004 | 4.6902e-05 | 17 | 3045 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses LI107 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 0858 Cause: Unknown Weather (wind/rain): Wind / Rain Follow up required (select advisory)? | .
1419 |  | JE24044946 | 47 KOPIKOPIKO ROAD,PAHIATUA,PAHIATUA | Western | MANGAMAIRE | 2024-12-09 | 6:20 | 2024-12-09 | 12:30 | 0.032705 | 8.8287e-05 | 32 | 11854 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: Fuses R54 No. Fuses: 2 Fuse Amp Size: 12A TIME CLOSED: 1230 Cause: Weather Weather (wind/rain): Wind / Rain Follow up required (select advisory)? | .
1420 |  | JE24044948 | 220 MORETON ROAD,PARKVALE,CARTERTON | Western | PARK RD | 2024-12-09 | 6:22 | 2024-12-09 | 8:56 | 0.0051101 | 3.3108e-05 | 12 | 1852 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: Fuses 7614 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 0855 Cause: Wind Weather (wind/rain): Wind Follow up required (select advisory)? + Replaced 1x Barrell under 2R | .
1421 |  | JE24044974 | 263 TE MATAI ROAD,WHAKARONGO,PALMERSTON NORTH | Western | ROBERTS LINE | 2024-12-09 | 8:13 | 2024-12-09 | 12:44 | 0.00074921 | 2.759e-06 | 1 | 272 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: Fuses E90 No. Fuses: 2x Fuse Amp Size: 20A TIME CLOSED: 12:44 Cause: Suspect Line Clash by wind - Long river crossing Weather (wind/rain): Wind / Rain Follow up required (select advisory)? Full Power Restored | .
1422 |  | JE24045016 | 519 TIRIRAUKAWA ROAD,TAIHAPE,TAIHAPE | Western | MATAROA A | 2024-12-09 | 5:52 | 2024-12-09 | 9:30 | 0.0042182 | 1.9313e-05 | 7 | 1529 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: 914 No. Fuses: 2 Fuse Amp Size: 6a TIME CLOSED: 09:30 Cause: unknown windy last night Weather (wind/rain): windily little rain Follow up required (select advisory)? NA | .
1423 |  | JE24045019 | 216 WEST ROAD,MAURICEVILLE,MASTERTON | Western | MAURICEVILLE | 2024-12-09 | 9:50 | 2024-12-09 | 14:06 | 0.0070708 | 2.759e-05 | 10 | 2563 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: Fuses U35 No. Fuses: 2x Fuse Amp Size: 6A TIME CLOSED: 14:05 Cause: Wind - suspect line clash Weather (wind/rain): Windy Follow up required (select advisory)? Unsure if it was windy enough last night to use the ''Adverse Weather' Close out code, so went with line clash | .
1424 |  | JE24045029 | 996 ARARATA ROAD,ARARATA,HAWERA | Western | TAWHITI RD | 2024-12-09 | 10:09 | 2024-12-09 | 11:48 | 0.0013578 | 1.3795e-05 | 5 | 492 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses CA465 No. Fuses: 3 Fuse Amp Size: 8A TIME CLOSED: 11:47 Cause: Unknown - Dylan noted that there is tree felling near lines in the area, suspects this may be something to do with he recent trippings in the area, but cannot confirm or prove it. Weather (wind/rain): Rain Last night Follow up required (select advisory)? 2R used for the Line Patrol | .
1425 |  | JE24045042 | 158 KELVIN GROVE ROAD,KELVIN GROVE,PALMERSTON NORTH | Western | POHANGINA | 2024-12-09 | 11:00 | 2024-12-09 | 11:03 | 0.0093296 | 0.0035149 | 1274 | 3382 | Unplanned | HUMAN ERROR - POTENTIAL WORKMANSHIP | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 8 Protection flags (nil where none): B & C ph fault CAUSE: Branch got caught in wind while been cut by trainee and fell on lines. Location: pole 470718 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: N Weather (wind/rain): Wind LFI (Y/N + Comments): N Follow up Required (select advisory)? Y - safety manager Additional fault restoration comments: After tripping confirmed with tree contractor all personal safe and no body injured, safety measures were re-applied for work to proceed. Tree contractor called back to advise work will be stopped as crew a bite shaken and after consulting with their boss work was stopped and cancelled. CAC 117652-01 was then cancelled and safety measures restored back to normal. | .
1426 |  | JE24045050 | 2803 STATE HIGHWAY 4,MANGAMAHU,WANGANUI | Western | MAKIRIKIRI | 2024-12-09 | 11:20 | 2024-12-09 | 12:20 | 0.0013147 | 2.2072e-05 | 8 | 477 | Unplanned | VEGETATION - INSIDE ZONE | Faultman found tree on lines past Fuses 882 while issuing a CAC permit. Line was isolated at Fuses 882 to remove tree from lines at pole 783377. | .
1427 |  | JE24045057 | 582 BLUFF RANGITUMAU ROAD,RANGITUMAU,MASTERTON | Western | OXFORD ST | 2024-12-09 | 13:41 | 2024-12-09 | 15:31 | 0.00091073 | 8.2769e-06 | 3 | 330 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faultman found line down due to joint failure at pole 446323, line was isolated at Fuses 7480 to repair the line. | .
1428 |  | JE24045095 | 101 MAXWELL STATION ROAD,MAXWELL,WANGANUI | Western | WESTMERE PEAT ST | 2024-12-09 | 6:05 | 2024-12-09 | 14:01 | 0.010489 | 2.2072e-05 | 8 | 3802 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: 2712 No. Fuses: 2 Fuse Amp Size: 8a TIME CLOSED: 14:00 Cause: weather Weather (wind/rain): windy Follow up required (select advisory)?NA full power restored | .
1429 |  | JE24045100 | 966 MOREA ROAD,ARARATA,HAWERA | Western | TAWHITI RD | 2024-12-09 | 18:00 | 2024-12-09 | 19:06 | 0.00036299 | 5.5179e-06 | 2 | 132 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Broken Jumper at Pole 724906 due to old age, EPO joint had burnt out Isolated at Fuses CA443 Replaced EPO joint and Jumper, Full power restored | .
1430 |  | JE24045111 | 101 MAXWELL STATION ROAD,MAXWELL,WANGANUI | Western | WESTMERE PEAT ST | 2024-12-09 | 17:15 | 2024-12-09 | 20:01 | 0.0036595 | 2.2072e-05 | 8 | 1326 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faultman found rotten cross arm and damaged insulator on pole 773902. Line was isolated at Fuses 2712 replaced cross arm & hardware, Full power restored | .
1431 |  | JE24045124 | 527 MILLIKEN ROAD,MORRINSVILLE,MORRINSVILLE | Eastern | KEREONE | 2024-12-09 | 18:03 | 2024-12-09 | 22:49 | 0.071159 | 0.00092701 | 163 | 25792 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC RC35 Protection flags (nil where none): B PH - OC EF CAUSE: Cracked Insulator Location: Pole I2066 Circuit patrolled and type: Cursory Patrol Weather (wind/rain): Fine LFI (Y/N + Comments): SAP 13587189 - B PH OC Follow up Required (select advisory)? NIL Additional fault restoration comments: - Sectionalized and Fault Found | .
1432 |  | JE24045433 | pole_P12059 | Western | APITI | 2024-12-09 | 13:01 | 2024-12-09 | 14:21 | 0.0048305 | 6.0697e-05 | 22 | 1751 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | PTP Red Defect JE24044241 - Replace Binders at pole P12059 | .
1433 |  | JE24045434 | pole_P14356 | Western | POHANGINA | 2024-12-09 | 9:01 | 2024-12-09 | 10:41 | 0.029162 | 0.00028969 | 105 | 10570 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | PTP Red Defect 24 hours - Je24044205 - Replace Corssarms at pole P14356 | .
1434 |  | JE24042293 | BREAKWATER RD | Western | BREAKWATER RD | 2024-12-08 | 8:30 | 2024-12-08 | 10:05 | 0.031174 | 0.00032832 | 119 | 11299 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove 11kV Links 6250. Cut and cap 11kV cable below ground. Isolate and earth 974/4 | .
1435 |  | JE24042501 | 60 MARSHALL ROAD, KATIKATI, KATIKATI, 3178 | Eastern | WHARAWHARA ROAD | 2024-12-08 | 23:09 | 2024-12-09 | 0:47 | 0.021111 | 0.0002152 | 78 | 7652 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Test 33KV cable screens Job not fully completed due to Aon CB 32 not closing remotely or onsite. | .
1436 |  | JE24044435 | 94 LAKE DOMAIN ROAD, LAKE RESERVE, FEATHERSTON, 5771 | Western | SOUTH FEATHERSTON | 2024-12-08 | 15:30 | 2024-12-08 | 16:01 | 0.0039533 | 0.00012691 | 46 | 1433 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Repair broken 11kv binder at pole 812435 | .
1437 |  | JE24044854 | 63A KAYELENE PLACE,OMOKOROA,TAURANGA | Eastern | BARRETT RD | 2024-12-08 | 8:20 | 2024-12-08 | 11:41 | 0.0044477 | 7.7251e-05 | 28 | 1612 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: fans SC3-0123 Protection flags (nil where none): nil CAUSE: cable fault Location: Between Sw/Gear 9330/3 and Link Box TC3-105 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): 2412006 Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): Follow up Required (select advisory)? No Additional fault restoration comments: Isolated at Sw/Gear 9330/3 and cable breaks at TC3-105 and TC3-119 Generator connected at Transformer TC3-105 at 11:35 Generator connected at Transformer TC3-119 at 11:40 . | .
1438 |  | JE24044856 | 114 OXFORD STREET,LANSDOWNE,MASTERTON | Western | TOTARA ST | 2024-12-08 | 7:43 | 2024-12-08 | 8:55 | 0.039744 | 0.0013519 | 490 | 14405 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | REGULATORY INFORMATION Voltage & Device ID: C817 Protection flags (nil where none): Nil CAUSE: Jumper failure Location: Pole 825386 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): None Follow up Required (select advisory)? No Additional fault restoration comments: Isolated pole 825386and repaired jumer under Access Permit. Break Before Make Switching. , opened Switchgear 11083/3 and Switchgear 11467/3 to avoid earth fault trip on Mobile Sub CB CB 1132 and TOO C821 on earth (phase imbalance). Jumper repaired Full power restored. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1439 |  | JE24044875 | 76 BRANDON HALL ROAD,BULLS,BULLS | Western | PAREWANUI | 2024-12-08 | 10:37 | 2024-12-08 | 14:40 | 0.0026817 | 1.1036e-05 | 4 | 972 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faulty TFR X1994 (Internal fault, no damage on the outside, lightning prone area, possible struck about a month a go and only failed now) Isolated at TFR X1994 Fuses TFR Replaced, Full Power restored | .
1440 |  | JE24044878 | unknown COLVILLE ROAD,Colville,Rural | Eastern | COLVILLE | 2024-12-08 | 9:34 | 2024-12-08 | 17:33 | 0.06652 | 0.0009077 | 329 | 24110 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: Recloser 9736 Protection flags (nil where none): Phase C OC CAUSE: Faulty Transformer TC1301 Location: Pole V12815 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Transformer TC1301 replaced. Power ON -17:32 | .
1441 |  | JE24044889 | 366 RATAPIKO ROAD,RATAPIKO,INGLEWOOD | Western | RATAPIKO | 2024-12-08 | 11:41 | 2024-12-08 | 13:46 | 0.001033 | 8.2769e-06 | 3 | 374 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: 6236 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 13:45 Cause: Chiller pump fault at cow shed Weather (wind/rain): calm Follow up required (select advisory)?n LV fuses removed, HV fuses replaced, testing completed, livened LV circuits one by one, found a fault on the cow shed circuit, tracked down to a fault chiller pump, customer advised to get an electrician in to replace pump | .
1442 |  | JE24044892 | 621 WAIKAWAU BEACH ROAD,WAIKAWAU,COROMANDEL | Eastern | COLVILLE | 2024-12-08 | 12:37 | 2024-12-08 | 15:34 | 0.056594 | 0.00032004 | 116 | 20513 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: Recloser 9776 Protection flags (nil where none): None CAUSE: Floating Conductor Location: Pole V0786 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): None Follow up Required (select advisory)? No Additional fault restoration comments: Dropped Recloser 9776 after receiving a call from Shane Walker that a LIVE conductor was lying on the ground. Opened Recloser 9776 at 12:37.Issued Operational Control to Hamish McMillan to work past Recloser 9776., Very bad comms in the area. This is a safety manager issue if the recloser is not tripping and a conductor is lying on the ground. To check protection settings SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1443 |  | JE24044893 | 5362 TAIHAPE-NAPIER ROAD, TAIHAPE | Western | MOAWHANGO | 2024-12-08 | 17:36 | 2024-12-08 | 19:23 | 0.0044654 | 4.1384e-05 | 15 | 1619 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Location: 787095 Isolation: Fuses 1260 Weather (wind/rain): Light Rain / Calm Additional fault restoration comments: Replaced Damaged jumper & binder | .
1444 |  | JE24044926 | 3 ARAPUNI ROAD,LICHFIELD,PUTARURU | Eastern | ARAPUNI ST | 2024-12-08 | 23:27 | 2024-12-09 | 2:26 | 0.08577 | 0.00069802 | 253 | 31088 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: TIR CB 3132 Protection flags (nil where none): PH A OC EF CAUSE: Unknown - Could be from CB4 not opening fast enough - Live both Sides of CB Location: Tirau Sub Voltage & Device ID: PUT CB 4 Protection flags (nil where none): PH B - OC CAUSE: Cable Fault Between Sw/Gear 9215/3 and 13149/1 Location: Sw/Gear 9215/3 Sw/Gear 13149/1 PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): Rain LFI (Y/N + Comments): NIL Follow up Required (select advisory)? Additional fault restoration comments: Patrol Overhead, Livend in sections to sectionlize fault, Fault Found Between Two Switch Gears DNO 2412014 | .
1445 |  | JE24044433 | 971 GLENBURN ROAD, GLENBURN, MASTERTON, 5883 | Western | WESTMERE GLADSTONE | 2024-12-07 | 9:01 | 2024-12-07 | 10:36 | 0.007145 | 7.4492e-05 | 27 | 2590 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace broken binders at poles 832337 and 841488 | .
1446 |  | JE24044434 | 349 CRAIGIE LEA ROAD, TE WHARAU, MASTERTON, 5883 | Western | WESTMERE GLADSTONE | 2024-12-07 | 11:30 | 2024-12-07 | 12:41 | 0.0021522 | 3.0349e-05 | 11 | 780 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Repair broken 11kV binders at poles 832167, 841879 and 366677 | .
1447 |  | JE24044731 | 4842 TAIHAPE-NAPIER ROAD, TAIHAPE, 4792 | Western | MOAWHANGO | 2024-12-07 | 13:10 | 2024-12-07 | 14:59 | 0.0012013 | 1.1036e-05 | 4 | 435 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fault man will attend tomorrow morning 7/12/24 at 07;00am Adrian Marshal was onsite while FM had power off so the onsite FM made Repairs to pole 787120 - It has a Brocken binder Aswell Broken binders and burnt cross arms at poles 787120 & 787122 Isolated at Fuses 1290 1 x Binder replaced at Pole 787120 & 2 x Binder replaced at Pole 787122 Full power restored Cross arms not replaced as this line is going to be removed soon | .
1448 |  | JE24044768 | 9438 2 ,WAIHI,WAIHI | Eastern | WAIHI GOLD 2 | 2024-12-07 | 0:40 | 2024-12-07 | 3:01 | 0.00038975 | 2.759e-06 | 1 | 141 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: CB, 2 CB 7 Protection flags (nil where none): A & B phase OC CAUSE: Unknown Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): FIne LFI (Y/N + Comments): N Follow up Required (select advisory)? Additional fault restoration comments: LOS to Oceania Gold, patrolled Powerco lines no fault found. Oceania Gold opened their incommers and feeders livened one at a time. Once lines proved de-energised using Powerco CB's and relivened site to allow for Oceania to complete restoration of their network. Emailed Shirley McGrath with details of outage | .
1449 |  | JE24044772 | 355 MINDEN ROAD,TE PUNA,TAURANGA | Eastern | WAIPUNA | 2024-12-07 | 7:21 | 2024-12-07 | 7:26 | 0.001516 | 0.00028693 | 104 | 549 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fused ABS SD3-147 No. Fuses: 2 Fuse Amp Size: 40A TIME CLOSED: 07:26 Cause: Unknown Weather (wind/rain): Fine Follow up required (select advisory)? NIL LFI's at pole 213162 operated | .
1450 |  | JE24044841 | 2248 OPUNAKE ROAD,AWATUNA,HAWERA | Western | RIVERLEA | 2024-12-07 | 17:33 | 2024-12-07 | 18:31 | 0.0018929 | 3.3108e-05 | 12 | 686 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 5896 No. Fuses: 2 Fuse Amp Size: 8 Amp TIME CLOSED: 18:30 hrs Cause: Unk Weather (wind/rain): Calm Follow up required (select advisory)? | .
1451 |  | JE24044848 | 219 TE ORE ORE ROAD,TE ORE ORE,MASTERTON | Western | TOTARA ST | 2024-12-07 | 21:46 | 2024-12-08 | 3:00 | 0.36288 | 0.0028969 | 1050 | 131529 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: CB C821 Protection flags (nil where none): 3 phase OC CAUSE: Car V pole Location: Pole 845848 Temp generation (stat details when used): N PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): fine LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Car V Pole F4104357 2 properties had the service cables ripped away from the house. Tried to contact but no one answering, disconnected for safety. A35897 108 Oxford Street A35898 110 Oxford Street | .
1452 |  | JE24044853 | 149 25 ,WAITAKARURU,THAMES | Eastern | MANGATARATA | 2024-12-07 | 23:19 | 2024-12-08 | 1:58 | 0.014943 | 9.3805e-05 | 34 | 5416 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: FP770 No. Fuses: 2 Fuse Amp Size: 30A TIME CLOSED: 0158 Cause: Unknown Weather (wind/rain): Fine Follow up required (select advisory)? | .
1453 |  | JE24041324 | 690 AUTAWA ROAD, TARATA, INGLEWOOD, 4387 | Western | TARATA | 2024-12-06 | 9:46 | 2024-12-06 | 12:50 | 0.0025451 | 1.3795e-05 | 5 | 923 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Helicopter string new span 6.6kV conductor between poles 762002 & 762003 | .
1454 |  | JE24041837 | 104 HUNGERS ROAD, PUKENGAHU, STRATFORD, 4393 | Western | CLOTON RD INDUSTRIAL | 2024-12-06 | 9:16 | 2024-12-06 | 13:40 | 0.0036492 | 1.3795e-05 | 5 | 1323 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV pin crossarms at Poles 738158, 738159, 738160, 738161, 738163, 738165, 738166, 738170, 738173, 738157, 738167. | .
1455 |  | JE24041920 | 234 BRUNSWICK ROAD, BRUNSWICK, WANGANUI, 4571 | Western | BRUNSWICK | 2024-12-06 | 8:31 | 2024-12-06 | 16:01 | 0.0037264 | 8.2769e-06 | 3 | 1351 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Vegetation cutting between poles 782753 to 844772 | .
1456 |  | JE24041970 | 11 POHUTUKAWA DRIVE, ATHENREE, KATIKATI, 3177 | Eastern | ATHENREE | 2024-12-06 | 10:00 | 2024-12-06 | 11:17 | 0.014209 | 0.00018485 | 67 | 5150 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Link Box Maintenance - SA2-016 | .
1457 |  | JE24042002 | 236 OTUMOETAI ROAD, OTUMOETAI, TAURANGA, 3110 | Eastern | CENTRAL OTUMOETAI | 2024-12-06 | 3:17 | 2024-12-06 | 4:48 | 0.039102 | 0.0004304 | 156 | 14173 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Linkbox maintenance at SD4-411 | .
1458 |  | JE24042005 | 110 FAULL ROAD, TIKORANGI, WAITARA, 4383 | Western | TIKORANGI | 2024-12-06 | 9:01 | 2024-12-06 | 12:29 | 0.0057396 | 2.759e-05 | 10 | 2080 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Upgrade pole 754692 to a new double pole transformer structure. Remove and relocate the existing transformer 4910T across to the new structure. | .
1459 |  | JE24042011 | 296 MARAMARAHI ROAD, THAMES, THAMES, 3578 | Eastern | TOTARA | 2024-12-06 | 9:46 | 2024-12-06 | 10:15 | 0.00054637 | 1.9313e-05 | 7 | 198 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv Pole S12638 with new 11m Busk | .
1460 |  | JE24042042 | 118 MATATOKI ROAD, MATATOKI, THAMES, 3578 | Eastern | PURIRI | 2024-12-06 | 8:35 | 2024-12-06 | 14:48 | 0.043237 | 0.00011588 | 42 | 15672 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace HV and LV cross arms on Poles 877721, S0134, S12705, S0141, S0146, S12710, S0166, S0173 and S12717 | .
1461 |  | JE24042055 | 162 REYNOLDS ROAD, RATANA, WANGANUI, 4581 | Western | TURAKINA | 2024-12-06 | 8:31 | 2024-12-06 | 14:42 | 0.0051227 | 1.3795e-05 | 5 | 1857 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | HV reconductoring from and including pole 794716 to 375502. | .
1462 |  | JE24042061 | 2 MOWBRAY ROAD, WAHAROA, WAHAROA, 3401 | Eastern | MOWBRAY RD | 2024-12-06 | 8:47 | 2024-12-06 | 12:49 | 0.0073373 | 3.0349e-05 | 11 | 2659 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace LV panel on 11kV Transformer TC4436 with an RDL pillar. | .
1463 |  | JE24042295 | 99 PUKEKAURI ROAD, WAIKINO, WAIHI, 3682 | Eastern | WAITAWHETA | 2024-12-06 | 9:15 | 2024-12-06 | 14:51 | 0.17237 | 0.00051317 | 186 | 62478 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Stringing fibre between poles 391542 / 388501 & P2246. LIVE 11kV Overhead lines between poles 391542 / 38850 & P2265 fibre run outside of MADs. | .
1464 |  | JE24042642 | 575 3 ROAD, TE PUKE, TE PUKE, 3183 | Eastern | MANOEKA RD | 2024-12-06 | 9:54 | 2024-12-06 | 13:03 | 0.050089 | 0.00026762 | 97 | 18155 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace DNO sectionaliser 9878/2 | .
1465 |  | JE24044378 | 52 RANGITATAU EAST ROAD, KAI IWI, WANGANUI, 4578 | Western | WESTMERE PEAT ST | 2024-12-06 | 10:32 | 2024-12-06 | 12:25 | 0.040612 | 0.00036142 | 131 | 14720 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11KV X-Arm on pole 781878 raised by Helicopter Pole Top Topography | .
1466 |  | JE24044396 | HUNTERVILLE 22KV | Western | HUNTERVILLE 22KV | 2024-12-06 | 10:40 | 2024-12-06 | 11:57 | 0.0006347 | 8.2769e-06 | 3 | 230 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11KV Binder on pole 810138 raised by Helicopter Pole Top Topography | .
1467 |  | JE24044624 | 534F MCLAREN FALLS ROAD,OMANAWA,TAURANGA | Eastern | KEENAN RD | 2024-12-06 | 0:30 | 2024-12-06 | 2:06 | 0.0018495 | 1.9313e-05 | 7 | 670 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | HV jumper broke between the fuse and HV bushing of transformer. Transformer isolated and jumper was repaired. | .
1468 |  | JE24044633 | 711 SALISBURY ROAD,MIDHIRST,STRATFORD | Western | CLOTON RD SOUTH | 2024-12-06 | 5:27 | 2024-12-06 | 7:26 | 0.0026291 | 2.2072e-05 | 8 | 953 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Lines down found at Pole 740651 Cause Age Isolated at Fuses 5600 | .
1469 |  | JE24044649 | 57 TAI ROAD,OPUNAKE,OPUNAKE | Western | SOUTH RD NGARIKI | 2024-12-06 | 11:18 | 2024-12-06 | 12:49 | 0.0059914 | 6.6215e-05 | 24 | 2172 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Broken Jumper found at Fused ABS 6916 Isolated at Links 12302 Jumper Repaired | .
1470 |  | JE24044713 | 27B RAETIHI OHAKUNE ROAD,RAETIHI,RAETIHI | Western | RAETIHI | 2024-12-06 | 13:21 | 2024-12-06 | 15:16 | 0.0012722 | 1.1036e-05 | 4 | 461 | Unplanned | VEGETATION - INSIDE ZONE | Branch damaged LV cables Cables repaired Damage caused HV fuse to blow Fuses Location: X1943 No. Fuses: 3 Fuse Amp Size: 2 TIME CLOSED: 15-15 Cause: Branch fell on lines Weather (wind/rain): Windy Follow up required (select advisory)? also replaced 3 x LV Fuse boxes complete With Fuses at transformer X1943 At Pole 448007 Replaced 1 X 40 Amp Fuse for House number 27 Also 1 X 40 Amp fuse for House 27A at same Pole Smart meters no good so WELLS bypassed them They will return to replace them Number 27 Liven and tested ok Number 27A liven but no good on test so Disconnected on Tag A46522 Replace 6M Of Conductor at Job site | .
1471 |  | JE24044741 | 21 SHAFTESBURY ROAD, MANAWARU, TE AROHA, 3391 | Eastern | MAUNGAKAWA ROAD | 2024-12-06 | 19:55 | 2024-12-06 | 21:50 | 0.00031815 | 2.759e-06 | 1 | 115 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Cross arm replaced on private Pole C13401 under SRC | .
1472 |  | JE24044742 | unknown MASTERTON CASTLEPOINT ROAD,Tinui,Rural | Western | LANGDALE | 2024-12-06 | 12:25 | 2024-12-06 | 15:12 | 0.00046102 | 2.759e-06 | 1 | 167 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: 7867 No. Fuses: 3 Fuse Amp Size: 6A TIME CLOSED: 15:12 hrs Cause: Unknown / Operational Patrolled Weather (wind/rain): Calm Follow up required (select advisory)? | .
1473 |  | JE24041533 | 383 STRANGE ROAD, OTWAY, TE AROHA, 3392 | Eastern | SPRINGDALE | 2024-12-05 | 10:01 | 2024-12-05 | 13:25 | 0.0090281 | 4.4143e-05 | 16 | 3272 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Red tagged 11kV Pole C2720. Replace Crossarms at 11kV Poles C2721 & C2723. | .
1474 |  | JE24041622 | 4238 27, TATUANUI, MORRINSVILLE, 3374 | Eastern | TATUANUI | 2024-12-05 | 8:30 | 2024-12-05 | 12:31 | 0.011925 | 4.9661e-05 | 18 | 4322 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | PQI Case 13377 - Replace transformer structure TP1445 with a double pole 100kVA transformer | .
1475 |  | JE24041633 | 50 DONOVANS ROAD, KOPUARANGA, MASTERTON, 5882 | Western | OXFORD ST | 2024-12-05 | 9:06 | 2024-12-05 | 14:20 | 0.058916 | 0.00018761 | 68 | 21354 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Change 11kV x-arms between S88 & S123 | .
1476 |  | JE24041638 | 3 PERCIVAL AVENUE, MATUA, TAURANGA, 3110 | Eastern | WARATAH ST | 2024-12-05 | 23:30 | 2024-12-06 | 1:26 | 0.040058 | 0.00034763 | 126 | 14519 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Linkbox maintenance at TC4-052 | .
1477 |  | JE24041717 | 11 AIRPORT ROAD, WHANGANUI AIRPORT, WANGANUI, 4501 | Western | MARANGAI | 2024-12-05 | 9:31 | 2024-12-05 | 15:16 | 0.041034 | 0.00011864 | 43 | 14873 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles & x-arms between 774073 - 774048 & 468970 | .
1478 |  | JE24041816 | LINDERMANN RD | Eastern | LINDERMANN RD | 2024-12-05 | 8:46 | 2024-12-05 | 19:56 | 0.083239 | 0.00012415 | 45 | 30170 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Reconductor 11kV between Poles 263964 & 204444. Isolation SB1-025. | .
1479 |  | JE24041836 | 5249 SOUTH ROAD, OAONUI, OPUNAKE, 4681 | Western | SOUTH RD NGARIKI | 2024-12-05 | 9:04 | 2024-12-05 | 14:54 | 0.024156 | 6.8974e-05 | 25 | 8755 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace poles 713159, 713160, 713161,713163, 713165, 713080, 851262, 713119 & 713158. replace over head conductor from pole 851262 to 713080 with new Bare Kutu | .
1480 |  | JE24041872 | 81 CLIFTON GROVE ROAD, ADMIRAL HILL, MASTERTON, 5883 | Western | LONGBUSH | 2024-12-05 | 8:45 | 2024-12-05 | 14:40 | 0.047943 | 0.00013519 | 49 | 17377 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles and hardware past S333 | .
1481 |  | JE24041927 | 42 RATANA ROAD, RATANA, WANGANUI, 4581 | Western | TURAKINA | 2024-12-05 | 8:36 | 2024-12-05 | 14:13 | 0.14616 | 0.00043316 | 157 | 52977 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | HV reconductoring from and including poles 360746 to 474795. | .
1482 |  | JE24041974 | 107 EDGECUMBE ROAD, TAURANGA SOUTH, TAURANGA, 3112 | Eastern | 11TH AVE | 2024-12-05 | 23:46 | 2024-12-06 | 1:46 | 0.017876 | 0.00014898 | 54 | 6479 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV RMU oil maintenance - SK5-124/SK5-125/SK5-127 | .
1483 |  | JE24042026 | 356 PUKEPAPA ROAD, MARTON, MARTON, 4789 | Western | BULLS | 2024-12-05 | 8:45 | 2024-12-06 | 17:32 | 0.011974 | 1.6554e-05 | 3 | 4340 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Shut 4 - Connect new HV Cable between CB6 and new RMU 16136/1. | .
1484 |  | JE24042654 | 105 CENTENNIAL DRIVE, PORT TARANAKI, NEW PLYMOUTH, 4310 | Western | CENTENNIAL DR | 2024-12-05 | 9:30 | 2024-12-05 | 12:12 | 0.00044631 | 2.759e-06 | 1 | 162 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Tx 933, replace severely rusted lid. | .
1485 |  | JE24044485 | 3091 CARRINGTON ROAD,OKATO,NEW PLYMOUTH | Western | INLAND COAST | 2024-12-05 | 2:51 | 2024-12-05 | 6:42 | 0.0025529 | 1.1036e-05 | 4 | 925 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 681 No. Fuses: 2 Fuse Amp Size: 3 Amp TIME CLOSED: 06:42 Cause: Unknown Weather (wind/rain): Windy Follow up required (select advisory)? N | .
1486 |  | JE24044490 | unknown unknown,Kahutara,Rural | Western | KUMENGA | 2024-12-05 | 9:05 | 2024-12-05 | 15:33 | 0.0032049 | 8.2769e-06 | 3 | 1162 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: Twisted Crossarm due to rusted King bolt Location: 799078 Isolation: Fuses 7312 Additional Info: Twisted Xarm caused lines to come down. Replaced King bolt & nuts and repaired lines down | .
1487 |  | JE24044502 | 149 PAEROA-TAHUNA ROAD,SPRINGDALE,MORRINSVILLE | Eastern | TE PUNINGA | 2024-12-05 | 7:33 | 2024-12-05 | 7:34 | 0.00051893 | 0.00051869 | 188 | 188 | Unplanned | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | Voltage & Device ID: RP05 Protection flags (nil where none): N/A Weather (wind/rain): Follow up required (select advisory): Recloser comms failed on A/R and it looked to be a feeder fault. Once comms came back REC indicated closed and showed an autoreclose event. Suspect failed batteries JE24044513 LFI Activation: N | .
1488 |  | JE24044505 | 21 HERBERT STREET,EKETAHUNA,EKETAHUNA | Western | EKETAHUNA | 2024-12-05 | 7:07 | 2024-12-05 | 13:09 | 0.058277 | 0.00022623 | 82 | 21123 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Location: P16814 Cause: HV Insulator came off pin & conductor burnt through X Arm. Isolation: ABS U7 Weather (wind/rain): Light Rain / Windy Follow up required (select advisory)? Additional Info: After burning through HV Xarm fell down onto LV. Premises were checked for an HV/LV clash but were all ok. Also 1x HV fuse replaced at Fuses U6 at 08:33 hrs | .
1489 |  | JE24044526 | unknown TINUI VALLEY ROAD,Tinui Valley,Rural | Western | CASTLEPOINT | 2024-12-05 | 8:51 | 2024-12-05 | 17:15 | 0.43566 | 0.0011505 | 318 | 157907 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV, Rec C225 Protection flags (nil when none): O/C B-C phase CAUSE: Broken tree branch contacting lines in strong winds Location: 838662 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: Yes / Operational Weather (wind/rain): Windy Follow up required (select advisory)? Chris Norman following up with vegetation control Additional fault restoration comments: Obertech staff were on way to start up generator at Castlepoint. Power restored before they arrived. SUBTRANSMISSION DETAIL LOS to sub (no or sub name): Circuit that tripped: DTF (KM): | .
1490 |  | JE24044538 | 71 AOTEA CRESCENT,TOKOROA,TOKOROA | Eastern | DUKE ST | 2024-12-05 | 9:31 | 2024-12-05 | 10:50 | 0.1049 | 0.0046047 | 1669 | 38020 | Unplanned | THIRD PARTY INTERFERENCE - DIG IN | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 6 Protection flags (nil where none): B ph O/C E/F CAUSE: Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): 2412004 Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): LFI's active at Sw/Gear 9896/1, not active at /3 or 4 FM tp confirm Follow up Required (select advisory)? Additional fault restoration comments: FM instructed to check LFI's at Sw/Gear 9896 (one set active) Found LFI's for /3 & /1 Active SW/Gear 9896/3 opened, CB 6 Closed LFI's Active at Sw/Gear 9598/1 & 3 Sw/Gear 9598/1 Opened , Sw/Gear 9896/3 Closed FM reported Under boring had been done near Sw/Gear IC3047 Cable to Sw/Gear livened, then de-energised, Sw/Gear and Cable to Transformers TC4433 & TC3207 Livened Cable Between Sw/Gear IC3028 & 9652/3 Isolated Back Feed installed via 9652/2 GMCB 14278/3 Tripped Sw/Gear 9652/2 Opened, GMCB 14278/3 Closed Bulldozer found ripping ground near Sw/Gear IC1472 Isolated & Earthed at Sw/Gears IC1472 & 9652/1 DNO Raised for cable FM talked to Bulldozer operator. (Company Camex Earth Works) SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1491 |  | JE24044563 | 236 PARTON ROAD,PAPAMOA,TE PUKE | Eastern | STEVENSON DRIVE | 2024-12-05 | 11:15 | 2024-12-05 | 12:05 | 0.00027231 | 5.5179e-06 | 2 | 99 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Repair 1 x jumper on load side of Fuses FP518 | .
1492 |  | JE24044585 | 344 PUKEMAPOU ROAD, TAIHAPE, 4796 | Western | MATAROA A | 2024-12-05 | 20:16 | 2024-12-05 | 22:16 | 0.0023285 | 1.9313e-05 | 7 | 844 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Repairs to conductor at Pole 795228 Found by Poletech Isolated at Fuses 933 | .
1493 |  | JE24044605 | 4860 Taihape-Napier Road, Ngamahanga 4792 | Western | MOAWHANGO | 2024-12-05 | 19:55 | 2024-12-05 | 21:39 | 0.0011509 | 1.1036e-05 | 4 | 417 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Floating Conductor at Pole 787199 Isolated at Fuses 1290 Own Issue Etc of Permit | .
1494 |  | JE24044612 | 22 LANDGUARD ROAD,WHANGANUI AIRPORT,WANGANUI | Western | MARANGAI | 2024-12-05 | 17:46 | 2024-12-05 | 19:09 | 0.00045698 | 5.5179e-06 | 2 | 166 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Replaced Transformer 1398W due to High Voltages Isolated at Transformer | .
1495 |  | JE24044616 | 10 BEDFORD ROAD SOUTH,NORFOLK,INGLEWOOD | Western | MOUNTAIN RD | 2024-12-05 | 22:07 | 2024-12-06 | 0:56 | 0.0070071 | 4.1384e-05 | 15 | 2540 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Replaced 3 X DDOs and 1 X crossarm At Pole 757937 Isolated at Fuses 5421 | .
1496 |  | JE24041322 | 1403 KAHUTARA ROAD, KAHUTARA, FEATHERSTON, 5772 | Western | KUMENGA | 2024-12-04 | 9:05 | 2024-12-04 | 11:00 | 0.00095446 | 8.2769e-06 | 3 | 346 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re-sag 11kV lines past fuses 7305 | .
1497 |  | JE24041327 | 1403 KAHUTARA ROAD, KAHUTARA, FEATHERSTON, 5772 | Western | KUMENGA | 2024-12-04 | 13:31 | 2024-12-04 | 13:59 | 7.8676e-05 | 2.759e-06 | 1 | 29 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Tighten hardware on transformer T1906 | .
1498 |  | JE24041330 | 13573 52, TIRAUMEA, EKETAHUNA, 4996 | Western | BROOKLANDS | 2024-12-04 | 9:30 | 2024-12-04 | 12:21 | 0.011276 | 6.6215e-05 | 24 | 4087 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove 11kV poles P10663 & P10234 and re-bury to correct depth | .
1499 |  | JE24041365 | 65 MIRRIELEES ROAD, TAURANGA, TAURANGA, 3110 | Eastern | HARRINGTON ST | 2024-12-04 | 17:02 | 2024-12-04 | 18:59 | 0.0041958 | 3.5867e-05 | 13 | 1521 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To repair oil leaks on transformer TL2-002 | .
1500 |  | JE24041448 | 153 REA ROAD, TAHAWAI, KATIKATI, 3178 | Eastern | WHARAWHARA ROAD | 2024-12-04 | 8:32 | 2024-12-04 | 10:31 | 0.00032818 | 2.759e-06 | 1 | 119 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To repair oil leaks on TB1-123 | .
1501 |  | JE24041464 | 28 MOEWAI ROAD, WHITIANGA, WHITIANGA, 3591 | Eastern | BUFFALO BEACH | 2024-12-04 | 17:31 | 2024-12-04 | 23:18 | 0.0076729 | 2.2072e-05 | 8 | 2781 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To carry out oil leak repair on TP3151 | .
1502 |  | JE24041473 | WAVERLEY | Western | WAVERLEY | 2024-12-04 | 9:27 | 2024-12-04 | 11:26 | 0.0081677 | 6.8974e-05 | 25 | 2960 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace transformer 4651W 35 Rosemount road Waipipi | .
1503 |  | JE24041506 | 1511 UPPER BALL ROAD, HURLEYVILLE, PATEA, 4598 | Western | KAKARAMEA | 2024-12-04 | 9:13 | 2024-12-04 | 14:47 | 0.0055306 | 1.6554e-05 | 6 | 2005 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Asplundh to cut trees between 11kV Poles 731181 & 731188. | .
1504 |  | JE24041528 | 711 MANGAONE ROAD, HALCOMBE, FEILDING, 4779 | Western | MT STEWART | 2024-12-04 | 8:30 | 2024-12-04 | 11:25 | 0.014933 | 8.5528e-05 | 31 | 5413 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace all hardware including 11kV Transformer T3/211 at Pole P09143. | .
1505 |  | JE24041557 | TOKO | Western | TOKO | 2024-12-04 | 9:01 | 2024-12-04 | 14:10 | 0.044712 | 0.00014623 | 53 | 16206 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replacing N/O ABS 4890 with an automated Safelink 12779. Outage done in 2 shuts to accommodate backfeeds. Shut 2 to remove ABS 4890 and connect new cable to O/H line pole 739394 from SW 12779/1 Shut 1 to be completed first on NAPA116480 Recloser 12328/2 Tripped during switching on feeder. Left open until FM contacted to confirm operation time CB D21 found to be able to be operated electrically while in the earth position. DNO 2412002 Raised to repair this. | .
1506 |  | JE24041725 | 109 MAIN ROAD, TOKOROA, TOKOROA, 3420 | Eastern | BROWNING ST | 2024-12-04 | 23:30 | 2024-12-05 | 1:43 | 0.0054841 | 4.1384e-05 | 15 | 1988 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - IC1923-IC1912-FC5032 | .
1507 |  | JE24041726 | 162 REYNOLDS ROAD, RATANA, WANGANUI, 4581 | Western | TURAKINA | 2024-12-04 | 8:31 | 2024-12-04 | 14:41 | 0.0051062 | 1.3795e-05 | 5 | 1851 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 794719, 794720, 794721,794724 and 794726 and crossarms from and including 482063 to 794726 | .
1508 |  | JE24041729 | 1328 TARATA ROAD, KAIMATA, INGLEWOOD, 4387 | Western | KOHETE RD | 2024-12-04 | 9:31 | 2024-12-04 | 15:21 | 0.046309 | 0.00013243 | 48 | 16785 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To Replace tx 4412 - new 30kva dual + change tx structure 2237T with new pole - shut 2 | .
1509 |  | JE24042037 | 120 LOVEGROVE ROAD, TE AROHA, TE AROHA, 3393 | Eastern | LOVEGROVE RD | 2024-12-04 | 8:55 | 2024-12-04 | 16:09 | 0.037105 | 8.5528e-05 | 31 | 13449 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Poles and hardware at C342, C343, C13155, C13156, C13157, C13158. Replace Transformer TC4016. | .
1510 |  | JE24043109 | 410 WAIHI BEACH ROAD, WAIHI, WAIHI, 3681 | Eastern | WAIHI3122-WAIHI BEACH3132 33KV | 2024-12-04 | 23:00 | 2024-12-05 | 16:03 | 0.10039 | 0.0096453 | 3496 | 36388 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 33kV Crossarms between poles CREWBH052 - CREWBH057 Waihi Beach Rd | .
1511 |  | JE24043747 | 3 GRIDLEY ROAD, RANGIURU, TE PUKE, 3188 | Eastern | TE MATAI RD | 2024-12-04 | 8:46 | 2024-12-04 | 14:11 | 0.024209 | 7.4492e-05 | 27 | 8775 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 1. Install new pole between 221104 & 221105 and terminate new cable to O/H line and 14966/4. 2.Transfer Load from O/H TX TE6-026 to G/M TP4503 connected to 14966/2 (RMU6). 3. Remove O/H HV from new pole to 394745. | .
1512 |  | JE24044290 | 4929 Taihape-Napier Road, Ngamahanga 4792 | Western | MOAWHANGO | 2024-12-04 | 9:59 | 2024-12-04 | 12:12 | 0.005511 | 4.1384e-05 | 15 | 1998 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faultman reported safe to leave over night and will return in morning, Faultman also informed Controller that he was worried about been fatigued to drive home as has been a long drive just to get to site and there is no comms out there at pole 787221 a 30 minute round trip just to find comms. 04/12/2024 Isolated at Fuses 1260 09:59 Repairs carried out at Pole 787221 (Replaced Cross arms) Power restored 12:12 | .
1513 |  | JE24044319 | 1048 MAIN DRAIN ROAD,RANGIOTU,PALMERSTON NORTH | Western | TAIKOREA | 2024-12-04 | 7:01 | 2024-12-04 | 8:41 | 0.016849 | 0.0001683 | 61 | 6107 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | REGULATORY INFORMATION Voltage & Device ID: Not a Feeder Fault Protection flags (nil where none): N/A CAUSE: Blown Jumper Location: Pole P36019 Temp generation (state details when used): PERFORMANCE DETAIL Weather (wind/rain): Fine Follow up Required (select advisory)? Additional fault restoration comments: Replaced 2 Jumper connections 1 Was old age the other Copper Link on Ali Wire | .
1514 |  | JE24044326 | 1333 LAKE FERRY ROAD,DYERVILLE,MARTINBOROUGH | Western | OTARAIA | 2024-12-04 | 6:42 | 2024-12-04 | 9:16 | 0.00083136 | 5.5179e-06 | 2 | 301 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: 7354 2 x 3amp 9:15am / 7355 2 x 8 amp 9:10am No. Fuses: Fuse Amp Size: TIME CLOSED: Cause: Wind Weather (wind/rain): calm Follow up required (select advisory)? | .
1515 |  | JE24044343 | 1151 MAKURI ROAD,HUIROA,STRATFORD | Western | STRATHMORE | 2024-12-04 | 8:14 | 2024-12-04 | 8:19 | 0.00075191 | 0.0001545 | 56 | 273 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | . | .
1516 |  | JE24044349 | 58 MATAKOKIRI DRIVE,TAURIKO,TAURANGA | Eastern | PYES PA | 2024-12-04 | 8:47 | 2024-12-04 | 17:03 | 0.055303 | 0.0021216 | 691 | 20045 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Pole 216629 Protection flags (nil where none): Nil CAUSE: Rotten Crossarm Broken Pole 216629 Location: Pole 216629 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Reported to Dispatch Weather (wind/rain): Fine LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Contractor Reported Broken Crossarm lying in Circuit below, Line De Energized till contractor got on site to ascertain voltages involved. Broken HV arm lying on D/Out Arm. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1517 |  | JE24044362 | 6 RANGIORA ROAD,RANGIWAEA,WANGANUI | Western | IRIRANGI | 2024-12-04 | 9:13 | 2024-12-04 | 11:46 | 0.0012642 | 8.2769e-06 | 3 | 458 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 011 2 x 6amp fuses 11:46am / X704 2 x 2amp fuses 11:21am No. Fuses: 4 Fuse Amp Size: TIME CLOSED: Cause: Possible lightning Weather (wind/rain): Over cast Follow up required (select advisory)? | .
1518 |  | JE24044436 | 839A STATE HIGHWAY 53,TAUHERENIKAU,FEATHERSTON | Western | DAIRY FACTORY | 2024-12-04 | 15:20 | 2024-12-04 | 17:25 | 0.00034507 | 2.759e-06 | 1 | 125 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: 8015 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 17-25 Cause: Unknown Weather (wind/rain): Fine Follow up required (select advisory)?Happen over a week ago as freezer thawed out | .
1519 |  | JE24038866 | 1671 WELLINGTON ROAD, MARTON, MARTON, 4787 | Western | CROFTON | 2024-12-03 | 8:54 | 2024-12-03 | 12:57 | 0.0013386 | 5.5179e-06 | 2 | 485 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Isolation for vegetation cutting 800779-800782 | .
1520 |  | JE24041156 | 561 MATAHIWI ROAD, MATAHIWI, MASTERTON, 5888 | Western | MOUNT BRUCE | 2024-12-03 | 8:31 | 2024-12-03 | 13:14 | 0.002347 | 8.2769e-06 | 3 | 851 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace red tag pole 836405 and re-sag 11kV lines & replace/tighten 11kV insulator/xarm at pole 836407 | .
1521 |  | JE24041157 | 81 CLIFTON GROVE ROAD, ADMIRAL HILL, MASTERTON, 5883 | Western | LONGBUSH | 2024-12-03 | 8:46 | 2024-12-03 | 15:19 | 0.05312 | 0.00013519 | 49 | 19254 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles and hardware past S333 | .
1522 |  | JE24041179 | MANAIA | Western | MANAIA | 2024-12-03 | 9:16 | 2024-12-03 | 14:17 | 0.014135 | 4.6902e-05 | 17 | 5123 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace fused ABS 6935 + Earthing @ 844564, Tx M4180 structure, pole structure 718470, staywire @ 718474. | .
1523 |  | JE24041338 | 521 MAUNGARANGI ROAD, PAENGAROA, TE PUKE, 3189 | Eastern | MANGOREWA | 2024-12-03 | 8:46 | 2024-12-03 | 14:55 | 0.054891 | 0.00014898 | 54 | 19895 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv overhead conductors between poles 221849 & 221860 with ACSR Ferret | .
1524 |  | JE24041364 | 26 WEKA STREET, MATAMATA, MATAMATA, 3400 | Eastern | RAWHITI AVE | 2024-12-03 | 8:32 | 2024-12-03 | 15:41 | 0.10825 | 0.00025382 | 92 | 39237 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Disconnect and remove TC3794 and associated pad. Install new pad and 300kVA CityPad. Re-term and connect 11kV cable to new transformer. Relocate the cable connected to source A of TC3785 onto switch 3 of the new CFCF and re-terminate. Connect new 11kV cable between fuse switch 4 and source A of TC3785. Switch T-Blade switch in TC3785 so source B is isolated. Joint new section of 11kV cable connected to fuse switch 2 to existing cable connected to TC3794. | .
1525 |  | JE24041397 | 195 PARTON ROAD, PAPAMOA BEACH, TE PUKE, 3187 | Eastern | SIMPSON RD | 2024-12-03 | 9:46 | 2024-12-03 | 12:46 | 0.010927 | 6.0697e-05 | 22 | 3960 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9048/1/2/3/4 | .
1526 |  | JE24041407 | 77 MCKAYS LINE, BEACONSFIELD, FEILDING, 4777 | Western | MAKINO | 2024-12-03 | 13:01 | 2024-12-03 | 13:56 | 0.0015096 | 2.759e-05 | 10 | 547 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV crossarm at Pole P17264. | .
1527 |  | JE24041544 | 1801 OHURA ROAD, DOUGLAS, STRATFORD, 4392 | Western | CLOTON RD SOUTH | 2024-12-03 | 9:12 | 2024-12-03 | 14:09 | 0.0024639 | 8.2769e-06 | 3 | 893 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replacing N/O ABS 4890 with an automated Safelink 12779. Outage done in 2 shuts to accommodate backfeeds. Shut 1 to remove 11kV cable below ABS 4890 to re-terminate into ne SW 12779/2. Shut 2 to follow on NAPA 116489 | .
1528 |  | JE24041655 | 2263A 56, LONGBURN, PALMERSTON NORTH, 4477 | Western | DAIRYFACT | 2024-12-03 | 9:30 | 2024-12-03 | 14:35 | 0.038611 | 0.00012691 | 46 | 13995 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace ABS H61 structure & poles between H61, A55 | .
1529 |  | JE24044137 | 91 WESTERN LAKE ROAD,WESTERN LAKE,FEATHERSTON | Western | REVANS ST | 2024-12-03 | 5:06 | 2024-12-03 | 12:58 | 0.047289 | 0.00066767 | 121 | 17140 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11KV Rec C634/2 Protection flags (nil where none): B Phase E/F CAUSE: Floating Conductor Location: Pole 461067 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Replaced Cross arm as well as it was burnt very badly SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1530 |  | JE24044191 | 400 TAUHEI ROAD,MANGATEPARU,MORRINSVILLE | Eastern | MANGATEPARU | 2024-12-03 | 17:48 | 2024-12-03 | 19:04 | 0.01063 | 0.00014071 | 51 | 3853 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: deterioration What was replaced? NA inspection Where was it replaced (pole K0130 Is 2R required? Y 2R Y - What is the timeframe for repairs? will be completed tonight 3/12 Additional Info: 2R to be used Insulators replaced isolated at ABS IC1107-Power restored 19:08Hrs | .
1531 |  | JE24044221 | unknown PAHAUTEA ROAD,Kahutara,Rural | Western | FEATHERSTON No 1 33kV | 2024-12-03 | 12:14 | 2024-12-03 | 12:29 | 0.030602 | 0.0027921 | 1012 | 11092 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 33KV Rec 3139/2 & 3141/2 Protection flags (nil where none): B Phase O/C E/F CAUSE: Unknown Location: Unknown Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): no Circuit patrolled and type: Cursory Patrol 33Kv Lines to Sub From reclosers Weather (wind/rain): Fine LFI (Y/N + Comments): Yes But not working Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Tuhitarata Circuit that tripped: Rec 3139 &3141 DTF (KM):N/A | .
1532 |  | JE24044247 | 281 MANGATARERE VALLEY ROAD,CARRINGTON,CARTERTON | Western | CHESTER RD | 2024-12-03 | 13:22 | 2024-12-03 | 14:10 | 0.0033103 | 6.8974e-05 | 25 | 1200 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: 7576 No. Fuses: 2 Fuse Amp Size: 15 TIME CLOSED: 14:10pm Cause: line clash Weather (wind/rain): fine Follow up required (select advisory)? | .
1533 |  | JE24041123 | LINTON | Western | LINTON | 2024-12-02 | 9:39 | 2024-12-02 | 16:13 | 0.14048 | 0.00035591 | 129 | 50916 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove 11kV ABS H135 from network and replace Pole P03667. Install ENTEC LBS 10901/2 at Pole site P03667 and Source side Solid Links 10901/4 and Commission. Job had an over run due to problems with the comms channel to make Sectionalizer operate. | .
1534 |  | JE24041141 | 332 KIWITAHI STATION ROAD, MORRINSVILLE, MORRINSVILLE, 3371 | Eastern | KEREONE | 2024-12-02 | 9:30 | 2024-12-02 | 11:01 | 0.0059627 | 6.6215e-05 | 24 | 2161 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove ABS 2574, Extend 11kV wires and jumper through HV conductor | .
1535 |  | JE24041146 | 3/95 DEVONPORT ROAD, TAURANGA, TAURANGA, 3110 | Eastern | 5TH AVE | 2024-12-02 | 21:54 | 2024-12-03 | 4:11 | 0.017483 | 4.6902e-05 | 17 | 6337 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | AP-01: Backfeed TL4-016. Remove Sw/Gears SL4-084, SL4-086 & SL4-088 and Tx TL4-016. Retain LV panel for Tx TL4-016 inside Kiosk Building. Tx TL4-016 backfeed to continue to AP-02. AP-02: Remove backfeed. Upgrade LV panels for Tx's TL4-016 & TL4-017. Install new 185mm2 cable between LV panels and transfer load from TL4-016 to TL4-017. | .
1536 |  | JE24041150 | 132 HARRISON STREET, WHANGANUI, WANGANUI, 4500 | Western | BELL ST | 2024-12-02 | 9:31 | 2024-12-02 | 15:32 | 0.067799 | 0.00018761 | 68 | 24574 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Poles 705892 & 705894 | .
1537 |  | JE24041371 | 551 HUTCHINSON ROAD, RICHMOND DOWNS, MORRINSVILLE, 3371 | Eastern | CAMPBELL RD | 2024-12-02 | 8:45 | 2024-12-02 | 9:07 | 0.0032954 | 0.00015174 | 55 | 1194 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REMOVAL OF LFIs AT POLE H3339 ID 11537741 | .
1538 |  | JE24041385 | 346 WAIHEKAU ROAD, TE AROHA WEST, TE AROHA, 3393 | Eastern | NGARUA | 2024-12-02 | 10:30 | 2024-12-02 | 10:48 | 0.0025059 | 0.00014347 | 52 | 908 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE LFIs AT POLE C12611 ID 11537757 | .
1539 |  | JE24041389 | 124 MANGAWARA ROAD, HOE-O-TAINUI, MORRINSVILLE, 3373 | Eastern | HOE-O-TAINUI | 2024-12-02 | 10:00 | 2024-12-02 | 12:37 | 0.0012949 | 8.2769e-06 | 3 | 469 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV Pole K12923 & 11kV Crossarms at Poles K1989 & K1987. | .
1540 |  | JE24041402 | 492 PIAKOITI ROAD, RICHMOND DOWNS, WALTON, 3475 | Eastern | PIAKOITI RD | 2024-12-02 | 12:30 | 2024-12-02 | 12:41 | 0.0018511 | 0.00017657 | 64 | 671 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REMOVAL OF LFIs AT POLE H1843 ID 11530337 | .
1541 |  | JE24041640 | 5137 4, KAKATAHI, WANGANUI, 4573 | Western | IRIRANGI | 2024-12-02 | 9:18 | 2024-12-02 | 9:21 | 0.00047027 | 0.00015174 | 55 | 170 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace multiple poles & x-arms between ABS 596 & ABS TEMP 137 | .
1542 |  | JE24041858 | 360 WAIHI BEACH ROAD, WAIHI, WAIHI, 3681 | Eastern | ATHENREE | 2024-12-02 | 23:02 | 2024-12-03 | 14:42 | 0.068116 | 0.0050848 | 1843 | 24689 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 33kV Crossarms between poles CREWBH041 - CREWBH051 Waihi Beach Rd | .
1543 |  | JE24041892 | 23 HARBOTTLE ROAD, MOTUMAOHO, MORRINSVILLE, 3372 | Eastern | MOTUMAOHO | 2024-12-02 | 13:46 | 2024-12-02 | 14:09 | 0.0041961 | 0.00018485 | 67 | 1521 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace LFIs & install smart navigator at I13266 | .
1544 |  | JE24041896 | 7 DODD ROAD, MOTUMAOHO, MORRINSVILLE, 3372 | Eastern | MOTUMAOHO | 2024-12-02 | 11:45 | 2024-12-02 | 12:02 | 0.0014935 | 8.8287e-05 | 32 | 541 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE LFIs AND INSTALL SMART NAVIGATOR AT POLE I13041 | .
1545 |  | JE24043930 | 142 RICHMOND ROAD,BRIXTON,NEW PLYMOUTH | Western | WAITARA RD | 2024-12-02 | 0:01 | 2024-12-02 | 4:06 | 0.0033839 | 1.3795e-05 | 5 | 1227 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Car V Pole 847991 (LV Pole), first LV pole out from TFR 1765N, LV Fuse blown Isolated & Earthed at TFR 1765N Fuses Pole replaced, full power restored | .
1546 |  | JE24043934 | 12 CARRS ROAD,URENUI,URENUI | Western | MAIN RD MOTONUI | 2024-12-02 | 5:36 | 2024-12-02 | 7:42 | 0.0069421 | 5.5179e-05 | 20 | 2516 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: 5265 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 07:42 Cause: UNKNOWN Weather (wind/rain): RAIN Follow up required (select advisory)? FULL POWER | .
1547 |  | JE24043938 | 11 TARAHUA ROAD,VOGELTOWN,NEW PLYMOUTH | Western | BROOKLANDS 7 | 2024-12-02 | 6:48 | 2024-12-02 | 12:29 | 0.34191 | 0.0024665 | 894 | 123928 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 7 Protection flags (nil where none): Non Feeder de-energized for safety CAUSE: Broken Jumper causing Arcing at pole Location: 846695 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Feeder De-energised for safety While Isolating Work Area found Jumper at ABS 525 almost broken. Isolations moved out to allow for this to be repaired as well. Isolated at ABS's 126, 270, 8519 & Sw/gear 12306/4 and CB 7 Back feeds installed Jumpers repaired LV fuses at Transformer 391 opened for livening Power restored at 12:29 LV Fuses at Transformer closed 12:40 Feeder Restored to normal configuration SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1548 |  | JE24043972 | unknown TAWERA ROAD,Mangatainoka,Pahiatua | Western | RUAWHATA | 2024-12-02 | 9:23 | 2024-12-02 | 9:56 | 0.00045499 | 1.3795e-05 | 5 | 165 | Unplanned | WILDLIFE - BIRD | Fuses Location: T7/501 No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 09:55 Cause: BIRD Weather (wind/rain): CALM Follow up required (select advisory)? FULL POWER | .
1549 |  | JE24044040 | 1807 KAHUTARA ROAD,KAHUTARA,FEATHERSTON | Western | KUMENGA | 2024-12-02 | 11:28 | 2024-12-02 | 13:03 | 0.00026285 | 2.759e-06 | 1 | 95 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: 7302 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 13:03 Cause: UNKNOWN Weather (wind/rain): OVERCAST Follow up required (select advisory)? FULL POWER waiting for emap update | .
1550 |  | JE24044065 | 942 COACH ROAD,PONGAKAWA,TE PUKE | Eastern | ROTOEHU | 2024-12-02 | 11:35 | 2024-12-02 | 15:00 | 0.00093331 | 0.00011864 | 42 | 338 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 4 Protection flags (nil where none): Nil CAUSE: Burnt off jumper Location: ABS SE7-014 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4, No Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: ABS SE7-014 off loaded. Jumper, lug and insulator repaired under Live Line permit issued to Kenny Douglas. Network restored. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1551 |  | JE24044094 | 723 TE ORE ORE BIDEFORD ROAD,BIDEFORD,MASTERTON | Western | BIDEFORD | 2024-12-02 | 15:12 | 2024-12-02 | 17:48 | 0.036327 | 0.00031728 | 115 | 13167 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV REC C217/2 Protection flags (nil where none): A,B,C ph E/F CAUSE: unknown Location: Nil Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: Cursory Weather (wind/rain): calm LFI (Y/N + Comments): N Follow up Required (select advisory)? N Additional fault restoration comments: Line was patrolled and sectionalized and no fault was found. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1552 |  | JE24041041 | 635 1, MARTON, MARTON, 4787 | Western | RACECOURSE | 2024-12-01 | 9:00 | 2024-12-01 | 12:36 | 0.010722 | 4.9661e-05 | 18 | 3886 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace multiple defected 11KV X-Arms between poles 809933 & 806025 & remove ABS 4241 | .
1553 |  | JE24041625 | 120 LOVEGROVE ROAD, TE AROHA, TE AROHA, 3393 | Eastern | MCCABE ROAD | 2024-12-01 | 9:04 | 2024-12-01 | 14:49 | 0.063622 | 0.00018485 | 67 | 23060 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Poles C341 and C13154. Replace ABS IC2500 on replacement pole for C13154. | .
1554 |  | JE24043890 | 2062 MORRINSVILLE-WALTON ROAD,RICHMOND DOWNS,WALTON | Eastern | PIAKOITI RD | 2024-12-01 | 1:46 | 2024-12-01 | 6:25 | 0.04451 | 0.00033935 | 123 | 16133 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Sectionliser 13065 Protection flags (nil where none): C Phase EF - OC CAUSE: Termination Cross Arm Broken Location: Pole H1799 Temp generation (state details when used): NIL PERFORMANCE DETAIL DNO (number or state No): NIL Circuit patrolled and type: Cursory Weather (wind/rain): Fine LFI (Y/N + Comments): LFI Activated in field - out of scan on SCADA So no remote visibility Follow up Required (select advisory)? NIL Additional fault restoration comments: LV Line Clash - Transformer TC992 Left Isolated Inspection done after line clash and full power restored to all customers | .
1555 |  | JE24043893 | 151 BEACH ROAD,KATIKATI,KATIKATI | Eastern | TETLEY ROAD | 2024-12-01 | 6:37 | 2024-12-01 | 8:20 | 0.0014229 | 1.3795e-05 | 5 | 516 | Unplanned | WILDLIFE - BIRD | Fuses Location: FABS IP464 No. Fuses: 2 Fuse Amp Size: 20A TIME CLOSED: 08:20 Cause: Bird Strike Weather (wind/rain): Rain Follow up required (select advisory)? No | .
1556 |  | JE24043894 | 200 PARIHAKA ROAD,PUNGAREHU,OPUNAKE | Western | PARIHAKA | 2024-12-01 | 8:41 | 2024-12-01 | 10:35 | 0.0021968 | 1.9313e-05 | 7 | 796 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faultman found this job is a actually off the child job attached as this customer has multiple properties. Faultman found a damaged and burnt cross arm due to cracked insulator on pole 710468 due to deuteriation. Line was isolated at Fuses 6635 to replace the cross arm & hardware. | .
1557 |  | JE24043920 | 372 MORRINSVILLE-TAHUNA ROAD,MORRINSVILLE,MORRINSVILLE | Eastern | HORRELLS RD | 2024-12-01 | 20:15 | 2024-12-01 | 21:09 | 0.00083905 | 0.00020692 | 75 | 304 | Unplanned | WILDLIFE - OTHER | First Outage - Odd Voltages 205V - 217V 226V - Reload reliven to prove Fuses not at fault. Fuses Location: Transformer TP835 No. Fuses: 3 Fuse Amp Size: NIL TIME CLOSED: Opened - 20:15 - Closed 20:26 Cause: - Bad LV Voltage - Fault Finding Weather (wind/rain): Fine Further Outage - Found Regulator Set 13387 Faulty Break Make Between PKO 1 and 3 - to Isolate Regulator Set - 20:57 - Outage Isolate Reg Set - 21:05 - 21:09 Reg Set 13387/1 Bypassed - Boaz Forwarded onto Hub requirement for Tech In morning to investigate - Regulator set has no Power at Control Box, Tap Settings 1 tank is on tap 12 the other two tanks are on tap 2 Tested LV Voltage after bypass of regulator and have returned to within Regulated Standards. Also to Note Recloser 9599 Voltage indications are transposed, While the outage between Reg Set and Rec 9599 Was showing Voltage on incorrect side. 04/12/24 - Sam Jones found the the controller is dead and will not start up, on investigation found that the control cables had been damaged by rodents who had chewed through the control cables. Sam tried to fire up the controller but it did not work at all. There has been a DNO raised for the replacement of the controller and cables. DNO2412003 | .
1558 |  | JE24043841 | 57 MATAPIHI ROAD,MOUNT MAUNGANUI,TAURANGA | Eastern | MATAPIHI RD | 2024-11-30 | 5:53 | 2024-11-30 | 6:58 | 0.047933 | 0.0008001 | 290 | 17374 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: CB 2 Protection flags (nil where none): Phase B, C OC CAUSE: Bird Strike Location: Fuses SD4-110, Pole 486295 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Rain LFI (Y/N + Comments): None Follow up Required (select advisory)? No Additional fault restoration comments: Replaced two x 20A Fuses and barrels at Fuses SD4-110 and relivened.-06:58 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): No Circuit that tripped: N/A DTF (KM):N/A | .
1559 |  | JE24043853 | 7337 2 ,PAEROA,PAEROA | Eastern | SHAW AVE | 2024-11-30 | 11:10 | 2024-11-30 | 14:05 | 0.011868 | 7.1733e-05 | 26 | 4302 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: Recloser 14793 Protection flags (nil where none): Phase A-OC CAUSE: Cracked Insulator Location: Pole N2555 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Replaced insulator and binders at Pole N2555 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): N/A Circuit that tripped: N/A DTF (KM):N/A | .
1560 |  | JE24043857 | 297A No 1 Line, Tauherenikau, 5771 | Western | DAIRY FACTORY | 2024-11-30 | 18:10 | 2024-11-30 | 18:18 | 3.9637e-05 | 5.5179e-06 | 2 | 14 | Unplanned | THIRD PARTY INTERFERENCE - VANDALISM/THEFT | Isolated at Trf Fuses T3706 to replace stolen & missing Earthing Conductor .up the pole and in conduit. Power Off 18:10, Power ON 18:17 | .
1561 |  | JE24043863 | 224 HETHERINGTON ROAD,WHANGAMATA,WHANGAMATA | Eastern | HETHERINGTON RD | 2024-11-30 | 17:49 | 2024-11-30 | 21:31 | 0.21041 | 0.00094908 | 344 | 76265 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Incident Number F4098879 REGULATORY INFORMATION Voltage & Device ID: Sectionliser 13503 Protection flags (nil where none): Phase COC, EF-OC CAUSE: Broken 11kV Pin Insulator Location: Pole R1032 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): NIL Circuit patrolled and type: Cursory - Call From Fire Comms Weather (wind/rain): Fine LFI (Y/N + Comments): NIL Follow up Required (select advisory)? Additional fault restoration comments: | .
1562 |  | JE24043871 | 53 ROTOKOHU ROAD,PAEROA,PAEROA | Eastern | TIROHIA-KARANGAHAKE | 2024-11-30 | 21:20 | 2024-12-01 | 1:33 | 0.034497 | 0.00030073 | 109 | 12504 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kv Paeroa CB 3 Protection flags (nil where none): B - C Phase OC - Ground CAUSE: Possum at Pole N1230 Burnt Line Down- Tree branch through lines Location: Pole N13220 - Pole N1230 Temp generation (state details when used): NIL PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: Cursory Weather (wind/rain): Rain LFI (Y/N + Comments): Y SAP 13703102 - Indicated Wrong Direction of Fault B - C Fault One - Indicatons where all christmas tree one green and one red Needs investigation Follow up Required (select advisory)? No Additional fault restoration comments: Removed tree branch at pole N13220 and repaired lines, Removed possum at Pole N1230 Returning In Morning to Install Possum Guards on Pole N1230 - Leave 2R Open Till then Possum guard installed 12:05 Hrs | .
1563 |  | JE24040917 | 28 HAKAO ROAD, TE PUNA, TAURANGA, 3171 | Eastern | WAIPUNA | 2024-11-29 | 10:10 | 2024-11-29 | 13:25 | 0.014282 | 7.7251e-05 | 28 | 5177 | Planned | PLANNED SHUTDOWN - MAINTENANCE | RMU 11kv oil maintenance - 9302/1/2/3 | .
1564 |  | JE24040946 | 595 WARDS LINE, MORRISONS BUSH, GREYTOWN, 5794 | Western | TAWAHA | 2024-11-29 | 9:27 | 2024-11-29 | 13:36 | 0.0055076 | 2.2072e-05 | 8 | 1996 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace transformer site t2358 with new structure and 15 kva 3 phase transformer | .
1565 |  | JE24040961 | 1284 RANGITIKEI LINE, NEWBURY, PALMERSTON NORTH, 4475 | Western | TE ARAKURA | 2024-11-29 | 9:00 | 2024-11-29 | 14:45 | 0.094695 | 0.00027866 | 101 | 34323 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove 11kV ABS D89 at Pole P33095. Replace Pole P33095. Install Manual ENTEC LBS 10911/2 on Pole site with Source side Solid Links 10911/4. | .
1566 |  | JE24041011 | 5340 SOUTH ROAD, OAONUI, OPUNAKE, 4681 | Western | SOUTH RD NGARIKI | 2024-11-29 | 9:16 | 2024-11-29 | 14:04 | 0.030901 | 0.0001076 | 39 | 11200 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace poles 713062, 713063, 713064, 713066, 713068, 713069, 713070, 713073, 713074, 713075 & 713076. remove 3 x spans of redundant lv between poles 713061 & 713064 | .
1567 |  | JE24041346 | 99 TARATA ROAD, INGLEWOOD, INGLEWOOD, 4387 | Western | KAIMATA | 2024-11-29 | 9:01 | 2024-11-29 | 15:03 | 0.014987 | 4.1384e-05 | 15 | 5432 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace crossarms at poles 760520,760519,760518,760517,760516,760515,760514,760512. | .
1568 |  | JE24041414 | 125 WHAKATOMOTOMO ROAD, PIRINOA, FEATHERSTON, 5772 | Western | BURNSIDE | 2024-11-29 | 9:31 | 2024-11-29 | 14:51 | 0.034428 | 0.0001076 | 39 | 12479 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT line repairs and vegetation cutting Downer are doing line repairs, Vegetation cutting is past pole 440464 | .
1569 |  | JE24041700 | 61 PIRAUNUI ROAD, MANAWARU, TE AROHA, 3391 | Eastern | NGARUA | 2024-11-29 | 8:30 | 2024-11-29 | 15:11 | 0.0011624 | 8.2769e-06 | 3 | 421 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV poles C266 and C1919 with a new 11m concrete busck via liveline procedure GB-12 Transformer TC6534 has no ICP against it No OMS job created Job for TC3023 was done de energised due to pole Deteriating further & not safe to be carried out live line. Outage JE24043816 created for this | .
1570 |  | JE24042883 | 38B CATHERINE CRESCENT, WHITIANGA, WHITIANGA, 3510 | Eastern | COOK DRIVE | 2024-11-29 | 11:03 | 2024-11-29 | 11:15 | 0.0085259 | 0.00072561 | 263 | 3090 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Tap change on TC3728 for PV solar generation voltage issues | .
1571 |  | JE24043314 | 207 BUSH GULLY ROAD, HINAKURA, MARTINBOROUGH, 5784 | Western | COLOGNE ST | 2024-11-29 | 13:16 | 2024-11-29 | 14:01 | 0.0047126 | 0.00010484 | 38 | 1708 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | All work to be done under urgent NAPA E00164 today. MDP Isolated at ABS S535, Replaced broken binder and installed breast block at pole 841963 Full power restored | .
1572 |  | JE24043316 | 1974 HINEKURA ROAD, HINAKURA, MARTINBOROUGH, 5784 | Western | COLOGNE ST | 2024-11-29 | 9:48 | 2024-11-29 | 11:25 | 0.0010732 | 1.1036e-05 | 4 | 389 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | All work to be done today under urgent NAPA E00163. MDP urgent outage, Isolated at Fuses 7374 Cross Arms replaced at Pole 816727, Full power restored | .
1573 |  | JE24043685 | 259 BROOKLYN ROAD,CARTERTON,CARTERTON | Western | TAVERNER ST | 2024-11-29 | 8:21 | 2024-11-29 | 8:40 | 5.4444e-05 | 2.759e-06 | 1 | 20 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Damaged / deteriorated jumpers between TFR T794 LV Bushings and Fuse boxes due to age De-energised TFR T794 at HV Fuses replaced Jumpers between TFR T794 LV Bushings and Fuse boxes Full power restored | .
1574 |  | JE24043705 | unknown KAIWHATA ROAD,Kaiwhata,Rural | Western | BLAIRLOGIE | 2024-11-29 | 12:23 | 2024-11-29 | 15:05 | 0.0013402 | 8.2769e-06 | 3 | 486 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Broken Binder / floating conductor at Pole 444963 Faultman found 2 x Fuses Blown at Fuses 7139 Isolated Fuses 7139 Line patrolled, Broken Binder / floating conductor found Faultman replaced Insulators at Pole 444963 with Clamp top type insulators (as ongoing problem with the binders breaking on this pole / line) 2 x 6 Amp Fuses replaced and Full power restored | .
1575 |  | JE24043773 | 5722 STATE HIGHWAY 26, MANGAITI | Eastern | SPRINGDALE | 2024-11-29 | 14:35 | 2024-11-29 | 16:53 | 0.011776 | 8.5528e-05 | 31 | 4268 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION CAUSE: 11kV Insulator Broken off Pin - at Pole C3179 Location: Pole 3179 Isolated At ABS 561 | .
1576 |  | JE24043784 | 13 TOWAI ROAD,WAIONE,DANNEVIRKE | Western | HOROEKA | 2024-11-29 | 7:32 | 2024-11-29 | 11:34 | 0.0073317 | 3.0349e-05 | 11 | 2657 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | Fuses Location: v13 No. Fuses: 2 Fuse Amp Size: 6a TIME CLOSED: 11:34 Cause: wind line in trees stuck on pinecone Weather (wind/rain): windy Follow up required (select advisory)? line stuck in trees on pinecone FM cut branch and cleared fault 2R for line patrol and cutting tree | .
1577 |  | JE24043791 | unknown HOMEWOOD ROAD,Homewood,Rural | Western | BLAIRLOGIE | 2024-11-29 | 13:43 | 2024-11-29 | 17:43 | 0.00066322 | 2.759e-06 | 1 | 240 | Unplanned | WILDLIFE - BIRD | Fuses Location: 8164 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 17:43 Cause: Bird strike Weather (wind/rain): calm Follow up required (select advisory)?n Line patrolled | .
1578 |  | JE24043838 | 58 MATAKOKIRI DRIVE,TAURIKO,TAURANGA | Eastern | PYES PA | 2024-11-29 | 23:20 | 2024-11-30 | 0:28 | 0.054485 | 0.001465 | 531 | 19748 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 1 Protection flags (nil where none): B phase E/F CAUSE: Suspect Possum Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursery Weather (wind/rain): Calm LFI (Y/N + Comments): Never Operated Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1579 |  | JE24040686 | 685 2 ROAD, TE PUKE, TE PUKE, 3182 | Eastern | ROADS | 2024-11-28 | 10:01 | 2024-11-28 | 16:12 | 0.11858 | 0.00032004 | 116 | 42981 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv ABS IP14 with new ENTEC Sectionaliser 14857 with on site 1kva transformer. | .
1580 |  | JE24040796 | 159 WAIRAKEI AVENUE, PAPAMOA BEACH, TAURANGA, 3118 | Eastern | GOLDEN SANDS | 2024-11-28 | 9:30 | 2024-11-28 | 13:27 | 0.066097 | 0.00027866 | 101 | 23957 | Planned | PLANNED SHUTDOWN - MAINTENANCE | RMU 11kV oil maintenance - 9019/1/2/3/4/5 | .
1581 |  | JE24040804 | 108 WAIHEKAU ROAD, TE AROHA WEST, TE AROHA, 3391 | Eastern | MAUNGAKAWA ROAD | 2024-11-28 | 8:46 | 2024-11-28 | 14:06 | 0.021186 | 6.6215e-05 | 24 | 7679 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV & 400V x-arms, hardware, stays and earthing at poles C132, C129, C123, C117, C12600, C113, C111, C110 & C102. | .
1582 |  | JE24040855 | 700 PAHIATUA AOKAUTERE ROAD, AOKAUTERE, PALMERSTON NORTH, 4471 | Western | AOKAUTERE | 2024-11-28 | 8:48 | 2024-11-28 | 13:56 | 0.16467 | 0.00053524 | 194 | 59685 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT: Multiple sites re-sagging and replacing hardware. Cut vegetation between poles P21429 - P21428. | .
1583 |  | JE24040922 | 75 WALLACE PLACE, WESTOWN, NEW PLYMOUTH, 4310 | Western | BREAKWATER RD | 2024-11-28 | 8:45 | 2024-11-28 | 14:42 | 0.31332 | 0.00088011 | 319 | 113565 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 700571 and replace 11kV ABS 255 with Entec sectionaliser 12758/2 and solid links 12758/4. To be 'open ' point. | .
1584 |  | JE24040937 | 1 DORSET AVENUE, WESTOWN, NEW PLYMOUTH, 4310 | Western | BROOKLANDS 14 | 2024-11-28 | 23:15 | 2024-11-29 | 0:13 | 0.049649 | 0.00085528 | 310 | 17996 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Close 11kV line break at pole 700565 once new entec sectionaliser 12758 is installed. | .
1585 |  | JE24040962 | 945 WIREMU ROAD, OPUNAKE, OPUNAKE, 4681 | Western | IHAIA RD | 2024-11-28 | 9:18 | 2024-11-28 | 16:04 | 0.015679 | 3.8625e-05 | 14 | 5683 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace pole 715074 with new tx structure and move tx T1150 to this pole. replace surge arrestors. remove lv arms, replace hv arms & straighten poles @ 715076, 715075 & 715072. replace pole 715061. | .
1586 |  | JE24041510 | 114 WAIHI BEACH ROAD, WAIHI, WAIHI, 3681 | Eastern | ATHENREE | 2024-11-28 | 9:01 | 2024-11-28 | 23:23 | 0.10586 | 0.0058242 | 1173 | 38371 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 33kV Crossarms Waihi Beach Rd | .
1587 |  | JE24042491 | 201 RANGIURU ROAD, RANGIURU, TE PUKE, 3188 | Eastern | TE MATAI RD | 2024-11-28 | 8:30 | 2024-11-28 | 13:14 | 0.013782 | 4.9661e-05 | 18 | 4995 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove existing HV cables off poles & transfer to new RMU's. 1) 221088 joint existing cable to new UG Cable, term to RMU3 14975/4 2) 221092 joint existing cable to new UG Cable, term to RMU4 14980/2 3) Transfer load from OH TX TE6-025 to GM TX TP4513. | .
1588 |  | JE24043284 | 140 SOUTH SOLDIERS SETTLEMENT ROAD, LAKE RESERVE, FEATHERSTON, 5771 | Western | SOUTH FEATHERSTON | 2024-11-28 | 10:02 | 2024-11-28 | 11:00 | 0.0073186 | 0.00012691 | 46 | 2653 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | HV Shut required Tom will scope all the affected poles and arrange it under 1x shut. Advised FM to contact Control NAPA E00161 | .
1589 |  | JE24043305 | 1206 TE WHARAU ROAD, MASTERTON, 5883 | Western | WESTMERE GLADSTONE | 2024-11-28 | 9:30 | 2024-11-30 | 13:07 | 0.093133 | 0.00040005 | 145 | 33756 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Scope has been done and work will be completed under urgent work, E00162 on the 28/11/2024 from 09:30 - 15:00. MDP Urgent work completed. Reconnected brackets to eye bolts at poles 453396 and 452102 | .
1590 |  | JE24043525 | 91 OKOROIRE ROAD,TIRAU,TIRAU | Eastern | OKOROIRE | 2024-11-28 | 7:25 | 2024-11-28 | 9:41 | 0.0032233 | 4.4143e-05 | 16 | 1168 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Arcing at Fuses FC2323 Fuses opened to Check, Jumper broke away at Fuses Back Feeds installed Via Sec 977 & ABS 1116 Isolated at ABS's 2505 & 2629 Jumper Repaired Power restored | .
1591 |  | JE24043585 | 545 HOMEWOOD ROAD,RIVERSDALE BEACH,MASTERTON | Western | BLAIRLOGIE | 2024-11-28 | 12:00 | 2024-11-28 | 14:42 | 0.00044767 | 2.759e-06 | 1 | 162 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: 7143 No. Fuses: 2 Fuse Amp Size: 8a TIME CLOSED: 14:42 Cause: unKnown Weather (wind/rain): windiy Follow up required (select advisory)? | .
1592 |  | JE24043599 | 34 PONGAKAWA BUSH ROAD,PONGAKAWA,TE PUKE | Eastern | ROTOEHU | 2024-11-28 | 10:33 | 2024-11-28 | 13:14 | 0.003544 | 2.2072e-05 | 8 | 1285 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: SF7-012 No. Fuses: 2 Fuse Amp Size:10A TIME CLOSED: 13:13 Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)?N | .
1593 |  | JE24043619 | 132 MANGAMAIRE ROAD, PAHIATUA, 4987 | Western | MANGAMAIRE | 2024-11-28 | 16:07 | 2024-11-28 | 16:45 | 0.0021244 | 5.5179e-05 | 20 | 770 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Replaced broken binder at Pole P29393 Cause: Aged Isolation: Fuses R48 | .
1594 |  | JE24043629 | 2008 WIREMU ROAD, OKATO | Western | PARIHAKA | 2024-11-28 | 17:44 | 2024-11-28 | 19:36 | 0.005906 | 5.242e-05 | 19 | 2141 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FM confirmed lines damaged Crew on Route to carry out repairs Insulators damaged at Regulator 12293 Isolated at ABS's 6434, NG408 & 12270/1 and Links 12270/4Replaced 6 Deadends at the regulators as they had Steel thumballs in causing Rusty | .
1595 |  | JE24043637 | 67 ROWE ROAD,OHAUITI,TAURANGA | Eastern | OHAUITI RD | 2024-11-28 | 15:59 | 2024-11-28 | 17:23 | 0.00023324 | 2.759e-06 | 1 | 85 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: TP278 No. Fuses: 2 Fuse Amp Size: 2Amp TIME CLOSED: 17:23 Cause: Unknown Weather (wind/rain): Fine Follow up required (select advisory)? No | .
1596 |  | JE24043667 | 199 KUAOTUNU WHAREKAHO ROAD,KUAOTUNU,WHITIANGA | Eastern | KUAOTUNU | 2024-11-28 | 19:56 | 2024-11-28 | 21:45 | 0.0059987 | 5.5179e-05 | 20 | 2174 | Unplanned | WILDLIFE - BIRD | Fuses Location: DTX TC1330 No. Fuses: 2 x 10A 3 x 160A Fuses Fuse Amp Size: 10A TIME CLOSED: 21:44 Cause: Bird in LV Circuit caused Flashover Weather (wind/rain): fine still Follow up required (select advisory)? | .
1597 |  | JE24043674 | KAIHERE | Eastern | KAIHERE | 2024-11-28 | 22:30 | 2024-11-29 | 0:07 | 0.62128 | 0.0093501 | 3389 | 225186 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: Total Kerepehi Sub 11kV Bus Fault Protection Operated Protection flags (nil where none): B Phase E/F CAUSE: Under invest , Relays being downloaded ASAP Location: Kerepehi Substation Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Calm LFI (Y/N + Comments): Nil Follow up Required (select advisory)? Additional fault restoration comments: CB 17 & CB 19 Tripped on a B Phase Earth Fault, Total Loss of Supply to Substation SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Kerepehi Circuit that tripped: 11kV CB 17 & CB 19 DTF (KM): | .
1598 |  | JE24038569 | TURAKINA | Western | TURAKINA | 2024-11-27 | 8:38 | 2024-11-27 | 13:44 | 0.022775 | 7.4492e-05 | 27 | 8255 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles at 794734(and ABS), 794695, 794692, 794694,794696 and replace xarms from and including 794734 to 794696.LV Reconductoring 794734,794692,794693,794694,794695,794696. | .
1599 |  | JE24040647 | 249 OHINEWAI ROAD, KAIHERE, MORRINSVILLE, 3373 | Eastern | KAIHERE | 2024-11-27 | 9:00 | 2024-11-27 | 12:31 | 0.0017427 | 8.2769e-06 | 3 | 632 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 1 x HV termination pole O14268 and straighten poles 321466 and 321872 | .
1600 |  | JE24040652 | 2476 TAHUNA-OHINEWAI ROAD, HOE-O-TAINUI, OHINEWAI, 3784 | Eastern | HOE-O-TAINUI | 2024-11-27 | 10:05 | 2024-11-27 | 12:41 | 0.0017253 | 1.1036e-05 | 4 | 625 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Repairing insulator stand and installing EOL earth on pole K13025 and installing EOL earth and pineapple insulators on pole K13024 | .
1601 |  | JE24040723 | 155 BOUCHER AVENUE, TE PUKE, TE PUKE, 3119 | Eastern | MOEHAU ST | 2024-11-27 | 10:00 | 2024-11-27 | 14:00 | 0.050498 | 0.0043426 | 1574 | 18303 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - SE5-256/SE5-252/SE5-250/SE5-254 Switching error involved with this Napa 24043431. Safety Manager for other job | .
1602 |  | JE24040727 | 1155 OROPI ROAD, OROPI, TAURANGA, 3173 | Eastern | OHAUITI RD | 2024-11-27 | 9:02 | 2024-11-27 | 15:30 | 0.18749 | 0.00048282 | 175 | 67955 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 211094 to 212810 (TE4-104) | .
1603 |  | JE24040739 | 745 RONGOTEA ROAD, RONGOTEA, PALMERSTON NORTH, 4476 | Western | KOPANE | 2024-11-27 | 8:52 | 2024-11-27 | 14:30 | 0.18532 | 0.00055731 | 202 | 67169 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Pole P44669. Install ENTEC LBS 10903 on pole Pole site P44669 with Solid Links. Commission ENTEC LBS 10903 | .
1604 |  | JE24040838 | 939 PALMER ROAD, KAPONGA, HAWERA, 4679 | Western | DUTHIE RD | 2024-11-27 | 9:31 | 2024-11-27 | 15:29 | 0.0042586 | 0.00014347 | 26 | 1544 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To be linked in with NAPA 111223 - 11kV line breaks to be installed to pole 731747 on the side of 731748. Once pole chip repair is complete at 940997/940996 and 33kv works complete line is to be reinstated at end of the day | .
1605 |  | JE24040936 | 4552 MASTERTON CASTLEPOINT ROAD, TINUI, MASTERTON, 5889 | Western | CASTLEPOINT | 2024-11-27 | 8:36 | 2024-11-27 | 15:58 | 0.28741 | 0.0018071 | 448 | 104174 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Maintenance on 11kv poles and hardware and tree work at multiple sites on castlepoint feeder | .
1606 |  | JE24041010 | 619 TARATA ROAD, KAIMATA, INGLEWOOD, 4387 | Western | KAIMATA | 2024-11-27 | 9:00 | 2024-11-27 | 14:43 | 0.015118 | 4.4143e-05 | 16 | 5479 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 760601,760603. Replace crossarms at poles 760599,760600,760602,760604,760606. | .
1607 |  | JE24041621 | 376 STARKEY ROAD, MORRINSVILLE, MORRINSVILLE, 3371 | Eastern | KIWITAHI | 2024-11-27 | 9:30 | 2024-11-27 | 15:14 | 0.17871 | 0.00052696 | 191 | 64774 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RETAIN ABS IP615 AND INSTALL NOJA 14929/2 & SOURCE SIDE LINKS 14929/4 REMOVE ABS IP616 AND INSTALL ENTEC 14937/2 & SOURCE SIDE LINKS 14937/4 | .
1608 |  | JE24043337 | 2033 WATERSHED ROAD,TAIHAPE,TAIHAPE | Western | MATAROA A | 2024-11-27 | 12:00 | 2024-11-27 | 14:10 | 0.0050162 | 3.8625e-05 | 14 | 1818 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faultman reported line is ok for tonight but will return tomorrow 27/11 at mid day to isolate line and make repair as customers are shearing, Faultman has spoken to the customers and they are happy with the mid day shut. 27/11/2024 Isolated at Fuses 1442 Power Off 12:00 Lines repaired Power restored 14:10 | .
1609 |  | JE24043384 | 30 JOLL STREET,WAITARA,WAITARA | Western | BLAKE ST | 2024-11-27 | 5:44 | 2024-11-27 | 7:27 | 0.0017047 | 1.6554e-05 | 6 | 618 | Unplanned | WILDLIFE - BIRD | Fuses Location: 5137 No. Fuses: 2 Fuse Amp Size: 6a TIME CLOSED: 0726 Cause: Suspected bird strike Weather (wind/rain): Calm Follow up required (select advisory)? | .
1610 |  | JE24043475 | unknown PA VALLEY ROAD,Alfredton,Rural | Western | RONGOMAI | 2024-11-27 | 14:55 | 2024-11-27 | 20:32 | 0.00093083 | 2.759e-06 | 1 | 337 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole & Crossarm will need to be replaced in near future. 2R left open to make repairs 06/03/2025 - Update from the hub - Wiremu to follow up with Anthony Rowden . MDP 21/03/2025 - As per SMC spreadsheet. Planned to be replace 28th March. DR 27/03/2025 - Update - Planned to be replace 28th March. MDP 14/04/2025 - Linked to the planned outage job NAPA 121021 on the 23/04/2025. MDP | .
1611 |  | JE24038050 | 113 REYNOLDS ROAD, RATANA, WANGANUI, 4581 | Western | TURAKINA | 2024-11-26 | 8:31 | 2024-11-26 | 13:35 | 0.015143 | 4.9661e-05 | 18 | 5489 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles and xarms from and including 794699 to 794711.Install TEMP ABS TEMP124 (at pole 794710). | .
1612 |  | JE24040134 | 16 HARRISON HILL ROAD, AOKAUTERE, PALMERSTON NORTH, 4471 | Western | AOKAUTERE | 2024-11-26 | 8:31 | 2024-11-26 | 15:19 | 0.028156 | 6.8974e-05 | 25 | 10205 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT: Replace crossarms on P21382. Re-sag 11kV lines at P26663. Clear vegetation at multiple sites | .
1613 |  | JE24040201 | 289 FABIANS ROAD, MORRISONS BUSH, GREYTOWN, 5794 | Western | PONATAHI | 2024-11-26 | 9:18 | 2024-11-26 | 15:03 | 0.060838 | 0.00017657 | 64 | 22051 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace multiple defects | .
1614 |  | JE24040300 | 1051 TAHUROA ROAD, MORRINSVILLE, MORRINSVILLE, 3371 | Eastern | KIWITAHI | 2024-11-26 | 9:28 | 2024-11-26 | 13:41 | 0.066341 | 0.0002621 | 95 | 24045 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REMOVE ABS IC779, AND INSTALL ENTEC 14931/2 AND SOURCE SIDE LINKS 14931/4 AT POLE I1740 | .
1615 |  | JE24040333 | 5429 SOUTH ROAD, RAHOTU, OPUNAKE, 4681 | Western | SOUTH RD NGARIKI | 2024-11-26 | 9:23 | 2024-11-26 | 15:53 | 0.068722 | 0.00017657 | 64 | 24909 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 712395, 713051, 713053, 713054, 713058, 713059, 713060, 713061 & 713077. Install temp ABS TEMP049 at pole 713077. | .
1616 |  | JE24040401 | 2676 LAKE FERRY ROAD, PIRINOA, FEATHERSTON, 5772 | Western | PIRINOA | 2024-11-26 | 9:47 | 2024-11-26 | 12:59 | 0.0010615 | 5.5179e-06 | 2 | 385 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace S576 with front mounted automated entec switch | .
1617 |  | JE24040557 | 338 OREIPUNGA ROAD, MAUNGATAUTARI, CAMBRIDGE, 3494 | Eastern | CAMBRIDGE RD TIRAU | 2024-11-26 | 9:48 | 2024-11-26 | 15:49 | 0.12159 | 0.00033659 | 122 | 44070 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace HV arm on Poles 877861 877863 D1096 263880 D0958, replace pole D1075 and carry out ABS maintenance on Fused ABS IP547 | .
1618 |  | JE24040600 | 91A WESTERN LAKE ROAD, WESTERN LAKE, FEATHERSTON, 5773 | Western | REVANS ST | 2024-11-26 | 9:00 | 2024-11-26 | 14:35 | 0.059189 | 0.00017657 | 64 | 21453 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Change 11kv arms between 798600 & 798399 | .
1619 |  | JE24040658 | 1 DORSET AVENUE, WESTOWN, NEW PLYMOUTH, 4310 | Western | BROOKLANDS 14 | 2024-11-26 | 23:15 | 2024-11-27 | 0:06 | 0.043633 | 0.00085528 | 310 | 15815 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install a temporary line break at pole 700565 to allow the replacement of ABS 255 on the 28th November. | .
1620 |  | JE24040783 | 21 SEDDON STREET, TE PUKE, TE PUKE, 3119 | Eastern | MOEHAU ST | 2024-11-26 | 9:50 | 2024-11-26 | 13:49 | 0.05611 | 0.00078079 | 283 | 20337 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kV oil maintenance - 9433/1/2/3 | .
1621 |  | JE24042739 | 2914 TURAKINA VALLEY ROAD, HUNTERVILLE, HUNTERVILLE, 4781 | Western | HUNTERVILLE 22KV | 2024-11-26 | 9:49 | 2024-11-26 | 14:37 | 0.0031704 | 1.1036e-05 | 4 | 1149 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace defected 11KV X-Arm on pole 807347 raised by Helicopter Pole Topography | .
1622 |  | JE24042874 | 152 RANGIURU ROAD, RANGIURU, TE PUKE, 3188 | Eastern | TE MATAI RD | 2024-11-26 | 8:30 | 2024-11-26 | 15:58 | 0.073034 | 0.00018485 | 67 | 26472 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install/Liven 6 x RMU: Sw/Gear 14970, 14968; 14975; 14980; 14985, 14966 & Transformerâ€™s TP4510, TP4506, TP4513. Remove 11kV Lines between Poles 221081, 221082 and 221072, 221073. P/M Transformers TE6-150 & TE6-167 to be replaced with G/M TX under new nbrs. Remove LV & tfr ICP's to new G/M TX. NB: P/M TX to remain on the poles until NAPA 115380 | .
1623 |  | JE24043231 | 5341 SH 2,TURUA,NGATEA | Eastern | NGATEA | 2024-11-26 | 6:00 | 2024-11-26 | 7:15 | 0.00020666 | 2.759e-06 | 1 | 75 | Unplanned | WILDLIFE - BIRD | Fuses Location: FP1670 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 07:15 Cause: Duck Strike Weather (wind/rain): windy Follow up required (select advisory)? | .
1624 |  | JE24043244 | recloser_C225:2 | Western | CASTLEPOINT | 2024-11-26 | 8:28 | 2024-11-26 | 11:23 | 0.13725 | 0.00087735 | 318 | 49746 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11KV Rec C225 Protection flags (nil where none): B & C Phase trip Flag CAUSE: Unknown Location: Unknown Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Fine LFI (Y/N + Comments): Yes but not working on Scada but working on site Paddock Side Flashing Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1625 |  | JE24043269 | 230 PAKARAKA ROAD,WAITOTARA,WANGANUI | Western | WAITOTARA | 2024-11-26 | 9:51 | 2024-11-26 | 11:46 | 0.00094941 | 8.2769e-06 | 3 | 344 | Unplanned | WILDLIFE - BIRD | Fuses Location: TX X96 No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 11:45 Cause: magpie Weather (wind/rain): overcast Follow up required (select advisory)? | .
1626 |  | JE24043270 | 2 NGAPEKE ROAD,WELCOME BAY,TAURANGA | Eastern | BRUCE RD | 2024-11-26 | 9:57 | 2024-11-26 | 11:30 | 0.0038446 | 4.1384e-05 | 15 | 1394 | Unplanned | WILDLIFE - BIRD | Fuses Location: SD4-479 No. Fuses: 2 Fuse Amp Size: 10a TIME CLOSED: 11:30 Cause: bird strike Weather (wind/rain): clear light wind Follow up required (select advisory)? | .
1627 |  | JE24043291 | 1458 PAHAOA ROAD, HINAKURA, MARTINBOROUGH, 5784 | Western | COLOGNE ST | 2024-11-26 | 12:27 | 2024-11-26 | 13:10 | 0.0010756 | 2.4831e-05 | 9 | 390 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Floating conductor at Pole 845647 Isolated at Fuses 7360 Put more dirty around Bottom of Pole as block was showing | .
1628 |  | JE24043294 | 820 CRAIGIE LEA ROAD, TE WHARAU, MASTERTON, 5883 | Western | WESTMERE GLADSTONE | 2024-11-26 | 13:01 | 2024-11-26 | 14:21 | 0.0024117 | 3.0349e-05 | 11 | 874 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Replace insulator at Pole 832215 Isolated at Fuses 7849 | .
1629 |  | JE24043302 | 347 WAITARA ROAD,HUIRANGI,WAITARA | Western | MAMAKU RD NO 1 33KV | 2024-11-26 | 10:47 | 2024-11-26 | 11:07 | 5.6697e-05 | 2.759e-06 | 1 | 21 | Unplanned | HUMAN ERROR - POTENTIAL SWITCHING ERROR | Switching Error during switching for NAPA 117490 FM open CB 3202, Not CB 3402 Power off 10:46 Power restored 11:07 CB 1292 dress open to create job | .
1630 |  | JE24043309 | 392C LUND ROAD,AONGATETE,KATIKATI | Eastern | KATIKATI | 2024-11-26 | 11:56 | 2024-11-26 | 13:00 | 0.00017699 | 2.759e-06 | 1 | 64 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: DTX TC1-029 Isolated for Safety No. Fuses: 3 Fuse Amp Size: 0 TIME CLOSED: Off 11:55 on 13:00 Cause: Safety Isolation to repair broken LV Conductor ( Private Service Line) Weather (wind/rain): windy Follow up required (select advisory)? | .
1631 |  | JE24043312 | 690 ALFREDTON ROAD,EKETAHUNA,EKETAHUNA | Western | RONGOMAI | 2024-11-26 | 13:28 | 2024-11-26 | 14:15 | 0.0018102 | 3.8625e-05 | 14 | 656 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Replaced King Bolt to Stay Stripes at pole 474116 Isolated at Fuses I44 | .
1632 |  | JE24043355 | 130 CANAL WEST ROAD,WAITAKARURU,THAMES | Eastern | MANGATARATA | 2024-11-26 | 18:15 | 2024-11-26 | 23:52 | 0.044465 | 0.00040833 | 94 | 16117 | Unplanned | VEGETATION - OUTSIDE ZONE | 11kV Rec RC24 Auto reclosed Trip flags: E/F 11kV Sec 14730/2 Tripped Tree through the lines on Church Rd. Temp line break cut to mitigate SAIDI impact at pole O4202. At Pole O13932 tree fell through lines, tree on road reserve, lines were repaired 10m x 16mm² HD Cu conductor 1 x HV pin arm complete assembly 12 x MST sleeves NDR to follow Switching incident occurred where the fault man did work on the O/H lines with no access permit. Instructions were given to apply earths at pole O4202 and report back and would then issue an access permit back, but the earths were applied, the the jumpers were cut, earths removed then I was informed that the work had already been done. The fault man reported back to me and admitted that he had made a mistake, I informed the fault man that this was the incorrect way to work on the network and compelled to report the incident. | .
1633 |  | JE24043357 | 1057 SOUTH ROAD,MOKOIA,HAWERA | Western | MANUTAHI | 2024-11-26 | 19:36 | 2024-11-26 | 23:26 | 0.0026735 | 2.4831e-05 | 9 | 969 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faultman found broken DDO's at transformer W1115, line was isolated at ABS WH191 & Links WH290/4 & 12290/4 to replace DDO's. While replacing DDO's Faultman tested transformer and found it to defective, transformer W1115 was isolated and line re-livened, transformer W1115 was replaced. | .
1634 |  | JE24043374 | unknown WHALES LINE,Marton,Marton | Western | LAKE ALICE | 2024-11-26 | 20:58 | 2024-11-26 | 22:05 | 0.0020248 | 3.0349e-05 | 11 | 734 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses 255 No. Fuses: 2 Fuse Amp Size: 8 TIME CLOSED: 22:05 Cause: Bird Strike Weather (wind/rain): calm Follow up required (select advisory)? N | .
1635 |  | JE24043379 | Tasman Sub - CB TA9 | Western | TE KIRI | 2024-11-26 | 21:59 | 2024-11-27 | 4:37 | 0.044368 | 0.00075044 | 272 | 16081 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB TA9 Protection flags (nil where none): DEF - E/F CAUSE: Car vs pole Location: 462032 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: N Weather (wind/rain): calm LFI (Y/N + Comments): N Follow up Required (select advisory)? N Additional fault restoration comments: Line was isolated at ABS's 6437 & TA985 to replace pole 462032 & hardware & a cross arm on pole 462061. ETA 30min given to Fire Service | .
1636 |  | JE24043730 | 30 MANUKA STREET, MATAMATA, MATAMATA, 3400 | Eastern | ELIZABETH ST | 2024-11-26 | 20:46 | 2024-12-01 | 15:39 | 0.038486 | 0.00044143 | 80 | 13949 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Repair 11kV cable fault on HV cable between FC2432 and TC3786. Remove temporary generation on completion. | .
1637 |  | JE24040046 | 2 COLOGNE STREET, MARTINBOROUGH, MARTINBOROUGH, 5711 | Western | NAPLES ST | 2024-11-25 | 9:00 | 2024-11-25 | 13:46 | 0.029138 | 0.00010208 | 37 | 10561 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace ABS S510 with new top mounted non automated Entec switch | .
1638 |  | JE24041195 | 1534A MASTERTON STRONVAR ROAD, WAINUIORU, MASTERTON, 5890 | Western | WERAITI | 2024-11-25 | 8:46 | 2024-11-25 | 15:23 | 0.10292 | 0.00025934 | 94 | 37305 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Vegetation cutting in Forestry between poles 827644 - 827645, 469254 - 827661 | .
1639 |  | JE24042262 | 106 MIDHURST STREET, KELVIN GROVE, PALMERSTON NORTH, 4470 | Western | STONEY CREEK | 2024-11-25 | 9:16 | 2024-11-25 | 16:18 | 0.07572 | 0.00017933 | 65 | 27445 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace P19943. Relocate Tx from pole P19833 to P19943. Remove pole P44693,ABS D46 and sleeve through conductor. Install links 10921 on Pole P19833 Replace LV between Poles P19833 & P19943 | .
1640 |  | JE24042936 | 63 WHEREWHERE ROAD, MOAWHANGO, TAIHAPE, 4792 | Western | MOAWHANGO | 2024-11-25 | 10:11 | 2024-11-25 | 10:47 | 0.00087859 | 2.4831e-05 | 9 | 318 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Repair spragged 11KV Conductor at pole 786360 reported by PoleTech | .
1641 |  | JE24043123 | recloser_C279:2 | Western | CHURCH ST | 2024-11-25 | 8:56 | 2024-11-25 | 12:22 | 0.050589 | 0.00087735 | 194 | 18336 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11KV Rec C279 Protection flags (nil where none): A & B Phase O/C CAUSE: Truck Hit Wires Location: Poles 829588 - 829589 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Called in by Customer Weather (wind/rain): Fine & Hot LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Made temp line Break so could get More people back on Repaired Fault Turned Power back off again to Close Line Break Times all on Paperwork SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1642 |  | JE24043218 | 137 GLOVER ROAD,HAWERA,HAWERA | Western | GLOVER RD WEST | 2024-11-25 | 18:49 | 2024-11-25 | 21:53 | 0.0081003 | 4.4143e-05 | 16 | 2936 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: Nil Tripping's Protection flags (nil where none): Nil CAUSE: Car vs Pole Location: 723580 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: Weather (wind/rain): windy LFI (Y/N + Comments): N Follow up Required (select advisory)? N Additional fault restoration comments: Car vs pole - reported by Police - Line was isolated at ABS's CA101, CA707, 8610 & CB 9, to replace the pole & hardware. | .
1643 |  | JE24043221 | 350 JUNCTION ROAD,BURGESS PARK,NEW PLYMOUTH | Western | BROOKLANDS 7 | 2024-11-25 | 17:26 | 2024-11-25 | 18:20 | 0.00014896 | 2.759e-06 | 1 | 54 | Unplanned | WILDLIFE - BIRD | Fuses Location: 1276 No. Fuses: 2 Fuse Amp Size: 3 Amp TIME CLOSED: 18:15 Cause: Bird strike Weather (wind/rain): Calm Follow up required (select advisory)? N | .
1644 |  | JE24041678 | 95 KAWEROA DRIVE, OMANAWA, TAURANGA, 3171 | Eastern | KAWEROA DR | 2024-11-24 | 9:30 | 2024-11-24 | 13:44 | 0.0028009 | 1.1036e-05 | 4 | 1015 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install automation retrofit kit on ABB Safelink 13555 | .
1645 |  | JE24043055 | 3 CORADINE STREET,MASTERTON,MASTERTON | Western | ESSEX ST | 2024-11-24 | 1:16 | 2024-11-24 | 6:38 | 0.057085 | 0.00019313 | 70 | 20691 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB C818 Protection flags (nil where none): Nil CAUSE: Car V pole Location: 318115 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: Not patrolled, F3 Weather (wind/rain): Calm LFI (Y/N + Comments): None Follow up Required (select advisory)? NDR to follow Additional fault restoration comments: Location: Pole 318115 - Old Pole 483110 Reported by Firecoms - Event number F4094110 1 x 11m pole 1 x HV pin cross arm complete assembly 1 x LV pin cross arm complete assembly SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1646 |  | JE24043061 | 3 HAUROTO ROAD,HAWERA,HAWERA | Western | KETEMARAE RD | 2024-11-24 | 5:35 | 2024-11-24 | 6:25 | 0.0015029 | 3.0349e-05 | 11 | 545 | Unplanned | WILDLIFE - BIRD | Fuses Location: WH831 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 06:24 Cause: Bird strike/line clash Weather (wind/rain): calm Follow up required (select advisory)?n Line patrolled | .
1647 |  | JE24043075 | 20 CENTENNIAL DRIVE,MOTUROA,NEW PLYMOUTH | Western | NGAMOTU RD | 2024-11-24 | 11:33 | 2024-11-24 | 12:44 | 0.00039118 | 5.5179e-06 | 2 | 142 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses 6923 No. Fuses: 2 Fuse Amp Size: 15 TIME CLOSED: 12:43 Cause: Bird Strike Weather (wind/rain): calm Follow up required (select advisory)? N | .
1648 |  | JE24043089 | unknown PUKE PUKE ROAD,Himatangi,Rural | Western | OROUA DOWNS | 2024-11-24 | 17:02 | 2024-11-24 | 18:31 | 0.0091108 | 0.00010208 | 37 | 3302 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Please check JE24043092 on completion Faultman found a line down at pole P20741 due to joint failure, line was isolated at Fuses L27 to repair the lines. | .
1649 |  | JE24042466 | 267 AWAHOU SOUTH ROAD, POHANGINA, ASHHURST, 4884 | Western | POHANGINA | 2024-11-23 | 9:00 | 2024-11-23 | 11:36 | 0.021026 | 0.00013519 | 49 | 7621 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: age What was replaced? rebind conductors Where was it replaced (pole/TX/pillar box)? Pole P11704 Is 2R required? Y 2R Y - What is the timeframe for repairs? Additional Info: HV Shut required LV Pin Insulator is OK just a little crack | .
1650 |  | JE24043002 | 31 LOCKINGTON ROAD,AONGATETE,unknown | Eastern | GRE3232-OMO62-AON82 33KV | 2024-11-23 | 11:30 | 2024-11-23 | 11:33 | 0.0056841 | 0.0024858 | 901 | 2060 | Unplanned | HUMAN ERROR - POTENTIAL WORKMANSHIP | REGULATORY INFORMATION Voltage & Device ID: CB 38 Protection flags (nil where none): Nil CAUSE: Tech testing Transformer T6 under Access Permit 117355-01 Location: AON Sub Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: N/A Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: NOC called TECH onsite and asked for cause of Trip and the safety status of crew on site and closed CB 38. CB tripped while TECH was carrying (Residual Earth Fault) tests on Transformer SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): No Circuit that tripped: N/A DTF (KM):N/A | .
1651 |  | JE24043004 | 177 UNDERHILL ROAD,TAUHERENIKAU,FEATHERSTON | Western | REVANS ST | 2024-11-23 | 12:51 | 2024-11-23 | 18:35 | 0.037072 | 0.0001076 | 39 | 13437 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: Fuses 7255 Protection flags (nil where none): Nil CAUSE: Car v Pole Location: Pole 848591 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): Yes at Pole 443373, Centre Phase Follow up Required (select advisory)? No Additional fault restoration comments: Line isolated at Fuses 7255, pole REPLACED AND LINES REPAIRED SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1652 |  | JE24043005 | 20 FAULKNER STREET,GATE PA,TAURANGA | Eastern | GATE PA | 2024-11-23 | 13:30 | 2024-12-04 | 12:30 | 0.10316 | 0.0006456 | 117 | 37391 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Fuses SD4-664 ORT 13:30 Cable Fault - Generator Installed at Transformer TD4-053 DNO 2411014 Repaired 04/12/24 New Cable Fitted | .
1653 |  | JE24043018 | unknown TAURANGA ROAD,Te Poi,Rural | Eastern | GORDON | 2024-11-23 | 13:43 | 2024-11-23 | 16:39 | 0.0097336 | 5.5179e-05 | 20 | 3528 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: Recloser 13379/2 Protection flags (nil where none): Nil CAUSE: Lightning Suspect Location: Pole F1716 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): None Follow up Required (select advisory)? No Additional fault restoration comments: Pole found cracked with concrete pieces on the ground. Suspected lightning .Isolated area and replaced pole. There as no tripping, site inspection then replaced pole SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): No Circuit that tripped: Nil DTF (KM):N/A | .
1654 |  | JE24043021 | unknown SH 2 ,Tanners Point,Rural | Eastern | ATHENREE | 2024-11-23 | 14:34 | 2024-11-23 | 15:23 | 0.0056915 | 0.00011588 | 42 | 2063 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | REGULATORY INFORMATION Voltage & Device ID: Recloser 9792 Protection flags (nil where none): None CAUSE: Tree Branch on lines Location: Pole 207211 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): N Follow up Required (select advisory)? No Additional fault restoration comments: Branch hanging on the lines at pole 207211. Could not be removed with hot stick. Isolated and issued permit to remove tree branch. Power restored after removing branch SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): No Circuit that tripped: N/A DTF (KM):N/A | .
1655 |  | JE24032200 | 52 AWAITI CANAL ROAD, KEREPEHI, PAEROA, 3671 | Eastern | KAIHERE | 2024-11-22 | 12:31 | 2024-11-22 | 14:04 | 0.0010282 | 1.1036e-05 | 4 | 373 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace 11kV spur line HV DDO cross arm and DDOs FC2393 at Pole 877714. | .
1656 |  | JE24039337 | 358 ROWAN ROAD, AUROA, HAWERA, 4679 | Western | AUROA | 2024-11-22 | 8:45 | 2024-11-22 | 14:16 | 0.032871 | 9.9323e-05 | 36 | 11914 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV arms 719007, 719010, 716989, 716975, 716982, 719012, 716996, 719019, 719020, 719023, 719022, 719015 | .
1657 |  | JE24039892 | 5 KNORP STREET, HALCOMBE, FEILDING, 4779 | Western | MT STEWART | 2024-11-22 | 9:01 | 2024-11-22 | 13:39 | 0.15134 | 0.00054352 | 197 | 54855 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replacing Xarms & ABS M55 Pole 19119/19120 Knorp St | .
1658 |  | JE24040023 | 848 BIDWILLS CUTTING ROAD, MORRISONS BUSH, GREYTOWN, 5794 | Western | TAWAHA | 2024-11-22 | 9:55 | 2024-11-22 | 14:01 | 0.015584 | 6.3456e-05 | 23 | 5648 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace transformer site t942 reusing existing transformer | .
1659 |  | JE24040293 | 43 FITZHERBERT EAST ROAD, AOKAUTERE, PALMERSTON NORTH, 4471 | Western | AOKAUTERE | 2024-11-22 | 8:45 | 2024-11-22 | 11:23 | 0.031825 | 0.0002014 | 73 | 11535 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT: Replace crossarms, repair conductor damage and re-sag conductors both sides of pole P46308. | .
1660 |  | JE24042458 | 147 EMERTON ROAD, WAIHI BEACH, WAIHI BEACH, 3611 | Eastern | ATHENREE | 2024-11-22 | 7:11 | 2024-11-22 | 7:13 | 0.00045976 | 0.00029797 | 108 | 167 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | change settings on 9225 , 9792 and 9405 and test Break Make Switching switching done at 07:11 am (31 seconds outage) | .
1661 |  | JE24042464 | 1032 POHANGINA VALLEY WEST ROAD, ASHHURST | Western | POHANGINA | 2024-11-22 | 9:53 | 2024-11-22 | 11:44 | 0.017396 | 0.00015726 | 57 | 6305 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Urgent outage, Repair Jumper and re-sag conductor, Fit polymers & bird spikes at Pole P14273 Isolated at ABS F67, E46 & Links E50 Repairs made, Full power restored | .
1662 |  | JE24042895 | 677 MAATA ROAD,RAWHITIROA,ELTHAM | Western | TE ROTI | 2024-11-22 | 11:42 | 2024-11-22 | 15:11 | 0.0011498 | 5.5179e-06 | 2 | 417 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: DTX Fuses CAUSE: Unknown Temp generation (stage details when used): N PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: Weather (wind/rain): rain, windy Follow up required (select advisory)? Additional fault restoration comments: Replace Tx 4479T | .
1663 |  | JE24042914 | 31 LAKEVIEW QUAY, PYES PA, TAURANGA, 3112 | Eastern | THE LAKES | 2024-11-22 | 14:40 | 2024-11-22 | 16:04 | 0.0048726 | 5.7938e-05 | 21 | 1766 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: CB 5 Protection flags (nil where none): Nil CAUSE: Flash over Location: Switchgear 9332 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): 2411007 Circuit patrolled and type: No Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Sw/Gear noticed during NAPA 115533(JE24039886) with an indication of internal fault with black soot around switchgear covers and blown hole on the end plate. NAPA switching and job cancelled until switchgear got fixed. Sw/Gear fixed - Terminal flashed over to the cover plate on Sw/Gear 9332.Cleaned out soot and re insulated cable ends and tightened connections and replaced the sw/gear end cover plate. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): No Circuit that tripped: No Tripping DTF (KM):N/A | .
1664 |  | JE24042947 | unknown KOHETE ROAD,Kaimata,Rural | Western | KAIMATA | 2024-11-22 | 15:35 | 2024-11-22 | 17:58 | 0.0054868 | 3.8625e-05 | 14 | 1989 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Outage to repair floating conductor at Pole 760210. Isolate 33kv Lines Between 33kV ABS 221 / ABS 160, 6.6kV (MOK H21) Links H22 / ABS 5325 | .
1665 |  | JE24042948 | 29 CHATHAM STREET,PAHIATUA,PAHIATUA | Western | COONOOR | 2024-11-22 | 16:20 | 2024-11-22 | 18:11 | 0.0021395 | 1.9313e-05 | 7 | 775 | Unplanned | WILDLIFE - BIRD | Blown Jumpers at Poles P37479 & P26819 due to Bird strike Isolated at ABS T17 & Q35 Jumpers repaired, Full power restored | .
1666 |  | JE24042973 | 92 WAITARA ROAD, WAITARA | Western | DEVON RD | 2024-11-22 | 23:06 | 2024-11-23 | 0:58 | 0.00062003 | 5.5179e-06 | 2 | 225 | Unplanned | ADVERSE ENVIRONMENT - FIRE | ETA fire coms 20mins at 22:40 Fire near HV line past fuses 8272 Fire Services required lines isolated while putting out fire and check waste site. Fire was NOT caused by Powerco equipment Isolated at fuses 8272 23:05 FM to return to site once contacted by customer FM contacted, Power re-stored 00:54 | .
1667 |  | JE24039204 | 495 PUKEKAURI ROAD, WAIHI, WAIHI, 3682 | Eastern | OLD TAURANGA RD | 2024-11-21 | 9:32 | 2024-11-21 | 17:44 | 0.039399 | 8.001e-05 | 29 | 14280 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 33kV Crossarms Pukekauri Rd between WKOCRE024 to WKOCRE046 | .
1668 |  | JE24039506 | 238 OHANGAI ROAD, HAWERA, HAWERA, 4673 | Western | CAMBRIA LS | 2024-11-21 | 8:45 | 2024-11-21 | 14:20 | 0.043483 | 0.00012967 | 47 | 15761 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11KV double pole 723137. Replace HV pin at 723136, 723139. | .
1669 |  | JE24039527 | 163 NORWOOD LANE, MARTON, MARTON, 4787 | Western | LEEDSTOWN 22KV | 2024-11-21 | 9:30 | 2024-11-21 | 13:16 | 0.0031151 | 1.3795e-05 | 5 | 1129 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | run new conductor between poles 804884 to 373384 | .
1670 |  | JE24039770 | 81 CLIFTON GROVE ROAD, ADMIRAL HILL, MASTERTON, 5883 | Western | LONGBUSH | 2024-11-21 | 8:46 | 2024-11-21 | 13:58 | 0.042262 | 0.00013519 | 49 | 15318 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles and hardware past S333 | .
1671 |  | JE24039810 | BOWENTOWN | Eastern | BOWENTOWN | 2024-11-21 | 8:39 | 2024-11-21 | 12:55 | 0.0056562 | 2.2072e-05 | 8 | 2050 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | PQR - To upgrade transformer TA2-033 to 50kVA and carry out insulation resistance checks on the underground cable from pole 207038 | .
1672 |  | JE24039820 | 1000 MORRINSVILLE-WALTON ROAD, MORRINSVILLE, MORRINSVILLE, 3371 | Eastern | KIWITAHI | 2024-11-21 | 9:24 | 2024-11-21 | 15:09 | 0.035477 | 0.00010484 | 38 | 12859 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE POLE I12693, REMOVE ABS IC780 & INSTALL NEW ENTEC / SOURCE SIDE LINKS ,14920/2 / 14920/4 | .
1673 |  | JE24039823 | 17 OPAL DRIVE, PAPAMOA BEACH, TAURANGA, 3118 | Eastern | PAPAMOA JUNCTION | 2024-11-21 | 9:45 | 2024-11-21 | 13:46 | 0.077714 | 0.0003228 | 117 | 28168 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv - S4796-S4798-S4800 | .
1674 |  | JE24039825 | 4 CORBETT STREET, PAEROA, PAEROA, 3600 | Eastern | WILLOUGHBY ST | 2024-11-21 | 23:01 | 2024-11-22 | 6:00 | 0.092591 | 0.00022072 | 80 | 33560 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE 11KV & 400V POLE'S N1050,862053,862054,N1061 & N12477 | .
1675 |  | JE24039903 | pole_P05288 | Western | KAKARIKI | 2024-11-21 | 9:15 | 2024-11-21 | 13:52 | 0.025967 | 9.3805e-05 | 34 | 9412 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replacing Xarms & ABS M67 Replacing Xarms Removing ABS M69 and sleeving conductor through | .
1676 |  | JE24039973 | 369 TARATA ROAD, NORFOLK, INGLEWOOD, 4387 | Western | KAIMATA | 2024-11-21 | 9:00 | 2024-11-21 | 14:17 | 0.013097 | 4.1384e-05 | 15 | 4747 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace crosarms at poles 760550,760552,760545,760546,760547,760548. | .
1677 |  | JE24039980 | 424 OMANAWA ROAD, OMANAWA, TAURANGA, 3171 | Eastern | KEENAN RD | 2024-11-21 | 8:45 | 2024-11-21 | 13:51 | 0.045026 | 0.00015174 | 55 | 16320 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv overhead conductors between poles 211666 &211670 with AAAC Iodine | .
1678 |  | JE24040176 | 3 RALEIGH STREET, WAITARA, WAITARA, 4320 | Western | BLAKE ST | 2024-11-21 | 8:46 | 2024-11-21 | 15:55 | 0.42171 | 0.00099874 | 362 | 152850 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Intersection of Raleigh Str, Mould Str and High Str West systematic undergrounding of HV and LV lines. This NAPA is for the outage requirements and work for DAY 2 to complete work for underground conversion. DAY 1 outage to be completed first on NAPA 115461 | .
1679 |  | JE24040215 | 32 RANGE ROAD, TUTURUMURI, MARTINBOROUGH, 5782 | Western | WINDFARM | 2024-11-21 | 8:39 | 2024-11-21 | 12:34 | 0.00064849 | 2.759e-06 | 1 | 235 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace C971 OYT CB for new Tavrida switch and SEL651R Relay CB Replaced, SCADA not commissioned | .
1680 |  | JE24042701 | 113 AWANUI STREET, MERRILANDS, NEW PLYMOUTH, 4312 | Western | BROOKLANDS 10 | 2024-11-21 | 0:30 | 2024-11-22 | 13:40 | 0.23677 | 0.00084976 | 246 | 85817 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | F4092114 no eta needed Car V Pole 751649 Isolated at Sw/Gear 8893/1 Sw/Gear 6797/3 & Sw /Gear 6983/2 Back feeds in At Sw/gear 12147/3 Gas/Sw 12221/2 Generator Installed at Transformer, H/V Cable and Pothead removed from the network. Cable to be replaced Cable replaced and generator removed | .
1681 |  | JE24042734 | 83 ASHBYS ROAD,LAKE RESERVE,FEATHERSTON | Western | SOUTH FEATHERSTON | 2024-11-21 | 9:11 | 2024-11-21 | 10:12 | 0.00016842 | 2.759e-06 | 1 | 61 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: T3208 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 10:12 Cause: unknown Weather (wind/rain): windy Follow up required (select advisory)?n | .
1682 |  | JE24042752 | 95 TE POI SOUTH ROAD, TE POI, MATAMATA, 3473 | Eastern | RANGITANUKU RD | 2024-11-21 | 12:13 | 2024-11-21 | 12:17 | 8.3137e-05 | 2.2072e-05 | 8 | 30 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Reports of high voltage. Isolate load from Tfr and voltage still high. DTX is on tap 3 and nearby DTX is set to tap 2 with good voltage. Outage to tap down DTX TC1936, voltage now 244V | .
1683 |  | JE24042777 | 78 MORIKAU ROAD,RANANA,WANGANUI | Western | RAETIHI | 2024-11-21 | 12:30 | 2024-11-21 | 14:50 | 0.005798 | 4.1384e-05 | 15 | 2102 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 224 No. Fuses: 2 Fuse Amp Size: 8A TIME CLOSED: 14:50 Cause: Unknown Weather (wind/rain): Beautiful Follow up required (select advisory)? No | .
1684 |  | JE24042799 | 86 MOUNTAIN ROAD,OROPI,TAURANGA | Eastern | WAIMAPU | 2024-11-21 | 15:06 | 2024-11-21 | 15:15 | 0.00020821 | 2.2072e-05 | 8 | 75 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tapping of transformer from Tap 5 to Tap 3. Voltage 232 with out solar at customers meter board | .
1685 |  | JE24042816 | 743 OLD TAUPO ROAD,WAOTU,PUTARURU | Eastern | WAOTU | 2024-11-21 | 15:01 | 2024-11-21 | 16:01 | 0.0098854 | 0.00016554 | 60 | 3583 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | REGULATORY INFORMATION Voltage & Device ID: REC 13109 Protection flags (nil where none): A/B phase OC CAUSE: tree branch on the lines Location: Pole M1545 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: cursory Weather (wind/rain): windy, heavy rain LFI (Y/N + Comments): LFI's are out of comms Follow up Required (select advisory)? Additional fault restoration comments: tree branch removed with hot sticks | .
1686 |  | JE24042828 | 206 MANGARERE ROAD,MANGAWEKA,MANGAWEKA | Western | MANGAWEKA | 2024-11-21 | 16:02 | 2024-11-21 | 18:42 | 0.003099 | 1.9313e-05 | 7 | 1123 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 926 No. Fuses: 2 Fuse Amp Size: 10 Amp TIME CLOSED: 18:42 Cause: Lightning Weather (wind/rain): Rain & Lightning Follow up required (select advisory)? | .
1687 |  | JE24042831 | unknown HENRY WATSON ROAD,Matamata,Matamata | Eastern | STATION RD | 2024-11-21 | 14:41 | 2024-11-21 | 16:56 | 0.0074791 | 5.5179e-05 | 20 | 2711 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: FP1342 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 1656 Cause: suspect line clash Weather (wind/rain): heavy rain, windy Follow up required (select advisory)? | .
1688 |  | JE24042842 | unknown SH 1 ,Utiku,Taihape | Western | MANGAWEKA | 2024-11-21 | 20:36 | 2024-11-21 | 22:55 | 0.0026851 | 1.9313e-05 | 7 | 973 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Broken Stand Offs Found at X4030 Isolated at Fuses 4015 All 3 stand offs replaced Power re-stored 22:55 Cause high winds | .
1689 |  | JE24042845 | sub_MAR | Eastern | OLD CAMBRIDGE RD | 2024-11-21 | 18:25 | 2024-11-21 | 19:57 | 0.076814 | 0.00097943 | 355 | 27842 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11KV CB 3 Protection flags (nil where none): A,B.C O/C Inv Time CAUSE: Suspect Branch blew onto lines. but nothing found Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Curse Weather (wind/rain): Windy LFI (Y/N + Comments): Yes ABS 979 Pole A12633 Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1690 |  | JE24042846 | 240 CLIFFORD ROAD, PATEA | Western | KAKARAMEA | 2024-11-21 | 20:51 | 2024-11-21 | 22:53 | 0.0010145 | 8.2769e-06 | 3 | 368 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Broken Dead Ends found at Transformer L4440 Isolated at Fuses LI706 Dead ends replaced Power re-stored 22:53 | .
1691 |  | JE24042857 | JE24042854 | Western | PARIHAKA | 2024-11-21 | 21:08 | 2024-11-21 | 22:46 | 0.0016315 | 1.6554e-05 | 6 | 591 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 6635 No. Fuses: 2 Fuse Amp Size: 8 Amp TIME CLOSED: 22:46 Cause: Lightning Weather (wind/rain): Raining, Lightning Follow up required (select advisory)? N | .
1692 |  | JE24042860 | unknown unknown,Rahotu,Rural | Western | NGARIKI RD | 2024-11-21 | 21:32 | 2024-11-21 | 23:45 | 0.0003675 | 2.759e-06 | 1 | 133 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: N1209 No. Fuses: 3 Fuse Amp Size: 3 Amp TIME CLOSED: 23:45 Cause: Lightning Weather (wind/rain): Raining, Lightning Follow up required (select advisory)? N | .
1693 |  | JE24039188 | 41 CREAN ROAD, WAIHI, WAIHI, 3682 | Eastern | WAIHI BEACH RD | 2024-11-20 | 9:30 | 2024-11-20 | 14:33 | 0.0025027 | 8.2769e-06 | 3 | 907 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 33kV Crossarms Creans Rd between poles WKOCRE051 - WKOCRE077 | .
1694 |  | JE24039424 | 141 VALLEY ROAD, MOUNT MAUNGANUI, TAURANGA, 3116 | Eastern | GOLF RD | 2024-11-20 | 9:45 | 2024-11-20 | 13:23 | 0.046206 | 0.00021244 | 77 | 16748 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9259/1/2/3 | .
1695 |  | JE24039463 | DAIRYFACT | Western | DAIRYFACT | 2024-11-20 | 9:30 | 2024-11-20 | 13:23 | 0.0064183 | 2.759e-05 | 10 | 2326 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Make Line Break P43789 then Replace ABS A87 and Pole P43740 then Close line break | .
1696 |  | JE24039479 | 244 COULTERS LINE, KIWITEA, FEILDING, 4777 | Western | WAITUNA | 2024-11-20 | 9:17 | 2024-11-20 | 15:11 | 0.041969 | 0.00011864 | 43 | 15212 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replacing Xarms & 11kV ABS P11 at Pole P19648. Replacing Xarms Removing 11kV ABS P12 and sleeving conductor through at Pole P20550. | .
1697 |  | JE24039505 | 158 WARNER ROAD, OROPI, TAURANGA, 3173 | Eastern | WAIMAPU | 2024-11-20 | 9:07 | 2024-11-20 | 15:02 | 0.02451 | 6.8974e-05 | 25 | 8884 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles and/or crossarms 211234 (TE4-020) to 211239 (TE4-021) | .
1698 |  | JE24039534 | KAIHERE | Eastern | KAIHERE | 2024-11-20 | 8:46 | 2024-11-20 | 14:34 | 0.038408 | 0.00011036 | 40 | 13921 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE 11KV POLE O14328 & O682. REPLACE 400V XARMS AT POLE O687 | .
1699 |  | JE24040199 | 1704B WESTERN LAKE ROAD, WESTERN LAKE, FEATHERSTON, 5773 | Western | REVANS ST | 2024-11-20 | 9:16 | 2024-11-20 | 12:37 | 0.0022123 | 1.1036e-05 | 4 | 802 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 848853 with new Tavrida switch (11490/1/2/4/6 ) Recloser not commissioned | .
1700 |  | JE24040590 | 542 TARATA ROAD, NORFOLK, INGLEWOOD, 4387 | Western | KAIMATA | 2024-11-20 | 9:01 | 2024-11-20 | 14:04 | 0.0092184 | 3.0349e-05 | 11 | 3341 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace crossarms at poles 760585,760586,760587,760590,760592, | .
1701 |  | JE24042534 | unknown ORCHARD WEST ROAD,Ngatea,Ngatea | Eastern | MANGATARATA | 2024-11-20 | 6:23 | 2024-11-20 | 9:16 | 0.00095136 | 5.5179e-06 | 2 | 345 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses FC768 No. Fuses: 3 Fuse Amp Size: 10A TIME CLOSED: 09:15 Cause: Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? No | .
1702 |  | JE24042591 | 350 PUKE PUKE ROAD,HIMATANGI,FOXTON | Western | OROUA DOWNS | 2024-11-20 | 17:41 | 2024-11-20 | 18:20 | 0.0039914 | 0.00010208 | 37 | 1447 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Broken Fuse found for Transformer T1/514 Isolated at Fuses L27 | .
1703 |  | JE24042614 | KAR Sub - CB 14 - RECLOSER 10715 | Western | TAIKOREA | 2024-11-20 | 11:20 | 2024-11-20 | 14:20 | 0.057452 | 0.00042212 | 153 | 20824 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Recloser 10715/2 Protection flags (nil where none): C Ph O/C, E/F CAUSE: Broken Insulator Location: Pole P16467 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Windy LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1704 |  | JE24042659 | 5 ARAPUNI ROAD,LICHFIELD,PUTARURU | Eastern | HORAHORA | 2024-11-20 | 15:36 | 2024-11-20 | 16:21 | 0.038624 | 0.0014705 | 533 | 13999 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 1 Protection flags (nil where none): A,B,C O/C CAUSE: Tree Branch blew onto line @ Pole M12778 Location: Pole M12778 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: curse Weather (wind/rain): High Winds at time LFI (Y/N + Comments): Yes 14306/1 & 4 Follow up Required (select advisory)? Additional fault restoration comments: | .
1705 |  | JE24042666 | 173 SNODGRASS ROAD, TAURANGA, 3174 | Eastern | PLUMMERS POINT | 2024-11-20 | 17:08 | 2025-01-15 | 14:04 | 0.22191 | 5.5179e-06 | 1 | 80432 | Unplanned | ADVERSE ENVIRONMENT - FIRE | ETA Fire coms F4091903 20 mins. Fire around transformer TC3-099. Isolated at Fused ABS SC3-025 for fire service VELD FIRE Isolated at FABS .Disconnected LV cable going to the meter all burnt down, Disconnection Tag A31733. closed FABS SC3025, to check condition of cables and Transformer. Tested okay. 20:31 Open, Lock n Tag fabs SC3025.OVERNIGHT at the request of FENZ incase the fire pops up again overnight. 2R left open. 21/11/24 customer cable to damaged to reliven, Transformer left off due to single consumer & no LV fuses installed. Customer to arrange electrician to replace cable & reconnect. 28/11 because HV fuses SC3-025 are still open QA is unable to process until job is completed, so have moved back to Under Action. Erin 14/01/2025 - Update from the hub - Paul Cooper has liaised with David Spellman and will be attending site before 17/01. MDP 15/01/25 - Fused ABS SC3-025 closed and transformer livened still no customer connected due to safety disconnection Tag No: A31733 | .
1706 |  | JE24042671 | 1423 TE PUKE HIGHWAY,TE PUKE,TE PUKE | Eastern | KAITUNA | 2024-11-20 | 14:20 | 2024-11-20 | 17:52 | 0.0050295 | 5.7938e-05 | 21 | 1823 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | REGULATORY INFORMATION Voltage & Device ID: CB 3 Protection flags (nil where none): Nil CAUSE: Broken Jumper Location: Pole 392520 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): None Follow up Required (select advisory)? No Additional fault restoration comments: Isolated area repaired jumper and restored power SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1707 |  | JE24042680 | 119 TE RERENGA KUAOTUNU ROAD,OTAPAURAU,COROMANDEL | Eastern | OWERA RD | 2024-11-20 | 18:18 | 2024-11-20 | 19:30 | 0.0018032 | 2.4831e-05 | 9 | 654 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses FC2311 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 19:30 Cause: (Unknown)_ Suspect Birds Weather (wind/rain): CALM Follow up required (select advisory)? No | .
1708 |  | JE24042687 | 7 PUKAKURA ROAD,KATIKATI,KATIKATI | Eastern | TETLEY ROAD | 2024-11-20 | 20:41 | 2024-11-20 | 22:29 | 0.011654 | 0.0001076 | 39 | 4224 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | update SMC to go to fuses SB2-037 check JE24042688 / 24042689 / 24042690 / 24042692 / 24042695 Fuses Location: Fuses SB2-037 No. Fuses: 2 Fuse Amp Size: 8A TIME CLOSED: 22:29 Cause: Line clash-wind Weather (wind/rain): Windy Follow up required (select advisory)? No | .
1709 |  | JE24039119 | pole_804864 | Western | LEEDSTOWN 22KV | 2024-11-19 | 9:10 | 2024-11-19 | 14:45 | 0.0046249 | 1.3795e-05 | 5 | 1676 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Run new conductor between poles 804864 and 373384 | .
1710 |  | JE24039171 | 327 PUKEKAURI ROAD, WAIHI, WAIHI, 3682 | Eastern | OLD TAURANGA RD | 2024-11-19 | 9:00 | 2024-11-19 | 15:31 | 0.031311 | 8.001e-05 | 29 | 11349 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 33kV Crossarms from pole 416744/416419 to WKOCRE027 Pukekauri Rd, Waihi | .
1711 |  | JE24039183 | 137 4 ROAD, TE PUKE, TE PUKE, 3183 | Eastern | NO 3 ROAD | 2024-11-19 | 10:30 | 2024-11-19 | 11:53 | 0.010072 | 0.00012139 | 44 | 3651 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Link box maintenance at SE5-235 | .
1712 |  | JE24039186 | 255 RUAHIHI ROAD, LOWER KAIMAI, TAURANGA, 3171 | Eastern | KAIMAI DRIVE | 2024-11-19 | 8:46 | 2024-11-19 | 14:12 | 0.033292 | 0.00010208 | 37 | 12067 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv overhead conductors between poles 211660 & 211638 with AAAC Iodine. | .
1713 |  | JE24039187 | 107 WAIMANA ROAD, ADMIRAL HILL, MASTERTON, 5883 | Western | LONGBUSH | 2024-11-19 | 8:45 | 2024-11-19 | 14:21 | 0.045383 | 0.00013519 | 49 | 16449 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles and hardware past S333 | .
1714 |  | JE24039263 | 81 DENNY HULME DRIVE, MOUNT MAUNGANUI, TAURANGA, 3116 | Eastern | EVERSHAM RD | 2024-11-19 | 9:46 | 2024-11-19 | 13:42 | 0.12627 | 0.00053524 | 194 | 45768 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - SD5-230/SD5-233/SD5-231 | .
1715 |  | JE24039361 | 339 PUKEHINA PARADE, PUKEHINA, TE PUKE, 3189 | Eastern | TAINUI | 2024-11-19 | 8:38 | 2024-11-19 | 10:16 | 0.014533 | 0.00014898 | 54 | 5268 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | PQI - To tap transformer TE7-075 down one tap and balance one ICP each from Red and Blue to White | .
1716 |  | JE24039482 | 3 RALEIGH STREET, WAITARA, WAITARA, 4320 | Western | BLAKE ST | 2024-11-19 | 8:31 | 2024-11-19 | 15:54 | 0.019161 | 0.0010043 | 364 | 6945 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Intersection of Raleigh Str, Mould Str and High Str West systematic undergrounding of HV and LV lines. This NAPA is for the outage requirements and work for DAY 1 to install nee switchgear 12774. DAY 2 outage to follow on NAPA 115469. | .
1717 |  | JE24040181 | 17 RAYMOND STREET, BUNNYTHORPE, PALMERSTON NORTH, 4481 | Western | SANSONW40-OHAKEA3132 33KV | 2024-11-19 | 9:16 | 2024-11-19 | 11:30 | 0.037516 | 0.00027866 | 101 | 13598 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Shutdown 1 - AP1 Isolation to allow SW pipe and duct install for Transpower and relay maintenance on 2232. AP3 Complete maintenance on Z15/Z19, 33kV injection plant and relay maintenance on 2192. | .
1718 |  | JE24042382 | 2396 1 ,RONGOTEA,PALMERSTON NORTH | Western | OROUA DOWNS | 2024-11-19 | 10:20 | 2024-11-19 | 10:42 | 6.0697e-05 | 2.759e-06 | 1 | 22 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Blown Jumper Found at Fuses L76 Isolated at Fuse L76 Jumper repaired | .
1719 |  | JE24042387 | 858 PONATAHI ROAD,MARTINBOROUGH,CARTERTON | Western | PONATAHI | 2024-11-19 | 7:33 | 2024-11-19 | 9:45 | 0.00072944 | 5.5179e-06 | 2 | 264 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 7268 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 09:45 Cause: Unknown Weather (wind/rain): Sunny Follow up required (select advisory)? No | .
1720 |  | JE24042417 | 78 CHAMBERS STREET,TOKOROA,TOKOROA | Eastern | DALMENY ST | 2024-11-19 | 19:04 | 2024-11-19 | 22:31 | 0.004035 | 7.1733e-05 | 13 | 1463 | Unplanned | HUMAN ERROR - POTENTIAL WORKMANSHIP | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 4 Protection flags (nil where none): Nil CAUSE: Sw/Gear 9385 slipped due to ground wash out Location: Sw/Gear 9385 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: No Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: There was a crew hydrovacing around the Sw/Gear and noticed that the RMU was on a lean. Sw/Gear 9385 isolated and ground around unit was back filled and compacted. It is unsure if the hydrovac activity caused the RMU to lean. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): called FM worksite getting set up. FM to call control in hour to start switching when gear and crew onsite | .
1721 |  | JE24042431 | 282 STEWART ROAD,WAVERLEY,WAVERLEY | Western | WAVERLEY | 2024-11-19 | 12:10 | 2024-11-19 | 14:14 | 0.00033995 | 2.759e-06 | 1 | 123 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Noises coming from LV end of Transformer 4826W Isolated at FABS 4682 for safety Checks carried out on transformer Transformer Livened 14:13 Still 1 phase down. Fuses Location: 4688 No. Fuses: 2 Fuse Amp Size: 20 Amp TIME CLOSED: 13:47 Cause: Possible high load contact Weather (wind/rain): Calm Follow up required (select advisory)? N Fuses Location: 4147 No. Fuses: 1 Fuse Amp Size: 20 Amp TIME CLOSED: 14:56 Cause: Possible high load contact Weather (wind/rain): Calm Follow up required (select advisory)? N | .
1722 |  | JE24042492 | 231 REA ROAD,TAHAWAI,KATIKATI | Eastern | WHARAWHARA ROAD | 2024-11-19 | 14:30 | 2024-11-19 | 15:56 | 0.0045375 | 5.242e-05 | 19 | 1645 | Unplanned | WILDLIFE - BIRD | Fuses Location: SB1-024 No. Fuses: 2 Fuse Amp Size: 8 TIME CLOSED: 15:56 Cause: Bird strike, Pole 208334 Weather (wind/rain): calm Follow up required (select advisory)?n Line patrolled | .
1723 |  | JE24042522 | 68 KAIMATA ROAD SOUTH,KAIMATA,INGLEWOOD | Western | KAIMATA | 2024-11-19 | 21:07 | 2024-11-19 | 22:24 | 0.00042889 | 5.5179e-06 | 2 | 155 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 5485 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 22-24 Cause: Unknown Weather (wind/rain): Fine Follow up required (select advisory)? | .
1724 |  | JE24038930 | SOUTH RD NGARIKI | Western | SOUTH RD NGARIKI | 2024-11-18 | 9:19 | 2024-11-18 | 14:48 | 0.0027282 | 8.2769e-06 | 3 | 989 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace poles 712389, 712390, 712392, 711530 & 712393 | .
1725 |  | JE24039027 | 807 OROPI ROAD, OROPI, TAURANGA, 3173 | Eastern | WAIMAPU | 2024-11-18 | 9:09 | 2024-11-18 | 15:33 | 0.1398 | 0.00036418 | 132 | 50670 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 211048 to 211089 | .
1726 |  | JE24039029 | 10 RESERVOIR ROAD, KARANGAHAKE, PAEROA, 3674 | Eastern | SHAW AVE | 2024-11-18 | 9:30 | 2024-11-18 | 14:49 | 0.018453 | 5.7938e-05 | 21 | 6689 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace HV and LV crossarms at poles N1855 N1850 N1851 N1870 and earthing and arms on N12550 | .
1727 |  | JE24039071 | 106B NOPERA ROAD, PIHAMA, OPUNAKE, 4682 | Western | AUROA | 2024-11-18 | 9:20 | 2024-11-18 | 15:15 | 0.0048944 | 1.3795e-05 | 5 | 1774 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | relocate tx T5175 to pole 357031. replace pole 357031 with new tx structure. | .
1728 |  | JE24039307 | 169 BROWN ROAD, TE PUKE, TE PUKE, 3188 | Eastern | RANGIURU | 2024-11-18 | 13:45 | 2024-11-18 | 15:28 | 0.00056347 | 5.5179e-06 | 2 | 204 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Link box maintenance at SE6-128 & SE6-180 | .
1729 |  | JE24039333 | 71 TARATA ROAD, INGLEWOOD, INGLEWOOD, 4387 | Western | KAIMATA | 2024-11-18 | 9:01 | 2024-11-18 | 14:44 | 0.014223 | 4.1384e-05 | 15 | 5155 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace crossarms on poles 760537,760540,760541,760542,760544,760533,760535 | .
1730 |  | JE24039437 | 347 BROWN ROAD, TE PUKE, TE PUKE, 3188 | Eastern | RANGIURU | 2024-11-18 | 10:30 | 2024-11-18 | 13:14 | 0.008032 | 4.9661e-05 | 18 | 2911 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Link box maintenance at SE6-150 and SE6-130 | .
1731 |  | JE24040099 | 3720 2, MANGATARATA, THAMES, 3576 | Eastern | MANGATARATA | 2024-11-18 | 9:49 | 2024-11-18 | 11:11 | 0.010019 | 0.00012139 | 44 | 3631 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | PTP Red Defect - Replace 11kv Insulator and binder at Pole O14170 | .
1732 |  | JE24042209 | 5889 29 ,KARAPIRO,TIRAU | Eastern | TOTMANS RD | 2024-11-18 | 0:53 | 2024-11-18 | 2:51 | 0.0074582 | 6.3456e-05 | 23 | 2703 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | REGULATORY INFORMATION Voltage & Device ID: CB 3 Protection flags (nil where none): NIL CAUSE: Broken jumper Location: Pole E22999 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Isolated work area at ABS 1154, ABS 13572, ABS 9790/1 and Links 9790/6 and replaced broken jumper at Transformer TC4527 including whole set of Fuses at TC4527 replaced and Cross arm | .
1733 |  | JE24042225 | 447 OWHAKURA ROAD,RANGIWAEA,TAIHAPE | Western | IRIRANGI | 2024-11-18 | 6:03 | 2024-11-18 | 10:50 | 0.013735 | 0.00029797 | 54 | 4978 | Unplanned | HUMAN ERROR - POTENTIAL WORKMANSHIP | Replaced 1 x 10A Fuse @ Fuses 1464 07:26 , Fuses underrated 2R to replace with 100A or Solid Links, 30A Fuse Temp installed ( Biggest we had on the Truck ) till new Links turn up. | .
1734 |  | JE24042228 | 1437 PALMER ROAD,MAHOE,STRATFORD | Western | MAHOE | 2024-11-18 | 6:28 | 2024-11-18 | 10:16 | 0.015138 | 6.6215e-05 | 24 | 5487 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 6266 No. Fuses: 2 Fuse Amp Size: 20A TIME CLOSED: 10:16 Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)? | .
1735 |  | JE24042229 | 818R PEMBROKE ROAD,PEMBROKE,STRATFORD | Western | CARDIFF RD | 2024-11-18 | 6:42 | 2024-11-18 | 8:41 | 0.00065608 | 5.5179e-06 | 2 | 238 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 5661 (NOT Transformer 4817, Incorrect Address, See Child Job for Correct Device) No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 08:40 Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)? | .
1736 |  | JE24042278 | 185 SHAFTESBURY ROAD,MANAWARU,TE AROHA | Eastern | MCCABE ROAD | 2024-11-18 | 12:33 | 2024-11-18 | 14:48 | 0.014908 | 0.00011036 | 40 | 5403 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Broken Cross arm at Pole C13721 Cause Age Isolated ABS's IP584, 1257, 9715/1 & Links 9715/6 Cross arm Replaced | .
1737 |  | JE24042285 | recloser_E33 | Western | POHANGINA | 2024-11-18 | 10:36 | 2024-11-18 | 14:14 | 0.066791 | 0.00033935 | 123 | 24209 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec E33 Protection flags (nil where none): A Phase O/C E/F CAUSE: Floating Conductor Location: Pole P14356 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Weather (wind/rain): Fine LFI (Y/N + Comments): No Follow up Required (select advisory)? Additional fault restoration comments: Replaced 1 X Pin & Insulator at the same time SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1738 |  | JE24042333 | recloser_13204:2 | Eastern | HIKUAI | 2024-11-18 | 13:47 | 2024-11-18 | 16:19 | 0.058132 | 0.0003835 | 139 | 21070 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Sec 13204/2 Protection flags (nil where none): A, B Ph O/C E/F CAUSE: Unknown (No Fault Found) Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Windy LFI (Y/N + Comments): N Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1739 |  | JE24042342 | 5383 STATE HIGHWAY 29,KARAPIRO,MATAMATA | Eastern | TOTMANS RD | 2024-11-18 | 14:45 | 2024-11-19 | 0:48 | 0.058777 | 0.0011836 | 429 | 21304 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV Recloser 13260 Protection flags (nil where none): B Phase O/C CAUSE: Car V DTX TC4525 Pole Location: TC4525 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: Cursory patrolled F4 Weather (wind/rain): Calm LFI (Y/N + Comments): Indicated Wrong Direction??? See Notes Follow up Required (select advisory)? LFI??? Additional fault restoration comments: Fault Locators Operated @ ABS 808 Pole E13009 Completely wrong direction!!! they may be facing the wrong way and seen the fault behind them??? 1 x 11m pole 1 x 15kVA transformer (original transformer was 5kVA) 1 x HV pin arm complete assembly 1 x Transformer hanger cross arm 1 x HV fuse arm The installation the transformer is feeding was deemed not safe to liven and a disconnection for safety was done at the service fuse, tag no: A39493. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1740 |  | JE24042363 | 23 MOEWAI ROAD,WHITIANGA,WHITIANGA | Eastern | PURANGI | 2024-11-18 | 17:39 | 2024-11-18 | 20:41 | 0.13904 | 0.003537 | 1282 | 50395 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 5 Protection flags (nil where none): Nil CAUSE: Line down Location: Between pole W0476 & 319329 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F3/4, Not patrolled. Weather (wind/rain): Calm LFI (Y/N + Comments): Fitted no indication Follow up Required (select advisory)? No Additional fault restoration comments: Lines repaired 10M Squirrel conductor 3 x FT joint sleeves SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1741 |  | JE24042369 | 65 VOSPERS ROAD,LICHFIELD,PUTARURU | Eastern | LICHFIELD | 2024-11-18 | 19:26 | 2024-11-19 | 11:01 | 0.11575 | 0.00031728 | 100 | 41955 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 13232/2 Protection flags (nil where none): E/F CAUSE: Line down7/14 CU Conductor failed, Deterioration or it had been clashing in middle of big span. Location: Pole 425825 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4, cursory patrolled. Weather (wind/rain): Calm LFI (Y/N + Comments): Yes at ABS 919 Follow up Required (select advisory)? Yes Additional fault restoration comments: TLB cut at Pole 878953 FRM called and said they have manpower issues due to car v pole JE24042342 and will tackle the job in the morning. Repaired 11:00 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1742 |  | JE24042164 | PYES PA | Eastern | PYES PA | 2024-11-17 | 0:37 | 2024-11-17 | 1:27 | 0.0074269 | 0.00014898 | 54 | 2692 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: Fuses SE3-017 Protection flags (nil where none): None CAUSE: Unknown Location: N/A Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Drizzling LFI (Y/N + Comments): Yes At ABS IP682 lit 2 phases centre and right (Pole 216656) Follow up Required (select advisory)? No Additional fault restoration comments: Tauranga on Emergencies Only-Upgraded this job to a feeder fault multiple transformers affected Fuses SE3-017 (54 ICPs) Line patrolled, nothing found. Relivened 01:26. Suspect bird strike common in this area SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): No Circuit that tripped: None DTF (KM):N/A | .
1743 |  | JE24042170 | OTAMARAKAU | Eastern | OTAMARAKAU | 2024-11-17 | 0:47 | 2024-11-17 | 5:18 | 0.065843 | 0.00043592 | 158 | 23865 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: Recloser 6029 Protection flags (nil where none): Phase A, B, C OC, EF, EF/OC CAUSE: Lines down, caused by suspect bird strike. Common problem during full moon. Conductors are only 25mm, could have brought down by fault current Location: Between Poles 227511 and 227512 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Light Rain LFI (Y/N + Comments): Yes at Pole 321260 Lit and at Pole 381286(ABS SE3-013) not lit Follow up Required (select advisory)? No Additional fault restoration comments: Line repaired Power restored 05:17Hrs. Cause Unknown but Suspect bird strike SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): No Circuit that tripped: N/A DTF (KM):N/A | .
1744 |  | JE24042188 | REID RD | Eastern | REID RD | 2024-11-17 | 9:07 | 2024-11-17 | 11:25 | 0.028569 | 0.00020692 | 75 | 10355 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 8 Protection flags (nil where none): Nil CAUSE: Car V Pole Location: 219823 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4, either side of the accident Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? NDR to follow Additional fault restoration comments: Pole 219823 broken by vehicle accident. 1 x 11m pole 1 x double back to back termination cross arms SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1745 |  | JE24042196 | 89 PONGAKAWA SCHOOL ROAD,PONGAKAWA,TE PUKE | Eastern | OTAMARAKAU | 2024-11-17 | 14:15 | 2024-11-17 | 20:04 | 0.13808 | 0.0010319 | 374 | 50047 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11 kV CB 2 Protection flags (nil where none): O/C E/F A - B Ø CAUSE: Car V pole Location: Pole 227339 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): Yes at Pole 497018 Follow up Required (select advisory)? No Additional fault restoration comments: Sectionalised and isolated faulty area. Restored power, Replaced Pole 227339 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): No Circuit that tripped: N/A DTF (KM):N/A | .
1746 |  | JE24042198 | 18 KAUARAPAOA ROAD,BRUNSWICK,WANGANUI | Western | MAKIRIKIRI | 2024-11-17 | 15:13 | 2024-11-17 | 17:27 | 0.011328 | 0.0001076 | 39 | 4106 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11KV Rec 2995 Protection flags (nil where none): A & B Phase Trip Flag CAUSE: Bit of Tree Location: Pole 784999 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Weather (wind/rain): Fine LFI (Y/N + Comments): No Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1747 |  | JE24042216 | 37 FLYGERS LINE,MILSON,PALMERSTON NORTH | Western | RANGITIKEI | 2024-11-17 | 22:23 | 2024-11-17 | 23:57 | 0.015026 | 0.00016002 | 58 | 5446 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Faultman found broken jumper on Fuses D24 reasons unknown, line was isolated at ABS's A18. D22 & D25 to repair the jumper, Faultman has also defected the Fuses D24 as they have no earthing spigots on them to earth hence the bigger outage area. | .
1748 |  | JE24042217 | 72 KITCHENER STREET,MARTINBOROUGH,MARTINBOROUGH | Western | PAHAUTEA 33KV TIE | 2024-11-17 | 22:39 | 2024-11-17 | 23:00 | 0.011209 | 0.00052972 | 192 | 4063 | Unplanned | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | Voltage device &amp; number: 33kV, CBC885 / Rec 3141/2 Protection flag indication: A/R, E/F, O/C, C Patrolled &amp; type: No Follow-up required? (Select advisory): No Weather at time of fault:Unknown LFI Activation: N Recloser 3141 also tripped. Closed 22:59 | .
1749 |  | JE24042218 | unknown WHANGAEHU VALLEY ROAD,Rangiwaea,Rural | Western | IRIRANGI | 2024-11-17 | 23:05 | 2024-11-18 | 13:24 | 0.061938 | 0.00010208 | 37 | 22450 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 107/2 Protection flags (nil where none): A & C ph E/F CAUSE: Tree through lines Location: Between poles 376306 & 375707 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: Cursory Weather (wind/rain): wind LFI (Y/N + Comments): N Follow up Required (select advisory)? N Additional fault restoration comments: Line was isolated at ABS's 4620 & 4621/1 & Links 4621/6. Crew will return in morning to remove tree and repair lines as not easy access in the dark.. Restored 13:23, Thrush Conductor, SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1750 |  | JE24040326 | 520 POLLEN STREET, THAMES, THAMES, 3500 | Eastern | POLLEN ST | 2024-11-16 | 23:01 | 2024-11-18 | 1:03 | 0.030138 | 0.00034763 | 63 | 10924 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Disconnect and remove TC5223 Disconnect and remove Reyrolle switchboard Liven generator before 0500, check phase rotation on LV bus before connecting load Install new Safelink. Install new transformer.Install 11kV cable between the CFC and the transformer Terminate the three 11kV cables into the CFC Terminate 11kV cable into the transformer Terminate LV cables onto the transformer Connect earthing to transformer and CFC. Liven CFC and Transformer. | .
1751 |  | JE24042105 | PAREWANUI | Western | PAREWANUI | 2024-11-16 | 0:20 | 2024-11-16 | 2:18 | 0.018301 | 0.0001545 | 56 | 6633 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: 742 No. Fuses: 2 Fuse Amp Size: 20 TIME CLOSED: 02:18 Cause: unknown Weather (wind/rain): calm Follow up required (select advisory)?n Line patrol done | .
1752 |  | JE24042107 | BLACK STUMP | Eastern | BLACK STUMP | 2024-11-16 | 0:28 | 2024-11-16 | 1:15 | 0.044092 | 0.00093805 | 340 | 15981 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 3 Protection flags (nil where none): A,B,C Fault, Ground Fault, OCIT CAUSE: Lines twisted together between poles 220725 & 381038. Location: Poles 220725 & 381038. Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Rain LFI (Y/N + Comments): Nil Follow up Required (select advisory)? No Additional fault restoration comments: Unsure of what caused the lines to twist together | .
1753 |  | JE24042127 | TE MATAI RD | Eastern | TE MATAI RD | 2024-11-16 | 12:51 | 2024-11-16 | 15:21 | 0.00041293 | 2.759e-06 | 1 | 150 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: SF5-206 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 15:20 Cause: Unknown, line patrolled. Weather (wind/rain): Calm Follow up required (select advisory)? N/A | .
1754 |  | JE24042148 | KOPANE | Western | KOPANE | 2024-11-16 | 18:33 | 2024-11-16 | 19:49 | 0.00021129 | 2.759e-06 | 1 | 77 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: Tfr T1/568 CAUSE: Suspect internal fault Temp generation (stage details when used): N PERFORMANCE DETAIL DNO (number or state no): N Circuit patrolled & type: N Weather (wind/rain): wind Follow up required (select advisory)?N Additional fault restoration comments: TFR Replaced, full power restored | .
1755 |  | JE24042158 | WAIHI BEACH RD | Eastern | WAIHI BEACH RD | 2024-11-16 | 19:56 | 2024-11-17 | 15:29 | 0.081477 | 0.00024831 | 66 | 29532 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: Sectionaliser 13200 Protection flags (nil where none): EF, Phase C-OC CAUSE: Rotten cross arm Location: POLE 876771 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): N Follow up Required (select advisory)? Yes Additional fault restoration comments: Circuit Partially Restored upto Line Break at Pole P13626. One conductor onto the deck into aa gulley. Job can only be done during daytime. Made a line Break at Pole P13626 and relivened upto Line Break. Work to continue early morning 17/11/24 Line repaired, replaced 3m HV rotten cross arm, re-joined the conductors. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1756 |  | JE24042162 | TOWNSHIP & LS | Eastern | TOWNSHIP & LS | 2024-11-16 | 21:42 | 2024-11-16 | 22:54 | 0.014639 | 0.00036694 | 133 | 5306 | Unplanned | WILDLIFE - POSSUM | REGULATORY INFORMATION Voltage & Device ID: Recloser 14697 Protection flags (nil where none): EF CAUSE: Possum Location: Pole C1662 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Sectionalised feeder. Opened Sectionaliser 14707 and closed backfeed Sectionaliser 14423.Line patrolled between Rec 146 97 and Sectionaliser 14707. Possum found on the ground at pole C1662. Power restored and feeder normalised SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): No Circuit that tripped: N/A DTF (KM):N/A | .
1757 |  | JE24036766 | SEAFORTH RD | Eastern | SEAFORTH RD | 2024-11-15 | 9:08 | 2024-11-15 | 11:22 | 0.07525 | 0.00056283 | 204 | 27275 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Link Box Maintenance on SA2-058 | .
1758 |  | JE24038948 | PORTSIDE | Eastern | PORTSIDE | 2024-11-15 | 9:19 | 2024-11-15 | 12:50 | 0.098646 | 0.00046626 | 169 | 35755 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace all x-arms on pole 213830 | .
1759 |  | JE24041914 | 9 MAIN STREET, HUNTERVILLE, HUNTERVILLE, 4730 | Western | PUTORINO | 2024-11-15 | 9:48 | 2024-11-15 | 10:11 | 0.0015462 | 6.8974e-05 | 25 | 560 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Tap down transformer Z63 due to high voltages. | .
1760 |  | JE24041963 | WESTMERE GLADSTONE | Western | WESTMERE GLADSTONE | 2024-11-15 | 3:18 | 2024-11-15 | 11:01 | 0.15477 | 0.00057662 | 195 | 56096 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kvCB c948 Protection flags (nil where none): A Fault, E/F CAUSE: Tree through lines Location: pole 419459 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: Cursory Weather (wind/rain): Rain LFI (Y/N + Comments): Nil Follow up Required (select advisory)? Additional fault restoration comments: Line patrolled and sectionalized, received call of tree through lines, line was isolated at Fuses 7842 to repair the lines. | .
1761 |  | JE24041965 | FORDELL | Western | FORDELL | 2024-11-15 | 5:13 | 2024-11-15 | 8:55 | 0.057614 | 0.00035039 | 127 | 20883 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 4200/2 Protection flags (nil where none): CAUSE: Branch through lines from Pine Trees. Location: Pole 791071 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: cursory Weather (wind/rain): wind & rain LFI (Y/N + Comments): N Follow up Required (select advisory)? Additional fault restoration comments: Line was isolated at ABS 906 to repair lines down, due to pine tree branches (forest block) | .
1762 |  | JE24041983 | PONATAHI | Western | PONATAHI | 2024-11-15 | 8:19 | 2024-11-15 | 9:23 | 0.00034903 | 5.5179e-06 | 2 | 127 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 7268 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 09:22 Cause: Unknown Weather (wind/rain): Calm, Cloudy Follow up required (select advisory)? | .
1763 |  | JE24041992 | WAITOTARA | Western | WAITOTARA | 2024-11-15 | 8:53 | 2024-11-15 | 13:09 | 0.29533 | 0.0021106 | 678 | 107043 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 242 Protection flags (nil where none): Nil CAUSE: Loss Stay wire rapped around fuses at transformer X2260 Location: pole 840092 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: cursory Weather (wind/rain): rain & wind LFI (Y/N + Comments): Y - pole 772061 Follow up Required (select advisory)? N Additional fault restoration comments: Faultman found a loss stay wire that had rapped over the transformer X2260 fuses. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1764 |  | JE24042013 | RUAWHATA | Western | RUAWHATA | 2024-11-15 | 14:24 | 2024-11-15 | 15:08 | 0.00060881 | 1.3795e-05 | 5 | 221 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: Tfr T7/534 CAUSE: Age - Had a number of lightning strikes hit tFr over time. Temp generation (stage details when used): N PERFORMANCE DETAIL DNO (number or state no): N Circuit patrolled & type: N Weather (wind/rain): Rain & Wind Follow up required (select advisory)? Additional fault restoration comments: | .
1765 |  | JE24042088 | SOUTH RD NGARIKI | Western | SOUTH RD NGARIKI | 2024-11-15 | 18:46 | 2024-11-15 | 20:11 | 0.0026019 | 3.0349e-05 | 11 | 943 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Broken insulator at Pole 713099 due to old age Isolated at Fuses NG377 Broken insulator replaced, Full power restored Dylan advised there are a lot of old insulator past Fuses NG377, there is a project to upgraded this line starting soon | .
1766 |  | JE24035460 | 20 COAST BOULEVARD PAPAMOA BEACH TAURANGA | Eastern | GRENADA ST | 2024-11-14 | 8:30 | 2024-11-14 | 16:02 | 0.089821 | 0.00019865 | 72 | 32556 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace rusted SD3 + SD2 base-units at SD switchgear 9360 | .
1767 |  | JE24038098 | 475 TE RERENGA KUAOTUNU ROAD OTAPAURAU COROMANDEL | Eastern | OWERA RD | 2024-11-14 | 7:00 | 2024-11-14 | 16:31 | 0.49526 | 0.0015064 | 512 | 179509 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV poles and crossarms at multiple sites beyond Recloser 15040 - CB1, Whitianga | .
1768 |  | JE24038642 | 357 HEREFORD ROAD OROPI TAURANGA | Eastern | WAIMAPU | 2024-11-14 | 9:04 | 2024-11-14 | 15:11 | 0.034415 | 9.3805e-05 | 34 | 12474 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles and/or crossarms 211063 (TE4-214) to 211075 (T4507) | .
1769 |  | JE24038644 | CAMBRIA LS | Western | CAMBRIA LS | 2024-11-14 | 8:46 | 2024-11-14 | 12:46 | 0.058813 | 0.00024555 | 89 | 21317 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace ABS CA460 & upgrade earthing on existing pole | .
1770 |  | JE24038647 | 80 ODEY ROAD WHAKAMARAMA | Eastern | WHAKAMARAMA | 2024-11-14 | 9:16 | 2024-11-14 | 10:53 | 0.017422 | 0.00017933 | 65 | 6315 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace X-arm on pole 210158 | .
1771 |  | JE24038808 | 424 OMANAWA ROAD OMANAWA TAURANGA | Eastern | KEENAN RD | 2024-11-14 | 8:45 | 2024-11-14 | 15:12 | 0.057814 | 0.00015174 | 55 | 20955 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv / 400vt poles 211669, 211666 & 211855 . Replace 11kv cross arm @ pole 211668. Replace 11kv conductors between poles 211855 & 211670. | .
1772 |  | JE24038815 | 188 NORWOOD LANE MARTON MARTON | Western | LEEDSTOWN 22KV | 2024-11-14 | 9:20 | 2024-11-14 | 14:19 | 0.0041148 | 1.3795e-05 | 5 | 1491 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles between poles 804863 and 804873 | .
1773 |  | JE24038905 | 2 NGAIRE STREET LONGBURN PALMERSTON NORTH | Western | DAIRYFACT | 2024-11-14 | 9:15 | 2024-11-14 | 15:07 | 0.032006 | 9.1046e-05 | 33 | 11601 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace ABS pole P44234 | .
1774 |  | JE24038933 | KUMENGA | Western | KUMENGA | 2024-11-14 | 9:01 | 2024-11-14 | 14:29 | 0.058908 | 0.00017933 | 65 | 21351 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Reconductor from 7274 to end of line , from 798438 to end of line & from 798536 to T1325 | .
1775 |  | JE24040174 | 1 PORTSIDE DRIVE, MOUNT MAUNGANUI, TAURANGA, 3116 | Eastern | HULL RD | 2024-11-14 | 23:30 | 2024-11-15 | 2:59 | 0.035221 | 0.0001683 | 61 | 12766 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - SC4-825/SC4-821/SC4-819/SC4-823 | .
1776 |  | JE24041807 | KUAOTUNU | Eastern | KUAOTUNU | 2024-11-14 | 8:53 | 2024-11-14 | 9:43 | 0.031792 | 0.00063732 | 231 | 11523 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | REGULATORY INFORMATION Voltage & Device ID: CB 3 Protection flags (nil where none): CAUSE: Broken jumper Location: at pole 854154 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (N + Comments): Follow up Required (select advisory)? No Additional fault restoration comments: BREAK BEFORE MAKE SWITCHING TO BACK FEED TO AVOID TRIPPING DUE TO PHASE IMBALANCE Jumper repaired, power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): No Circuit that tripped: N/A DTF (KM):N/A | .
1777 |  | JE24041904 | MATAROA A | Western | MATAROA A | 2024-11-14 | 13:58 | 2024-11-14 | 16:59 | 0.027407 | 0.0002621 | 95 | 9934 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Repair conductor at Pole 785938 Part power call on DTX X2581 may be a line down. De-energise feeder at REC 4692 for safety until crew are onsite to assess safety. Fault is coincidental will be repaired under 2r Replace 1 x 2A fuse at DTX X2581 | .
1778 |  | JE24041909 | PAHOIA | Eastern | PAHOIA | 2024-11-14 | 15:58 | 2024-11-14 | 16:09 | 9.7391e-05 | 8.2769e-06 | 3 | 35 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TAP CHANGE - TC2-084 - customer owns all 3 icp's on this TX tap up one tap customer aware outage required please give eta Tap 2 = Two phase system-Red -Blue = 473V A-N =235V C-N = 236V Tap 3 Red -Blue 482V A-N = 241V C-N = 240V Power Off = 15:57 Power ON =16:09 | .
1779 |  | JE24037607 | COLVILLE | Eastern | COLVILLE | 2024-11-13 | 8:30 | 2024-11-13 | 16:15 | 0.6947 | 0.0017078 | 619 | 251796 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace poles and crossarms beyond RP15 - CB1, Coromandel | .
1780 |  | JE24038245 | CENTRAL TRITON | Eastern | CENTRAL TRITON | 2024-11-13 | 9:34 | 2024-11-13 | 11:21 | 0.0011713 | 1.1036e-05 | 4 | 425 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Linkbox maintenance at TC4-177 | .
1781 |  | JE24038298 | 521 MAUNGARANGI ROAD PAENGAROA TE PUKE | Eastern | MANGOREWA | 2024-11-13 | 9:11 | 2024-11-13 | 15:15 | 0.043193 | 0.00011864 | 43 | 15656 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv overhead conductors between poles 221849 & 221860 with ACSR Ferret | .
1782 |  | JE24038570 | 123 RATANA ROAD RATANA WANGANUI | Western | TURAKINA | 2024-11-13 | 8:31 | 2024-11-13 | 14:15 | 0.013314 | 3.8625e-05 | 14 | 4826 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles and crossarms from and including 794756 to 794735. | .
1783 |  | JE24038585 | 118 COBDEN ROAD CARRINGTON CARTERTON | Western | BELVEDERE | 2024-11-13 | 8:55 | 2024-11-13 | 15:10 | 0.0031022 | 8.2769e-06 | 3 | 1124 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV Pole 940306 and relocate existing transformer T948 to new site. Remove poles 940306 and old T948 structure 817569 and the existing span of 11kv crossing the existing Dam this due to repeating swans clashing the lines. | .
1784 |  | JE24038610 | 328 JEFFERSONS LINE MARTON MARTON | Western | TUTAENUI | 2024-11-13 | 9:00 | 2024-11-13 | 14:39 | 0.20116 | 0.00059318 | 215 | 72910 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replacing X arms poles 804055, 804078. 804105 new fuses installed at these sites, replace fuses 426 with links, replace fuses 081 | .
1785 |  | JE24038641 | KUMENGA | Western | KUMENGA | 2024-11-13 | 9:00 | 2024-11-13 | 13:15 | 0.025342 | 9.9323e-05 | 36 | 9185 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove ABS S508 and install new automated Entec switch | .
1786 |  | JE24038798 | 14 KANE ROAD PAPAMOA BEACH TAURANGA | Eastern | EVANS RD | 2024-11-13 | 13:33 | 2024-11-13 | 15:02 | 0.032179 | 0.00036142 | 131 | 11663 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | linkbox Maintenance at TD5-194 | .
1787 |  | JE24038971 | 627 TARATA ROAD KAIMATA INGLEWOOD | Western | KAIMATA | 2024-11-13 | 9:16 | 2024-11-13 | 13:43 | 0.0036786 | 1.3795e-05 | 5 | 1333 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 760616. Replace arms at poles 760607,760608,760610,760611,760613,760614,760615,760617 | .
1788 |  | JE24039022 | 310 OPAKI KAIPARORO ROAD EKETAHUNA EKETAHUNA | Western | MAURICEVILLE | 2024-11-13 | 9:32 | 2024-11-13 | 15:51 | 0.062494 | 0.0001683 | 61 | 22651 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace pole P12972 with new 12.5 Busck pole and install a new recloser and commission . | .
1789 |  | JE24039147 | 8 PINELAND DRIVE TURITEA | Western | AOKAUTERE | 2024-11-13 | 9:16 | 2024-11-13 | 13:35 | 0.031706 | 0.00012415 | 45 | 11492 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT - Replace all crossarms on poles P26385 & P05680. | .
1790 |  | JE24041609 | HORAHORA | Eastern | HORAHORA | 2024-11-13 | 1:18 | 2024-11-13 | 3:49 | 0.076739 | 0.00065663 | 238 | 27814 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: Recloser 9636 Protection flags (nil where none): EF CAUSE: N/A Location: N/A Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): Yes-ABS 1314 no earths Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Line Patrolled, Nothing found | .
1791 |  | JE24041610 | TE MATAI RD | Eastern | TE MATAI RD | 2024-11-13 | 6:27 | 2024-11-13 | 9:54 | 0.0017166 | 8.2769e-06 | 3 | 622 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1x fuse blown initially. Fuse holder broken at fuses FP995. Isolated at SE5-287, SE5-139, Sw/Gear 13655/4 & Links 14923/4 to allow the replacement off the full set. | .
1792 |  | JE24041611 | MANGOREWA | Eastern | MANGOREWA | 2024-11-13 | 2:53 | 2024-11-13 | 15:15 | 0.067874 | 0.0013353 | 484 | 24601 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: Sectionaliser 9689 - Protection flags (nil where none): EF OC Phase C CAUSE: Tree on lines Location: Between Poles 230118 and 230119 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y + Comments): LFIs at Pole 221847 Lit at PGA6 Follow up Required (select advisory)? No Additional fault restoration comments: Job to be done during day as line passes through forestry and tree cutters required-Also NAPA planned for today same area, jobs will be combined-Power restored under NAPA 116210 | .
1793 |  | JE24041612 | KAIHERE | Eastern | KAIHERE | 2024-11-13 | 8:23 | 2024-11-13 | 9:14 | 0.001261 | 2.4831e-05 | 9 | 457 | Unplanned | WILDLIFE - BIRD | Jumper blown off at Pole O129 due to duck flying into lines between poles 384268 & O134. Isolated at ABS 1245 to allow repairs all jumpers replaced | .
1794 |  | JE24041652 | 75 WAIHI ROAD JUDEA TAURANGA | Eastern | WAIHI RD | 2024-11-13 | 23:30 | 2024-11-14 | 5:14 | 0.059723 | 0.00017381 | 63 | 21647 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Maintenance on RMU 11kv - 9106/1/2/3/4/5 | .
1795 |  | JE24041662 | APITI | Western | APITI | 2024-11-13 | 12:52 | 2024-11-13 | 13:37 | 0.0016038 | 3.5867e-05 | 13 | 581 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Burning cross Arm at Pole P03573, due to cracked insulator Isolated at ABS P54 Cross arm Replaced, Full power restored | .
1796 |  | JE24041672 | WAREA | Western | WAREA | 2024-11-13 | 10:29 | 2024-11-13 | 12:44 | 0.0022348 | 1.6554e-05 | 6 | 810 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1 x line down at Pole 479803 Line down caused by a broken sleeve | .
1797 |  | JE24041674 | 2645 LAKE FERRY ROAD, MARTINBOROUGH | Western | BURNSIDE | 2024-11-13 | 12:04 | 2024-11-13 | 12:57 | 0.00029236 | 5.5179e-06 | 2 | 106 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Blown Jumper at Fuses 7438 (Pole 797694), due to old age Isolated & Earthed at Fuses 7438 Jumper repaired, Full power restored | .
1798 |  | JE24041679 | 168A Nannestads Line, Bunnythorpe, Palmerston North, 4775 | Western | BUNNYTHORPE | 2024-11-13 | 15:10 | 2024-11-13 | 15:13 | 5.1501e-05 | 1.9313e-05 | 7 | 19 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | High LV voltage off TFR 7634, above 248V's at LV bushings De-energised TFR 7634, Tapped down to Tap 2, Re-energised TFR 7634 New Voltages R- 237V, Y-236V & B-238V This is a newly install TFR to a Subdivision for some reason it was install on Tap 3 which is not its nominal Tap | .
1799 |  | JE24041769 | TE ROTI | Western | TE ROTI | 2024-11-13 | 21:09 | 2024-11-14 | 0:52 | 0.0079899 | 3.5867e-05 | 13 | 2896 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: 2220T No. Fuses: 2 Fuse Amp Size: Failed TIME CLOSED: Cause: Faulty transformer Weather (wind/rain): Calm Follow up required (select advisory)? N Transformer 2220T faulty, No earthing spickets. So Isolated at Links 12281/4 & ABS 6004 Transformer replaced Power restored 00:51 | .
1800 |  | JE24041772 | KUMENGA | Western | KUMENGA | 2024-11-13 | 21:09 | 2024-11-13 | 22:56 | 0.00029378 | 2.759e-06 | 1 | 106 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 7302 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 22:55 Cause: Suspect Bird Strike Weather (wind/rain): Slight breeze Follow up required (select advisory)? | .
1801 |  | JE24041775 | RUAWHATA | Western | RUAWHATA | 2024-11-13 | 22:56 | 2024-11-14 | 0:12 | 0.012476 | 0.00032004 | 116 | 4522 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Broken Jumper found at Fuses 10320 Isolated at ABS's Q67 & 10271 Back feed installed via recloser Q77 LFI's active at Pole P45962 Checks carried out past LFI's, with nothing found | .
1802 |  | JE24038083 | 475 TE RERENGA KUAOTUNU ROAD OTAPAURAU COROMANDEL | Eastern | OWERA RD | 2024-11-12 | 7:01 | 2024-11-12 | 15:45 | 0.50811 | 0.0015119 | 514 | 184166 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace 11kV poles and crossarms at multiple sites beyond Recloser 15040 - CB1, Whitianga | .
1803 |  | JE24038099 | 2 MAUNGAWHARE PLACE OTUMOETAI TAURANGA | Eastern | CENTRAL OTUMOETAI | 2024-11-12 | 9:31 | 2024-11-12 | 11:12 | 0.026468 | 0.0002621 | 95 | 9593 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Linkbox maintenance at TD4-085 | .
1804 |  | JE24038110 | 205 LOWER STUART ROAD ELTHAM HAWERA | Western | MANGATOKI | 2024-11-12 | 9:04 | 2024-11-12 | 14:35 | 0.0027423 | 8.2769e-06 | 3 | 994 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install new 11m HV pole in between poles 733388 - 733389 | .
1805 |  | JE24038284 | OKOROIRE | Eastern | OKOROIRE | 2024-11-12 | 8:31 | 2024-11-12 | 12:51 | 0.0251 | 9.6564e-05 | 35 | 9098 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace D12911 with 11m Busck. Install new Entec Sectionaliser incl solid links. | .
1806 |  | JE24038376 | 91 SLOSS ROAD TOKOROA TOKOROA | Eastern | CAMPBELL ST | 2024-11-12 | 9:46 | 2024-11-12 | 11:36 | 0.0069781 | 6.3456e-05 | 23 | 2529 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE HV PIN ARMS AT POLES B0232 & B0233 | .
1807 |  | JE24038392 | 54 VILES ROAD WESTERN LAKE FEATHERSTON | Western | REVANS ST | 2024-11-12 | 9:01 | 2024-11-12 | 14:40 | 0.010808 | 3.3108e-05 | 12 | 3917 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | reconductor 11kv from 7261 to end of line | .
1808 |  | JE24038462 | 163 PILLANS ROAD OTUMOETAI TAURANGA | Eastern | BURETA RD | 2024-11-12 | 13:01 | 2024-11-12 | 14:32 | 0.030409 | 0.00033108 | 120 | 11022 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Linkbox maintenance at TC4-013 | .
1809 |  | JE24038522 | 905 OROPI ROAD OROPI TAURANGA | Eastern | WAIMAPU | 2024-11-12 | 9:16 | 2024-11-12 | 15:25 | 0.13427 | 0.00036418 | 132 | 48666 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 211033 to 211047 | .
1810 |  | JE24038562 | KAIMAI DRIVE | Eastern | KAIMAI DRIVE | 2024-11-12 | 8:48 | 2024-11-12 | 14:46 | 0.053026 | 0.00015174 | 55 | 19219 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv / 400vt poles 211664, 211670. & 211665. Replace 11kv cross arms @ pole 211667. Install and commission new ENTEC sectionaliser 15036. Remove ABS SE3-010 | .
1811 |  | JE24038604 | 22 CLYDE STREET MASTERTON MASTERTON | Western | CHURCH ST | 2024-11-12 | 8:46 | 2024-11-12 | 16:06 | 0.086691 | 0.00019865 | 72 | 31422 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace transformer pole T1923 and re sag 11kv conductors at pole 361439 | .
1812 |  | JE24039265 | 653 TAIRUA WHITIANGA ROAD WHENUAKITE WHITIANGA | Eastern | TAIRUA NORTH | 2024-11-12 | 9:43 | 2024-11-12 | 14:45 | 0.034954 | 0.00011588 | 42 | 12669 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles W1936 and W13417 | .
1813 |  | JE24040226 | KAPANGA ROAD | Eastern | KAPANGA ROAD | 2024-11-12 | 14:18 | 2024-11-12 | 15:03 | 0.27544 | 0.011905 | 2351 | 99834 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Coromandel Generator Project Switch network into configuration required for on network testing. Complete pre-commissioning checks/tests on Whangapoua generator control systems. Complete on network testing including grid tied run, grid to island run, island start and grid resynch tests. Re switching please refer to attached switching methodology & commissioning brief . | .
1814 |  | JE24040318 | DAIRYFACT | Western | DAIRYFACT | 2024-11-12 | 9:15 | 2024-11-12 | 14:31 | 0.005223 | 1.6554e-05 | 6 | 1893 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace TX structure at T6/72 | .
1815 |  | JE24041437 | RONGOTEA | Western | RONGOTEA | 2024-11-12 | 4:34 | 2024-11-12 | 7:26 | 0.00047309 | 2.759e-06 | 1 | 171 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: O79 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 1 at 06:40, 2nd at 07:25 Cause: Deterioration Weather (wind/rain): Calm Follow up required (select advisory)? Note: Replaced 1x Fuse at 06:40, Still no power so went back and found the 2nd blown Fuse closed at 07:25. | .
1816 |  | JE24041439 | RAILWAY ST | Eastern | RAILWAY ST | 2024-11-12 | 5:44 | 2024-11-12 | 7:42 | 0.18925 | 0.0020885 | 757 | 68595 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 2 Protection flags (nil where none): O/C A - B - C Ø CAUSE: Unknown Location: Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): NO Circuit patrolled and type: Cursory Weather (wind/rain): Fine LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Line sectionalised & Patrolled | .
1817 |  | JE24041440 | THOMAS ROAD | Eastern | THOMAS ROAD | 2024-11-12 | 6:15 | 2024-11-12 | 9:45 | 0.0056663 | 3.0349e-05 | 11 | 2054 | Unplanned | WILDLIFE - BIRD | Fuses Location: FP409 No. Fuses: 2 Fuse Amp Size: 6amp TIME CLOSED: 09:19 Cause: Duck in lines at pole on private lines Weather (wind/rain): fine Follow up required (select advisory)? Fuses Location: FP1979 No. Fuses: 2 Fuse Amp Size: 8amp TIME CLOSED: 09:38 Cause: Duck in lines at pole on private lines Weather (wind/rain): fine Follow up required (select advisory)? Fuses Location: FP1813 No. Fuses: 1 Fuse Amp Size: 10amp TIME CLOSED: 09:45 Cause: Duck in lines at pole on private lines Weather (wind/rain): fine Follow up required (select advisory)? Duck through he lines on private lines caused all 3 sets of line fuses to blow | .
1818 |  | JE24041444 | 48 REDWOOD LANE, TAURANGA | Eastern | KAIMAI DRIVE | 2024-11-12 | 7:47 | 2024-11-12 | 9:36 | 0.00033025 | 1.9313e-05 | 7 | 120 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV Fuse switch 14910/2 Protection flags (nil when none): Nil CAUSE: Tree through the lines at pole 211537, line down Location: Pole 211537 Temp generation (state details when used): no PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Cursory Weather (wind/rain): Fine Follow up required (select advisory)? No Additional fault restoration comments: Isolated at Fuses SD3-123 to allow repairs to lines. Fuse/Sw 14910/2 found blown at restoration on supply. 1x6amp fuse replaced | .
1819 |  | JE24041449 | LINTON | Western | LINTON | 2024-11-12 | 7:45 | 2024-11-12 | 9:14 | 0.00073805 | 8.2769e-06 | 3 | 268 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Fuses Location: H116 No. Fuses: 2 Fuse Amp Size: 20 Amp TIME CLOSED: 09:14 Cause: Truck contact Weather (wind/rain): Calm Follow up required (select advisory)? N | .
1820 |  | JE24041458 | STATION RD | Eastern | STATION RD | 2024-11-12 | 12:52 | 2024-11-12 | 13:06 | 0.00011063 | 8.2769e-06 | 3 | 40 | Unplanned | WILDLIFE - POSSUM | Remove dead possum from Transformer TC487 LV bushings. Isolated at Fuses FC2446 to allow safe removal of possum | .
1821 |  | JE24041463 | RUAPEHU | Western | RUAPEHU | 2024-11-12 | 10:00 | 2024-11-12 | 10:56 | 0.00015427 | 2.759e-06 | 1 | 56 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Pole 7788571 Protection flags (nil where none): CAUSE: Centre Bolt fallen out Location: Pole 778571 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1822 |  | JE24041505 | MATAPU | Western | MATAPU | 2024-11-12 | 10:09 | 2024-11-12 | 16:21 | 0.077394 | 0.0012139 | 220 | 28052 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Transformer DTX K4100 Failed 3 Phase 50kVA Protection flags (nil where none): E/F CAUSE: 11kV Transformer DTX K4100 Failed 3 Phase 50kVA Flashed over on D/Outs and damaged all 3 D/Outs Location: DTX K4100 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Curse Weather (wind/rain): Calm LFI (Y/N + Comments): ABS KA752 Comments below Follow up Required (select advisory)? Additional fault restoration comments: 11kV Transformer DTX K4100 Failed 3 Phase 50kVA Flashed over on D/Outs and damaged all 3 D/Outs , Fault Locator operated on restoration @ ABS KA752 Site ??? ABS KA704 was open at the time so the fault was isolated away??? Yet Locator operated. Replaced, Transformer, D/Outs, and lowered Structure to regulation Height, Locators @ KA752 gave incorrect reading. or may have been multi faults?? SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1823 |  | JE24041509 | FEATHERSTON No 1 33kV | Western | FEATHERSTON No 1 33kV | 2024-11-12 | 9:00 | 2024-11-12 | 9:24 | 0.061683 | 0.0027921 | 1012 | 22357 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: REC 3139 / REC 3141 Protection flags (nil where none): B phase OC EF CAUSE: Unknown Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): Fine LFI (Y/N + Comments): LFIs have been removed from Pole 370631, SCAD to remove from the page Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): TUH Sub Circuit that tripped: 3139 / 3141 Bidwells to Tuhitarata 33kV DTF (KM):N/A | .
1824 |  | JE24038034 | 101 NGARIKI ROAD RAHOTU OPUNAKE | Western | SOUTH RD NGARIKI | 2024-11-11 | 9:15 | 2024-11-11 | 15:27 | 0.0030717 | 8.2769e-06 | 3 | 1113 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace poles 712379, 712380, 712381, 712382, 712383, 712384, 712385, 712386, 712387 & 712388 | .
1825 |  | JE24038271 | ROYDEN DOWNS RD | Eastern | ROYDEN DOWNS RD | 2024-11-11 | 10:06 | 2024-11-11 | 13:41 | 0.066235 | 0.000309 | 112 | 24007 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Commission 3c 185mm 11kV cable between 11kV Poles 221847 & 221849. Remove redundant overhead conductors between 11kV Poles 221847 & 221849. Remove redundant 11kV Pole 221848. Transpower 110kV Owhata-Te Matai-Tarukenga circuit outage. | .
1826 |  | JE24038627 | KAIMATA | Western | KAIMATA | 2024-11-11 | 8:30 | 2024-11-11 | 15:07 | 0.016418 | 4.1384e-05 | 15 | 5951 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 760513,760511,760510. Replace crossarms at pole 760531 | .
1827 |  | JE24039464 | 180 RATANA ROAD RATANA WANGANUI | Western | TURAKINA | 2024-11-11 | 8:45 | 2024-11-11 | 16:53 | 0.20706 | 0.00042488 | 154 | 75049 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles and xarms from and including 360746 to 794766 | .
1828 |  | JE24040078 | 211 TOTARA STREET MOUNT MAUNGANUI TAURANGA | Eastern | CRANE SUPPLY | 2024-11-11 | 18:06 | 2024-11-12 | 1:59 | 0.0013051 | 2.759e-06 | 1 | 473 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace insulating oil in TC4-310 with new oil. Streamline new oil. Unit must settle for at least 6hrs after filling | .
1829 |  | JE24041091 | BLAIRLOGIE | Western | BLAIRLOGIE | 2024-11-11 | 9:31 | 2024-11-11 | 10:57 | 0.10116 | 0.001167 | 423 | 36667 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace broken 11KV Dropout Fuses Recloser 8097/2 failed to close on completion of work. ABS 8097/1 closed to restore power. After discussion with tech, re-booted recloser Issues with tie in with new generator site. Recloser closer & by pass opened | .
1830 |  | JE24041307 | WHARAWHARA ROAD | Eastern | WHARAWHARA ROAD | 2024-11-11 | 9:20 | 2024-11-11 | 9:31 | 6.1985e-05 | 5.5179e-06 | 2 | 22 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Open ABS S5626, Reload Fuses SB1-078, Close ABS S5626 Fuses Location: SB1-078 No. Fuses: 1 Fuse Amp Size: 65Amp TIME CLOSED: 0931 Cause: Unknown Weather (wind/rain): rain Follow up required (select advisory)?n Line was patrolled | .
1831 |  | JE24041360 | COROGLEN | Eastern | COROGLEN | 2024-11-11 | 12:01 | 2024-11-11 | 21:06 | 0.12149 | 0.0023865 | 853 | 44035 | Unplanned | THIRD PARTY INTERFERENCE - OVERHEAD CONTACT | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 9512/2 Protection flags (nil where none): E/F, O/C B & C CAUSE: Truck has hit the road crossing lines and pulled the lines down and a pole Location: Pole W1386 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: n Weather (wind/rain): calm LFI (Y/N + Comments): y, operated at pole W13361 Follow up Required (select advisory)? n Additional fault restoration comments: A truck has pulled down pole W1386 and the road crossing lines between Poles W1342 & W1388 Faulty network I & E between ABS IC2589 & IC399 Back feeds put in place for lines past ABS IC399 Line Break cut at Pole W1342, power restored to all but one TFR TC4256 Pole, crossarms and 100m Squirrel conductor replaced. NDR to follow SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1832 |  | JE24041361 | MANGATARATA | Eastern | MANGATARATA | 2024-11-11 | 12:00 | 2024-11-11 | 12:14 | 0.00071543 | 5.242e-05 | 19 | 259 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | NAPA 117057 , was meant to be live line work - job scope changed Contractors arrived onsite for LLP 117057-02, They found that the broken binder that was to be replaced under the LLP was millimeters away from the cross arm, the binder was arcing causing burning on the cross arm due to this it was determined that the binder could not be replaced under the LLP Back feed put in place, Line was de-energised between Sec 14730 & ABS IC2655 Binder was replaced using LLP techniques as per LLP 117057-02 Fault fixed, full power restored | .
1833 |  | JE24040155 | 1855 LAKE FERRY ROAD PIRINOA FEATHERSTON | Western | BURNSIDE | 2024-11-10 | 9:01 | 2024-11-10 | 10:18 | 0.00021226 | 2.759e-06 | 1 | 77 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re sag 11kv lines between poles 810873 and 853130 | .
1834 |  | JE24040170 | 2072 LAKE FERRY ROAD PIRINOA FEATHERSTON | Western | BURNSIDE | 2024-11-10 | 11:31 | 2024-11-10 | 14:16 | 0.0018189 | 1.1036e-05 | 4 | 659 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re Sag 11kv lines and remove / clear bad burning trees | .
1835 |  | JE24041281 | GORDON ST | Western | GORDON ST | 2024-11-10 | 11:53 | 2024-11-10 | 19:20 | 0.28249 | 0.0031176 | 1030 | 102389 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB C827 Protection flags (nil where none): O/C B & C CAUSE: Car V Pole // Blown Jumpers Location: 825792 // 825780 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: No Weather (wind/rain): rain LFI (Y/N + Comments): no Follow up Required (select advisory)? NDR to follow Additional fault restoration comments: Car V pole 825792, Isolated at ABS S191, Pole replaced, Faultman found blown jumpers on ABS S191(Pole 825780) source side due to fault current, Isolated at ABS S130 & S136, Jumpers Repaired, Full power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): n Circuit that tripped: n DTF (KM):n ETA 10 - 15 Mins | .
1836 |  | JE24041289 | TAWHITI RD | Western | TAWHITI RD | 2024-11-10 | 14:09 | 2024-11-10 | 18:38 | 0.016029 | 0.00024279 | 88 | 5810 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Car V Pole 725082 Isolated at ABS 6403 & ABS CA433 Backfeed in at Sec 12437 Also Put New Bolt in Cross arm at Pole 725081 as was nearly Out and rusty | .
1837 |  | JE24041292 | AOKAUTERE | Western | AOKAUTERE | 2024-11-10 | 15:21 | 2024-11-10 | 15:39 | 0.0033434 | 0.00018485 | 67 | 1212 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: T2/860 No. Fuses: 1 Fuse Amp Size: 3 Amp & Candle TIME CLOSED: Cause: Weather (wind/rain): Follow up required (select advisory)? Had to isolate at Recloser 10367 for safety has could not get Half of the Candle out of the DDO Removed using Gloves and Hot stick | .
1838 |  | JE24038022 | 635 PAIERAU ROAD OPAKI MASTERTON | Western | MOUNT BRUCE | 2024-11-09 | 8:30 | 2024-11-09 | 10:49 | 0.0011465 | 8.2769e-06 | 3 | 416 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace red tag poles 831943 and 831941 | .
1839 |  | JE24041228 | OTAKEHO | Western | OTAKEHO | 2024-11-09 | 12:28 | 2024-11-09 | 14:52 | 0.010662 | 7.4492e-05 | 27 | 3865 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | When doing a reload / Reliven 1 of the DDOs broke o On closer Inspection The Crossarms also needed Replacement ( Top Arm ,Fuse arm Replaced all 3 DDOs Isolated at Fuses MA 233 | .
1840 |  | JE24041236 | AWAITI | Eastern | AWAITI | 2024-11-09 | 12:00 | 2024-11-09 | 13:46 | 0.025359 | 0.00024003 | 87 | 9192 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | REGULATORY INFORMATION Voltage & Device ID: CB 2 Protection flags (nil where none): Nil CAUSE: Broken jumper Location: O1540 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4, not patrolled Weather (wind/rain): Calm LFI (Y/N + Comments): Yes, not flagged. Follow up Required (select advisory)? No Additional fault restoration comments: Broken jumper at Pole O1540 Replace 3 x 25mm² HD Cu conductor droppers 3 x HV fuse bases, holders and carriers 3 x 3A HV fuses 3 x HV connectors SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1841 |  | JE24041252 | WAITOTARA | Western | WAITOTARA | 2024-11-09 | 17:41 | 2024-11-09 | 23:02 | 0.078911 | 0.00024555 | 89 | 28602 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kv REC 693 Protection flags (nil where none): A & C Phase O/C E/F CAUSE: Lines Down x 2 locations - suspect bird strike Location: 781852 & 781767 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: cursory Weather (wind/rain): wind LFI (Y/N + Comments): N Follow up Required (select advisory)? N Additional fault restoration comments: Received a call from Fire Comms of lines down, Line was isolated at ABS 693/1 & Links 693/6 to repair lines at 2 locations. | .
1842 |  | JE24041256 | KATERE 5 | Western | KATERE 5 | 2024-11-09 | 21:18 | 2024-11-09 | 22:39 | 0.0049058 | 6.0697e-05 | 22 | 1778 | Unplanned | WILDLIFE - BIRD | Fuses Location: 6542 & 8195 No. Fuses: 2 & 2 Fuse Amp Size: 3 amp & 10 amp TIME CLOSED: 22:17 & 22: 38 Cause: Bird Strike Weather (wind/rain): wind Follow up required (select advisory)? N | .
1843 |  | JE24036770 | 23 CAPAMAGIAN DRIVE ATHENREE KATIKATI | Eastern | ATHENREE | 2024-11-08 | 10:00 | 2024-11-08 | 11:51 | 0.0088771 | 8.001e-05 | 29 | 3218 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Maintenance on Link Box SA2-030 | .
1844 |  | JE24036890 | 1522 PONATAHI ROAD PONATAHI CARTERTON | Western | PARK RD | 2024-11-08 | 8:45 | 2024-11-08 | 10:16 | 0.0069886 | 7.7251e-05 | 28 | 2533 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Fixing sprag in the line and replacing x3 HV fuses | .
1845 |  | JE24037429 | 255 RUAHIHI ROAD LOWER KAIMAI TAURANGA | Eastern | KAIMAI DRIVE | 2024-11-08 | 8:46 | 2024-11-08 | 15:17 | 0.039894 | 0.00010208 | 37 | 14460 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | #: Replace 11kv / 400vt poles 211660, 211661 & 267825. Replace 11kv overhead conductors between poles 211660 & 211661 with AAAC Fluorine. | .
1846 |  | JE24037685 | AUROA | Western | AUROA | 2024-11-08 | 9:00 | 2024-11-08 | 10:36 | 0.0015903 | 1.6554e-05 | 6 | 576 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove redundant TX M1017 on Thomas Rd | .
1847 |  | JE24037688 | 262 PALMER ROAD KAPUNI HAWERA | Western | KAPUNI | 2024-11-08 | 11:15 | 2024-11-08 | 12:13 | 0.00031949 | 5.5179e-06 | 2 | 116 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace TX K1003 | .
1848 |  | JE24037690 | 221 FABIANS ROAD MORRISONS BUSH GREYTOWN | Western | PONATAHI | 2024-11-08 | 13:00 | 2024-11-08 | 15:27 | 0.00040649 | 2.759e-06 | 1 | 147 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace transformer hanger cross arms and repair earthing at T1637 | .
1849 |  | JE24037691 | 73 GLENMORVEN ROAD MORRISONS BUSH GREYTOWN | Western | PONATAHI | 2024-11-08 | 9:00 | 2024-11-08 | 10:07 | 0.00018361 | 2.759e-06 | 1 | 67 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace red tag pole 819052 | .
1850 |  | JE24037765 | 71 BABERTON STREET TOKOROA TOKOROA | Eastern | CAMPBELL ST | 2024-11-08 | 9:30 | 2024-11-08 | 11:53 | 0.0072847 | 0.00027866 | 101 | 2640 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Low/No Oil - To top up oil through top bung and clean up transformer on TC2997 and TC2998 | .
1851 |  | JE24037790 | PATETONGA | Eastern | PATETONGA | 2024-11-08 | 9:31 | 2024-11-08 | 14:46 | 0.027841 | 8.8287e-05 | 32 | 10091 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace crossarms on poles K1185, K1172, K13045, K1159 & replace poles K1184 & K1181. | .
1852 |  | JE24037797 | 96 WHENUKU ROAD NORMANBY HAWERA | Western | KETEMARAE RD | 2024-11-08 | 9:17 | 2024-11-08 | 13:49 | 0.023982 | 8.8287e-05 | 32 | 8692 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace pole 379268 with new 12.5m to gain height for over head conductors | .
1853 |  | JE24037799 | 112 PYES PA ROAD PYES PA TAURANGA | Eastern | MALEME ST | 2024-11-08 | 9:50 | 2024-11-08 | 14:56 | 0.064086 | 0.00020968 | 76 | 23228 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9010/1/2/3 | .
1854 |  | JE24037808 | 692 LAKE ARAPUNI ROAD ARAPUNI PUTARURU | Eastern | HORAHORA | 2024-11-08 | 8:30 | 2024-11-08 | 13:52 | 0.037247 | 0.00011588 | 42 | 13500 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace Pole M0834 with new 11m concrete busck and HV arm on Pole M12943 & M0809 | .
1855 |  | JE24038017 | 187A MOWBRAY ROAD WAHAROA MATAMATA | Eastern | MOWBRAY RD | 2024-11-08 | 8:32 | 2024-11-08 | 13:24 | 0.011281 | 3.8625e-05 | 14 | 4089 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove ABS 884. Install new Busck 11 and Entec Front mounted Sectionaliser, incl solid links (source side). Replace existing crossarms on pole H2194. Replace existing crossarms on pole H2195. | .
1856 |  | JE24038066 | MAUNGAKAWA ROAD | Eastern | MAUNGAKAWA ROAD | 2024-11-08 | 9:00 | 2024-11-08 | 12:16 | 0.0027003 | 1.3795e-05 | 5 | 979 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole C12886 | .
1857 |  | JE24038079 | 113 OPITONUI ROAD OTAPAURAU COROMANDEL | Eastern | OWERA RD | 2024-11-08 | 9:16 | 2024-11-08 | 13:25 | 0.0061907 | 2.4831e-05 | 9 | 2244 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace poles and crossarms beyond fuses FC2311 | .
1858 |  | JE24038626 | 113 PUKEWHAI ROAD PAHIATUA PAHIATUA | Western | MANGAMAIRE | 2024-11-08 | 9:48 | 2024-11-08 | 13:06 | 0.0021875 | 1.1036e-05 | 4 | 793 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace leaking TX T8/301 | .
1859 |  | JE24038812 | 589 GLENBURN ROAD GLENBURN MASTERTON | Western | WESTMERE GLADSTONE | 2024-11-08 | 11:00 | 2024-11-08 | 12:20 | 0.0059519 | 7.4492e-05 | 27 | 2157 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re sag 11kv line between poles 362600 and 832312 | .
1860 |  | JE24039170 | 124 CORBETT ROAD BELL BLOCK NEW PLYMOUTH | Western | MANGATI RD | 2024-11-08 | 9:00 | 2024-11-08 | 14:51 | 0.015464 | 4.4143e-05 | 16 | 5605 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Car vs pole, new pole taller with 11kV cable not having clearance to 400V lines. Install section new 11kV cable up pole 947521 and joint to existing CB1 cable. Test and restore. | .
1861 |  | JE24041066 | ASHHURST | Western | ASHHURST | 2024-11-08 | 5:15 | 2024-11-08 | 6:05 | 0.046982 | 0.0009546 | 346 | 17029 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Replace Fuses F13 pole P07794 | .
1862 |  | JE24041072 | INLAND COAST | Western | INLAND COAST | 2024-11-08 | 6:01 | 2024-11-08 | 7:25 | 0.012896 | 0.0001545 | 56 | 4674 | Unplanned | WILDLIFE - BIRD | Fuses Location: 8470 No. Fuses: 2 Fuse Amp Size: 20A TIME CLOSED: 07:24 Cause: bird Weather (wind/rain): calm Follow up required (select advisory)? | .
1863 |  | JE24041077 | KATERE 5 | Western | KATERE 5 | 2024-11-08 | 8:55 | 2024-11-08 | 9:28 | 0.0012754 | 3.8625e-05 | 14 | 462 | Unplanned | WILDLIFE - BIRD | Fuses Location: 8196 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 09:27 Cause: Bird Strike Weather (wind/rain): calm/ over cast Follow up required (select advisory)? | .
1864 |  | JE24041159 | DAIRY FACTORY | Western | DAIRY FACTORY | 2024-11-08 | 13:01 | 2024-11-08 | 14:00 | 0.00032822 | 5.5179e-06 | 2 | 119 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Faultman found lv lines down at pole 872891, due to high winds, transformer T2832 was isolated so that lv lines could be repaired as there were no isolation point on lv side of transformer. | .
1865 |  | JE24041170 | TE MATAI RD | Eastern | TE MATAI RD | 2024-11-08 | 17:01 | 2024-11-08 | 19:07 | 0.027131 | 0.00026486 | 87 | 9834 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: deterioration What was replaced? 2 X CROSSARMS AND BOLTS Where was it replaced (pole) Is 2R required? Y 2R Y - What is the timeframe for repairs? this afternoon/evening Additional Info: crew coming out to replace HV cross arms under 2R 2 x cross arms replaced and power restored | .
1866 |  | JE24041178 | MOUNTAIN | Eastern | MOUNTAIN | 2024-11-08 | 13:21 | 2024-11-08 | 15:11 | 0.00030261 | 2.759e-06 | 1 | 110 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: FP358 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 15:10 Cause: Unknown, lines patrolled. Weather (wind/rain): Calm Follow up required (select advisory)?no High loop at TC5546 due blown HV fuses at FP358. Loop test 0.1Ω | .
1867 |  | JE24041200 | MANGATAINOKA | Western | MANGATAINOKA | 2024-11-08 | 16:46 | 2024-11-08 | 18:11 | 0.00094007 | 1.1036e-05 | 4 | 341 | Unplanned | THIRD PARTY INTERFERENCE - OVERHEAD CONTACT | Faultman isolated transformer T7/96 to repair LV lines hit by tractor from Higgons Job was not at T7/97 that was the nearest transformer to address. | .
1868 |  | JE24041222 | LINTON | Western | LINTON | 2024-11-08 | 23:26 | 2024-11-08 | 23:50 | 0.0026922 | 0.00011312 | 41 | 976 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Jumper to DTX T2/491 Fuses has blown off the main line. Outage from Fuses H134 to repair jumper | .
1869 |  | JE24041404 | GRAVATT RD | Eastern | GRAVATT RD | 2024-11-08 | 9:30 | 2024-11-08 | 10:50 | 0.0068337 | 8.5528e-05 | 31 | 2477 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove Generator & Connect LV cables after Car Vs pole JE24040483 | .
1870 |  | JE24037629 | 52 CROSS CREEK ROAD WESTERN LAKE FEATHERSTON | Western | REVANS ST | 2024-11-07 | 9:01 | 2024-11-07 | 14:02 | 0.011648 | 3.8625e-05 | 14 | 4222 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | change 11kv arms fro 7274 to end of line | .
1871 |  | JE24037667 | 28 CHUDLEIGH ROAD, TE AROHA | Eastern | NGARUA | 2024-11-07 | 8:38 | 2024-11-07 | 14:23 | 0.03423 | 9.9323e-05 | 36 | 12407 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV cross arms on poles C3520, C3540, C3600, C3640, C3680, C13045, C3790 & C13052 | .
1872 |  | JE24037670 | 1 HENDERSONS LINE KELVIN GROVE PALMERSTON NORTH | Western | ASHHURST | 2024-11-07 | 8:30 | 2024-11-07 | 12:26 | 0.04089 | 0.00017381 | 63 | 14821 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | LV reconducting from P41019 up to and including P41032 | .
1873 |  | JE24037675 | LEEDSTOWN 22KV | Western | LEEDSTOWN 22KV | 2024-11-07 | 9:02 | 2024-11-07 | 15:14 | 0.0051363 | 1.3795e-05 | 5 | 1862 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles and X arms between poles 804883 and pole 804873 | .
1874 |  | JE24037692 | 11 MINARAPA ROAD OKATO NEW PLYMOUTH | Western | WAREA | 2024-11-07 | 10:01 | 2024-11-07 | 12:02 | 0.01871 | 0.0001545 | 56 | 6782 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Add Deadman to pole 478764 / 478765 and straighten network poles on Minirapa rd | .
1875 |  | JE24037742 | 320 WAIHI WHANGAMATA ROAD WAIHI WAIHI | Eastern | WHIRITOA | 2024-11-07 | 9:30 | 2024-11-07 | 14:52 | 0.042559 | 0.00013243 | 48 | 15426 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Crossarms & hardware at Pole P1527,P1524, P1523, P1521, P1522, P13385, and 876612 | .
1876 |  | JE24037761 | 27 EDINBURGH STREET TOKOROA TOKOROA | Eastern | THOMPSON DR | 2024-11-07 | 8:45 | 2024-11-07 | 9:38 | 0.013419 | 0.00025382 | 92 | 4864 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Low/No Oil - To top up oil through top bung and clean up transformer on TC2976, TC2792 | .
1877 |  | JE24038049 | 791 OROPI ROAD OROPI TAURANGA | Eastern | WAIMAPU | 2024-11-07 | 9:00 | 2024-11-07 | 14:59 | 0.13063 | 0.00036418 | 132 | 47348 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 211017 (TE4-065) to pole 211031 (TE4-113) | .
1878 |  | JE24038058 | OWERA RD | Eastern | OWERA RD | 2024-11-07 | 7:01 | 2024-11-07 | 16:29 | 0.51438 | 0.0015064 | 512 | 186438 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV poles and crossarms at multiple sites beyond Recloser 15040 - CB1, Whitianga | .
1879 |  | JE24038206 | 173 LAKE ARAPUNI ROAD ARAPUNI PUTARURU | Eastern | HORAHORA | 2024-11-07 | 9:45 | 2024-11-07 | 14:24 | 0.001539 | 5.5179e-06 | 2 | 558 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | ISOLATION OF 11KV SOUR LINE FOR TREE CLEARING between M12973 - M12974. FRANKLIN TREES | .
1880 |  | JE24038208 | 249 GRAVATT ROAD PAPAMOA BEACH TAURANGA | Eastern | PALM BEACH | 2024-11-07 | 9:45 | 2024-11-07 | 12:56 | 0.062095 | 0.00032556 | 118 | 22507 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - IP331-FP417-IP342 | .
1881 |  | JE24038244 | 467 TARATA ROAD NORFOLK INGLEWOOD | Western | KAIMATA | 2024-11-07 | 9:23 | 2024-11-07 | 15:01 | 0.013973 | 4.1384e-05 | 15 | 5065 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 761405 and hardware. Replace crossarms at pole 760570,760571,760574,760576,760578,760582 | .
1882 |  | JE24038377 | 86 ELIZABETH DRIVE TOKOROA TOKOROA | Eastern | THOMPSON DR | 2024-11-07 | 12:16 | 2024-11-07 | 12:49 | 0.0045894 | 0.00014071 | 51 | 1663 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Low/No Oil - To drop oil, repair oil leaks and replace sight perspex and top up on Transformer TC1758 | .
1883 |  | JE24040910 | RESIDENTIAL | Western | RESIDENTIAL | 2024-11-07 | 4:49 | 2024-11-07 | 6:23 | 0.39962 | 0.0047592 | 1641 | 144845 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 14 Protection flags (nil where none): A, B, C, Ph O/C CAUSE: Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): N Follow up Required (select advisory)? Additional fault restoration comments: Unable to install back feed as Automated Sw/Gear not working LFI's at Sw/Gear 10779/1 found active , LFI's at /2 & /3 not active No Fault found during sectionalizing SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1884 |  | JE24040921 | PIONEER RD | Western | PIONEER RD | 2024-11-07 | 7:41 | 2024-11-07 | 8:47 | 0.003289 | 4.9661e-05 | 18 | 1192 | Unplanned | WILDLIFE - BIRD | Fuses Location: 6774 No. Fuses: 2 Fuse Amp Size:15A TIME CLOSED: 08:47 Cause: Bird Strike Weather (wind/rain):Calm Follow up required (select advisory)? | .
1885 |  | JE24040938 | 128 RAUPUHA ROAD, STRATFORD, 4392 | Western | TOKO | 2024-11-07 | 9:59 | 2024-11-07 | 10:19 | 0.0015347 | 7.7251e-05 | 28 | 556 | Unplanned | THIRD PARTY INTERFERENCE - OTHER | Cause: Fishing line sitting on O/H HV lines Location: 740341 Isolation: Fuses 6152 Is 2R required? No Weather: Calm Additional Info: Removed fishing line from HV lines using hot stick. No other damage caused. | .
1886 |  | JE24040965 | WHITIANGA 66kV | Eastern | WHITIANGA 66kV | 2024-11-07 | 12:03 | 2024-11-07 | 12:12 | 0.11894 | 0.034873 | 12640 | 43111 | Unplanned | HUMAN ERROR - PROTECTION SETTINGS - INCORRECT/ERROR | REGULATORY INFORMATION Voltage & Device ID: CB 1092/WHT CB 70 Protection flags (nil where none): Phase C Fault, Line Diff CAUSE: Circuit tripped while opening MABS 3600 while TAI CB 60 & MABS 3600 were open Location: WHT sub Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: No Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Diffrential protection disabled at WHT , COR, TAI and KOPU GXP(David Spellman) SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Whitinaga Coromandel Circuit that tripped: WHT CB 70 DTF (KM): N/A | .
1887 |  | JE24041036 | 128 KIRK ROAD, WALTON, 3475 | Eastern | PIAKOITI RD | 2024-11-07 | 18:00 | 2024-11-07 | 21:40 | 0.0066549 | 3.0349e-05 | 11 | 2412 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV Pole H1443 Protection flags (nil where none): Nil CAUSE: Unknown Truck Hit Pole & broke it Location: Pole H1443 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Unknown who damaged it, Farmer Knows nothing, Installed New 11m Busck Double HV & LV arms. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1888 |  | JE24041049 | PITT ST | Western | PITT ST | 2024-11-07 | 17:35 | 2024-11-07 | 18:35 | 0.019658 | 0.00032556 | 118 | 7125 | Unplanned | VEGETATION - OUTSIDE ZONE | Received a call from tree contractor to advise of a tree that had fallen down onto a house and was touching the lv line, line was isolated at transformer X1667 to cut tree away as lv is hard on to transformer. Isolated at DTX 1667W Fuses, tree removed and restored. | .
1889 |  | JE24041064 | WAREA | Western | WAREA | 2024-11-07 | 20:57 | 2024-11-07 | 23:21 | 0.0023867 | 1.6554e-05 | 6 | 865 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: PU204 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 2320 Cause: Unknown Weather (wind/rain): fine Follow up required (select advisory)? | .
1890 |  | JE24037496 | 2017 PYES PA ROAD OROPI TAURANGA | Eastern | PYES PA | 2024-11-06 | 8:46 | 2024-11-06 | 14:44 | 0.040509 | 0.00011312 | 41 | 14683 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV overhead conductors between Poles 217086 & 217092 with 2W ferret. | .
1891 |  | JE24037500 | BENNETT ST | Eastern | BENNETT ST | 2024-11-06 | 9:00 | 2024-11-06 | 13:40 | 0.027067 | 9.6564e-05 | 35 | 9811 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace HT arms along Rangiora Road between N0478 - N12745 | .
1892 |  | JE24037505 | 175 PAPAWAI ROAD PAPAWAI GREYTOWN | Western | PONATAHI | 2024-11-06 | 8:45 | 2024-11-06 | 10:41 | 0.0026777 | 2.4831e-05 | 9 | 971 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace red tag pole 819373 | .
1893 |  | JE24037508 | PONATAHI | Western | PONATAHI | 2024-11-06 | 12:31 | 2024-11-06 | 15:01 | 0.0023676 | 1.6554e-05 | 6 | 858 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace red tag pole 819420 | .
1894 |  | JE24037574 | 19 COLVILLE ROAD COROMANDEL COROMANDEL | Eastern | COLVILLE | 2024-11-06 | 8:31 | 2024-11-06 | 16:59 | 0.85834 | 0.0016885 | 612 | 311110 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace poles and crossarms beyond RP15 - CB1, Coromandel Power restored late (at 16:58) due to conductors being entangled into the trees | .
1895 |  | JE24037645 | 35 MATAVAI STREET MOUNT MAUNGANUI TAURANGA | Eastern | MOUNT | 2024-11-06 | 10:16 | 2024-11-06 | 11:04 | 0.004355 | 9.1046e-05 | 33 | 1579 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Virotech Contractors to carry out Asbestos check on TD5-094 NO OUTAGE CREATED | .
1896 |  | JE24037676 | TURAKINA | Western | TURAKINA | 2024-11-06 | 9:16 | 2024-11-06 | 15:01 | 0.15981 | 0.00046351 | 168 | 57924 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles and xarms 848845, 794759, 794758, 794757, 794745, 794747, 794762. Reconductoring from pole 794762 to 848845.Install TEMP ABS TEMP123(at pole 848845). | .
1897 |  | JE24038011 | 16A HINAU STREET TOKOROA TOKOROA | Eastern | RATA ST BAIRD ROAD | 2024-11-06 | 8:39 | 2024-11-06 | 15:12 | 0.061796 | 0.00015726 | 57 | 22398 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install CFC Switchgear 14998 between IC1500 & 9189/1. Existing Transformer TC2740 connects to 14998/2. Upgrade cable between IC1500 and 14998/1 to 300mm2. | .
1898 |  | JE24038612 | 171 Old Coach Road, Eketahuna | Western | MAURICEVILLE | 2024-11-06 | 9:30 | 2024-11-06 | 14:02 | 0.0044985 | 1.6554e-05 | 6 | 1631 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To install stub pole 2x 11kv stays straighten pole P12999 and resag 11kv conductor | .
1899 |  | JE24039455 | 320 Waihi Whangamata Road, Waihi | Eastern | WAIHI NORTH | 2024-11-06 | 9:31 | 2024-11-06 | 14:33 | 0.0025028 | 8.2769e-06 | 3 | 907 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Arms & Pole P13515 and arms on Pole WHIWGM033. | .
1900 |  | JE24040829 | TAWHITI RD | Western | TAWHITI RD | 2024-11-06 | 10:42 | 2024-11-06 | 12:33 | 0.0015267 | 1.3795e-05 | 5 | 553 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: CA465 No. Fuses: 3 Fuse Amp Size: 8 TIME CLOSED: 12:32 Cause: Unknown Weather (wind/rain): rain Follow up required (select advisory)?n Line patrol done | .
1901 |  | JE24040861 | BLAIRLOGIE | Western | BLAIRLOGIE | 2024-11-06 | 14:46 | 2024-11-11 | 10:57 | 0.019232 | 2.759e-06 | 1 | 6971 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | One of the Tfr T3401 Fuses have broken and is hanging. Fuses will need to be replaced but will need a outage past REC 8097. Crew will apply for a urgent NAPA to replace. Transformer only feeds a vacant holiday batch Tfr T3401 Fuses, Open Removed & Tagged Job Completed Under Urgent NAPA 117275 - Monday 11 November & Power Restored 11:00 am | .
1902 |  | JE24040868 | TIROHIA-KARANGAHAKE | Eastern | TIROHIA-KARANGAHAKE | 2024-11-06 | 14:52 | 2024-11-06 | 15:50 | 0.00015886 | 2.759e-06 | 1 | 58 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses FC2360 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 15:50 Cause: Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)?No | .
1903 |  | JE24037316 | HORAHORA | Eastern | HORAHORA | 2024-11-05 | 9:30 | 2024-11-05 | 13:54 | 0.0021807 | 8.2769e-06 | 3 | 790 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | ISOLATION OF 11KV SPUR LINE TO ALLOW FOR TREE CLEARING between poles M0875 - 859471. FRANKLIN TREES | .
1904 |  | JE24037320 | 992 AUROA ROAD AUROA HAWERA | Western | AUROA | 2024-11-05 | 8:56 | 2024-11-05 | 14:25 | 0.021759 | 6.6215e-05 | 24 | 7887 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace TX M1358 structure | .
1905 |  | JE24037337 | 497 MOWBRAY ROAD WAHAROA MATAMATA | Eastern | MOWBRAY RD | 2024-11-05 | 9:27 | 2024-11-05 | 15:14 | 0.086137 | 0.00024831 | 90 | 31221 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace existing pole 264201 with 13.65m Busck. Install new Entec Sectionaliser including solid links (source side. | .
1906 |  | JE24037345 | 1 HENDERSONS LINE KELVIN GROVE PALMERSTON NORTH | Western | ASHHURST | 2024-11-05 | 8:30 | 2024-11-05 | 13:41 | 0.053932 | 0.00017381 | 63 | 19548 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | LV reconducting from P41776 to P41025 | .
1907 |  | JE24037348 | 101 SOUTH ROAD, KAIHERE | Eastern | KAIHERE | 2024-11-05 | 8:35 | 2024-11-05 | 14:13 | 0.0046516 | 1.3795e-05 | 5 | 1686 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV cross arms on poles 877184, O719, O720, O721 & 877185 | .
1908 |  | JE24037421 | TOTARA ST | Western | TOTARA ST | 2024-11-05 | 8:45 | 2024-11-05 | 12:11 | 0.10575 | 0.00051317 | 186 | 38328 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv pole 825244 | .
1909 |  | JE24037427 | 255 RUAHIHI ROAD LOWER KAIMAI TAURANGA | Eastern | KAIMAI DRIVE | 2024-11-05 | 8:45 | 2024-11-05 | 14:23 | 0.034485 | 0.00010208 | 37 | 12499 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv / 400vt poles 211655, 267827. Replace 11kv cross arms @ pole 267828 & 267829. Remove un- numbered stay pole | .
1910 |  | JE24037430 | 344 HOGGS ROAD RANGIWAHIA KIMBOLTON | Western | RANGIWAHIA | 2024-11-05 | 9:30 | 2024-11-05 | 13:54 | 0.0029096 | 1.1036e-05 | 4 | 1055 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace /repair crossarms on poles P05217 and P05220 | .
1911 |  | JE24037431 | 620A WESTERN LAKE ROAD WESTERN LAKE FEATHERSTON | Western | REVANS ST | 2024-11-05 | 9:03 | 2024-11-05 | 14:05 | 0.0033361 | 1.1036e-05 | 4 | 1209 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | change 11kv rms from 7272 to end of line | .
1912 |  | JE24037474 | 25 TUI STREET MOUNT MAUNGANUI TAURANGA | Eastern | TUI ST | 2024-11-05 | 10:06 | 2024-11-05 | 14:09 | 0.13251 | 0.00054352 | 197 | 48030 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9258/1/2/3/4 | .
1913 |  | JE24037577 | KAIMAI DRIVE | Eastern | KAIMAI DRIVE | 2024-11-05 | 9:00 | 2024-11-05 | 12:43 | 0.044225 | 0.00019865 | 72 | 16030 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace HT arms at poles 200484, 200523, 200532 | .
1914 |  | JE24037580 | 1641 TE WHARAU ROAD TE WHARAU MASTERTON | Western | WESTMERE GLADSTONE | 2024-11-05 | 9:16 | 2024-11-05 | 15:02 | 0.12611 | 0.00036418 | 132 | 45709 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Isolation for Vegetation cutting Between poles 442555-365081 and 370707-832115 | .
1915 |  | JE24037627 | 1917 EGMONT ROAD KAIMIRO INGLEWOOD | Western | KAIPI RD | 2024-11-05 | 9:45 | 2024-11-05 | 15:31 | 0.031861 | 9.6564e-05 | 35 | 11548 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To complete upgrade works on pole 747619 - 747620 | .
1916 |  | JE24037669 | 163 NORWOOD LANE MARTON MARTON | Western | HUNTERVILLE 22KV | 2024-11-05 | 9:03 | 2024-11-05 | 15:47 | 0.061312 | 0.00015174 | 55 | 22223 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace switch pole 804863 (ABS 539) pole 804864, run span of conductor, replace pole 804884 and other poles between, install two new sets of links on pole 804463 ABS 539 can only be operated manually now as motor has been removed | .
1917 |  | JE24038032 | 475 TE RERENGA KUAOTUNU ROAD OTAPAURAU COROMANDEL | Eastern | OWERA RD | 2024-11-05 | 7:01 | 2024-11-05 | 16:25 | 0.53377 | 0.0015064 | 512 | 193466 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV poles and crossarms at multiple sites beyond ABS 332 - CB1, Whitianga Rebuild Recloser RC15 to new ID 15040 at existing ABS site (ABS 332). Install Load and Source side Links 15040/4 & /6. SCADA Commission under AP.***** UNABLE TO COMPLETE Recloser relocation !!!! Due to GMCB 9495/1 unable to close DNO Raised, Job half done. | .
1918 |  | JE24040651 | BENT ST | Eastern | BENT ST | 2024-11-05 | 9:45 | 2024-11-05 | 10:24 | 0.0016305 | 4.1384e-05 | 15 | 591 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Burnt up LV Fuse box and holder in TFR TC2633 cubicle, old fuse holder failed causing over heating of the contacts then arcing and sparking has burnt off the contacts in the fuse box and holder I & E at Fuse/Sw FC5021 Fuse box & holder replaced, full power restored | .
1919 |  | JE24040687 | BOWENTOWN | Eastern | BOWENTOWN | 2024-11-05 | 11:17 | 2024-11-11 | 14:21 | 0.0082778 | 6.0697e-05 | 11 | 3000 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Suspected fault on TFR TA2-063 Isolated and Earthed at Fused ABS IP668 HV Cable break made at TFR TA2-100 Generator installed for TFR TA2-063, Power restored to TFR TFR TA2-100 Testing carried out on the cable & TFR TA2-063, TFR tested OK, cable found to be faulty, Powerco approved replacement New Cable run between TFR TA2-100 & TFR TA2-063 11/11/24 - Isolated and Earthed at Fused ABS IP668 (JE24041351) Generator removed from Network for TFR TA2-063 New Cable connected to TFR TA2-100 & TFR TA2-063 Full power restored to TFR TA2-100 & TFR TA2-063 | .
1920 |  | JE24040691 | RAILWAY ST | Eastern | RAILWAY ST | 2024-11-05 | 9:52 | 2024-11-05 | 11:03 | 0.079699 | 0.0020885 | 757 | 28887 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 2 Protection flags (nil where none): B Phase E/F CAUSE: Unknown, Sectionalised northing Found Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Curse Weather (wind/rain): Slight Wind LFI (Y/N + Comments): None Operated @ 14008/4 Follow up Required (select advisory)? Additional fault restoration comments: Sectionalised nothing found, Had LLP running at the same time 115749 LLP O.K SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1921 |  | JE24040761 | MAIN RD MOTONUI | Western | MAIN RD MOTONUI | 2024-11-05 | 17:11 | 2024-11-05 | 18:32 | 0.00044875 | 5.5179e-06 | 2 | 163 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: 6097 No. Fuses: 2 Fuse Amp Size: Fuses NOT blown TIME CLOSED: 18:32 Cause: Loose fuse wires? Weather (wind/rain): Calm Follow up required (select advisory)?n N | .
1922 |  | JE24037150 | 22 ROUNTREE ROAD MANGATARATA THAMES | Eastern | MANGATARATA | 2024-11-04 | 9:16 | 2024-11-04 | 13:03 | 0.0043901 | 1.9313e-05 | 7 | 1591 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace transformer hanger arm @ pole 268878 Replace hv pin pole @pole 858393 Straighten poles 858393 and pole 320593 Replace lv arm O13349 | .
1923 |  | JE24037286 | RONGOTEA | Western | RONGOTEA | 2024-11-04 | 9:49 | 2024-11-04 | 12:35 | 0.0013749 | 8.2769e-06 | 3 | 498 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace split transformer Xarms @ T1/123 | .
1924 |  | JE24037291 | 1507 OPAKI KAIPARORO ROAD MAURICEVILLE MASTERTON | Western | MAURICEVILLE | 2024-11-04 | 9:10 | 2024-11-04 | 13:44 | 0.0015114 | 5.5179e-06 | 2 | 548 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace TX arms &TX T8/151 | .
1925 |  | JE24037300 | 204 PAHOIA ROAD WHAKAMARAMA TAURANGA | Eastern | PAHOIA | 2024-11-04 | 9:12 | 2024-11-04 | 13:41 | 0.0022204 | 8.2769e-06 | 3 | 805 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To upgrade transformer TC2-084 to 30kVA 1 phase | .
1926 |  | JE24037313 | 69 BURGON ROAD OKAIAWA HAWERA | Western | OKAIAWA | 2024-11-04 | 9:06 | 2024-11-04 | 14:24 | 0.00087744 | 2.759e-06 | 1 | 318 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Rplc arms 721212, 721213, 721214, 721215, 721216, 721218, 721220, 721221, 721222, Rplc poles 721217, 721219, 721224 | .
1927 |  | JE24037420 | 608 WAIHI WHANGAMATA ROAD, WAIHI | Eastern | WHIRITOA | 2024-11-04 | 9:30 | 2024-11-04 | 13:10 | 0.029128 | 0.00013243 | 48 | 10558 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove Lv line between Poles WHIWGM067 - 263604. Replace Pole P13399. Replace 11kv pin arm on Pole P13394. Install 11kv term arm on P13394. Reinstall 11kv line between Poles P13394 & new pole (P13399). Connect new 400v cable at Pole WHIWGM067 & install pillar, connect UG service base of new pole. | .
1928 |  | JE24037454 | TOTMANS RD | Eastern | TOTMANS RD | 2024-11-04 | 8:31 | 2024-11-04 | 14:48 | 0.020822 | 5.5179e-05 | 20 | 7547 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace Pole D1490, arms on poles D1492, D1494, D12704, D12707, D1506, D1499 and 877877 | .
1929 |  | JE24038823 | 5 BENMORE AVENUE CLOVERLEA PALMERSTON NORTH | Western | TREMAINE AVE | 2024-11-04 | 8:30 | 2024-11-04 | 16:54 | 0.10423 | 0.00020692 | 75 | 37779 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Overhead to U/G conversion, Install 300m of new 11kv cable between Tx T6/408 and Switch 291. We will be carrying out a transition join before Switch 291 . Install new RMU , CFC 10945 by Tx T6/408. Replace LV pole and crossarms Sw/Gear 291 to be operated using Rope & pulley by Downer Running overtime email sent Power restored 16:53 Phasing NOT OK at Sw/Gear 10173/4 FM checked Phasing ok between Transformers T6/408 and T6/477 Cable between Sw/Gear 10173/4 & 10945/1 Isolated and Earthed Terminations changed over, Phasing Tested again. Phasing OK | .
1930 |  | JE24040524 | WAIMAPU | Eastern | WAIMAPU | 2024-11-04 | 6:08 | 2024-11-04 | 6:19 | 0.030996 | 0.0027866 | 1010 | 11235 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 1 Protection flags (nil where none): O/C B - C Ø CAUSE: Bird strike Location: Pole 210980 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: Not patrolled F3/F4 Weather (wind/rain): Calm LFI (Y/N + Comments): Yes Follow up Required (select advisory)? No Additional fault restoration comments: Shay Deegan witnessed a bird strike at pole 210980 outside his property, no damage caused. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1931 |  | JE24040554 | BLAIRLOGIE | Western | BLAIRLOGIE | 2024-11-04 | 13:15 | 2024-11-04 | 14:21 | 0.00054214 | 8.2769e-06 | 3 | 197 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Blown fuse found at Fuses 7139 Floating conductor found at Pole Isolated at fuses 7139 Floater repaired | .
1932 |  | JE24040637 | PAPAKAI | Western | PAPAKAI | 2024-11-04 | 18:57 | 2024-11-04 | 20:51 | 0.0018747 | 1.6554e-05 | 6 | 679 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 2703 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 20-50 Cause: Maybe Bird Weather (wind/rain): Fine Follow up required (select advisory)? | .
1933 |  | JE24040483 | GRAVATT RD | Eastern | GRAVATT RD | 2024-11-03 | 7:45 | 2024-11-03 | 13:05 | 0.027336 | 8.5528e-05 | 31 | 9908 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Car V Ground Mount TFR TD5-060, (hit and run, no Vehicle on site) Isolated & Earthed at Fuses TD5-060 HV & LV cables disconnected, Temp LV panel installed & Generator connected and put into service for TFR TD5-060 13:05 New HV cables & TFR will have to be installed due to the damaged caused by the Vehicle Dower to advise when new TFR is going to be installed Transformer replaced on 06/11/24.Generator to be removed on 8/11/24 under urgent NAPA E00157 Gen removed, new transformer installed and connected | .
1934 |  | JE24040491 | WILLS RD | Eastern | WILLS RD | 2024-11-03 | 12:21 | 2024-11-03 | 17:18 | 0.0057468 | 1.9313e-05 | 7 | 2083 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Phase missing at TFR TB2-042, Suspected faulty HV cable of TFR Isolated & Earthed at Fuses SB2-046 Cable and TFR tested, no faults could be found After further investigation it was found the center phase at Fuses SB2-069 had blown, but the barrel was stuck/partially welded into the DDO holder so had not dropped down. TFR TB2-041 & TB2-110 where not affected as they are single phase TFR's connected to the out side phases on the line Fuse SB2-069 - Reloaded & Re-livened 1 x 8A 17:22, Full power restored, unknow cause | .
1935 |  | JE24039793 | 418 QUEEN STREET THAMES THAMES Service Lane 6 | Eastern | QUEEN ST | 2024-11-02 | 23:11 | 2024-11-03 | 23:55 | 0.025021 | 0.00040281 | 73 | 9069 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Reyrolle switchgear IC3206/IC3210 with CFC Safelink 15005. and upgrade Transformer TC5322. | .
1936 |  | JE24040445 | DUKE ST | Eastern | DUKE ST | 2024-11-02 | 9:57 | 2024-11-03 | 14:40 | 0.039917 | 0.00019865 | 36 | 14468 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Faulty TFR TC3223, Generator in service, TFR to be replaced 03/11/24 02/11/24 - Isolated & Earthed at Fuses/Sw 9547/2 Cable & TFR Tested, TFR found to have an internal fault, LV Cable break made at TFR Bushings, Generator installed, 03/11/24 - Generator removed TFR Replaced, New LV panel installed with Isolator, Fuse ways & generator port New Fuses installed in Fuses/Sw 9547/2, Full power restored | .
1937 |  | JE24040475 | HUKANUI | Western | HUKANUI | 2024-11-02 | 20:22 | 2024-11-02 | 21:42 | 0.0046533 | 5.7938e-05 | 21 | 1687 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | Fuses Location: Pole P10857 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 21:42 Cause: Branch on line Weather (wind/rain): wind Follow up required (select advisory)?N | .
1938 |  | JE24036925 | 7 LLOYDS LANE OROPI TAURANGA | Eastern | WAIMAPU | 2024-11-01 | 9:03 | 2024-11-01 | 15:11 | 0.010147 | 2.759e-05 | 10 | 3678 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles and/or crossarms 211106 to 211117 (TE4-176) and 211119 (TE4-204) | .
1939 |  | JE24036927 | 68 TARATA ROAD INGLEWOOD INGLEWOOD | Western | KAIMATA | 2024-11-01 | 9:00 | 2024-11-01 | 15:25 | 0.015923 | 4.1384e-05 | 15 | 5771 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 760524 and hardware. Replace crossarms at poles 840603, 760526, 760525, 760523, 760522, and pole 760521. | .
1940 |  | JE24037111 | KAIMAI DRIVE | Eastern | KAIMAI DRIVE | 2024-11-01 | 9:31 | 2024-11-01 | 16:33 | 0.090838 | 0.0002152 | 78 | 32925 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | PQR Case 10723 - To replace pole 217227, upgrade transformer to 50kVA 3 phase and LV conductor from Pole 217227 to 217229 to Kutu | .
1941 |  | JE24037147 | 241 SURREY HILL ROAD KAITAKE NEW PLYMOUTH | Western | OAKURA | 2024-11-01 | 9:31 | 2024-11-01 | 13:09 | 0.047213 | 0.00023451 | 85 | 17113 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Straighten 11Kv poles 756154 & 756156 + Replace some 11kV Namu conductor as there's multiple sleeves | .
1942 |  | JE24037164 | 255 RUAHIHI ROAD LOWER KAIMAI TAURANGA | Eastern | KAIMAI DRIVE | 2024-11-01 | 8:46 | 2024-11-01 | 15:00 | 0.038245 | 0.00010208 | 37 | 13862 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv/400vt Poleâ€™s 211652, 211653, & 386184. | .
1943 |  | JE24037191 | 335 FERRY ROAD KEREPEHI PAEROA | Eastern | AWAITI | 2024-11-01 | 10:16 | 2024-11-01 | 13:50 | 0.024982 | 0.00012139 | 44 | 9055 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REMOVE TEMPORARY POLE BETWEEN POLES O125 & O124 AND DIVERT 11KV O/H LINES ONTO NEW REGULATOR SITE 14983 | .
1944 |  | JE24037245 | 1 SANTA BARBARA DRIVE PAPAMOA BEACH TAURANGA | Eastern | PALM BEACH | 2024-11-01 | 9:45 | 2024-11-01 | 13:20 | 0.076538 | 0.00035591 | 129 | 27741 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - S4586-S4588-S4590 | .
1945 |  | JE24040266 | PUTORINO | Western | PUTORINO | 2024-11-01 | 6:25 | 2024-11-01 | 9:15 | 0.0018805 | 1.1036e-05 | 4 | 682 | Unplanned | WILDLIFE - POSSUM | Fuses Location: 4171 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 0915 Cause: possum Weather (wind/rain): Follow up required (select advisory)? Restored | .
1946 |  | JE24040274 | PIRINOA | Western | PIRINOA | 2024-11-01 | 7:56 | 2024-11-01 | 13:33 | 0.036339 | 0.0002759 | 100 | 13171 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11KV CB C926 Protection flags (nil where none): B & C Phase trip Flags CAUSE: Trees Location: Pole 361844 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Weather (wind/rain): Windy LFI (Y/N + Comments): Yes but not Flashing on My Screen Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1947 |  | JE24040320 | BRASSEY ROAD | Western | BRASSEY ROAD | 2024-11-01 | 10:48 | 2024-11-01 | 11:28 | 0.10949 | 0.0027259 | 988 | 39685 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | REGULATORY INFORMATION Voltage & Device ID: 11KV CB4747-2 Protection flags (nil where none): A & B Phase O/C CAUSE: Tree Location: Pole 707283 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Weather (wind/rain): Windy LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Called in by passer by SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1948 |  | JE24040404 | KUMENGA | Western | KUMENGA | 2024-11-01 | 15:11 | 2024-11-01 | 17:37 | 0.00040214 | 2.759e-06 | 1 | 146 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: 7302 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 17-36 Cause: weather line clash Weather (wind/rain): windy Follow up required (select advisory)? | .
1949 |  | JE24036667 | 81 CLIFTON GROVE ROAD ADMIRAL HILL MASTERTON | Western | LONGBUSH | 2024-10-31 | 9:15 | 2024-10-31 | 15:15 | 0.048646 | 0.00013519 | 49 | 17632 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles and hardware past S333 | .
1950 |  | JE24036886 | 1234 SOUTH ROAD KAITAKE NEW PLYMOUTH | Western | SEAWARD COAST | 2024-10-31 | 8:46 | 2024-10-31 | 14:21 | 0.0046217 | 1.3795e-05 | 5 | 1675 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 759075 with a new B11 and remove ABS 172. Replace pole 756699 with a new B11 and replace ABS 116 with new horizontal ABS. Install new HV knife links on pole 364639 | .
1951 |  | JE24037197 | ASHHURST | Western | ASHHURST | 2024-10-31 | 8:30 | 2024-10-31 | 13:51 | 0.055751 | 0.00017381 | 63 | 20207 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install new pole between P19930 and P19935. Remove pole P19935. OH to UG conversion from new pole to P19992. Convert Xarm to Term arm on P19992. | .
1952 |  | JE24037630 | 2 MANCHESTER WAY JUDEA TAURANGA | Eastern | SUMMIT | 2024-10-31 | 9:45 | 2024-10-31 | 13:50 | 0.060839 | 0.00024831 | 90 | 22052 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9466/1/2/3/4 | .
1953 |  | JE24038649 | 34 KAIPIKARI ROAD LOWER URENUI URENUI | Western | TIKORANGI | 2024-10-31 | 10:05 | 2024-10-31 | 11:57 | 0.00030956 | 2.759e-06 | 1 | 112 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replacement of leaking 50 KVA TX 4684T | .
1954 |  | JE24039872 | OTAMARAKAU | Eastern | OTAMARAKAU | 2024-10-31 | 9:31 | 2024-10-31 | 10:40 | 0.0022806 | 3.3108e-05 | 12 | 827 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace rotten xarms at pole#227469 - RED DEFECT | .
1955 |  | JE24040120 | MCCABE ROAD | Eastern | MCCABE ROAD | 2024-10-31 | 5:45 | 2024-10-31 | 6:50 | 0.00018077 | 2.759e-06 | 1 | 66 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses FP512 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 06:50AM Cause: Bird on LV Bushing Of Transformer Weather (wind/rain): Sunny Follow up required (select advisory)? NIL Restored | .
1956 |  | JE24040133 | STRATHMORE | Western | STRATHMORE | 2024-10-31 | 9:06 | 2024-10-31 | 11:27 | 0.0038888 | 2.759e-05 | 10 | 1410 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Line down past pole 741221 cause of fault was old age, the old No8 wire broke where it was bound onto the insulator, Fuses 5483 did not operate, conductor was broken on the load side of the insulator, this line was still alive as it was being back feed from the down stream TFR's Isolated at Fuses 5483 Line repaired, Full power restored | .
1957 |  | JE24040139 | 210 UPPER GLENN ROAD, MANAIA, 4678 | Western | AUROA | 2024-10-31 | 11:00 | 2024-10-31 | 12:09 | 0.0077907 | 0.00011312 | 41 | 2824 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: 5319E No. Fuses: 1 Fuse Amp Size: 3 TIME CLOSED: Went to close and the top of the DDO broke off Cause: faulty DDO Barrel Weather (wind/rain): calm Follow up required (select advisory)?n Faulty barrel, had exploded out the side and was still sparking and hissing when faultman arrived 1 x Broken DDO due to corrosion Isolated at Links 12567/4 & ABS MA191 3 x DDO's replaced for TFR 5319E at Pole 844623, Full power restored | .
1958 |  | JE24040224 | MEREMERE | Western | MEREMERE | 2024-10-31 | 15:29 | 2024-10-31 | 16:39 | 0.0015519 | 2.2072e-05 | 8 | 562 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: WH201 No. Fuses: 2 Fuse Amp Size: 8 TIME CLOSED: 16:38 Cause: unknown Weather (wind/rain): calm Follow up required (select advisory)?n Line patrolled | .
1959 |  | JE24030208 | 416 NO 3 LINE OKOIA WANGANUI | Western | NO 3 LINE | 2024-10-30 | 9:15 | 2024-10-30 | 12:56 | 0.042717 | 0.00019313 | 70 | 15483 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11KV Defected poles & X-Arms between 790924 & 790933 | .
1960 |  | JE24036568 | 175 RUAHIHI ROAD LOWER KAIMAI TAURANGA | Eastern | KAIMAI DRIVE | 2024-10-30 | 8:49 | 2024-10-30 | 14:27 | 0.034551 | 0.00010208 | 37 | 12523 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv/400vt Poleâ€™s 211648, 211649, 211650 & 211651. | .
1961 |  | JE24036656 | 572 WESTERN LAKE ROAD WESTERN LAKE FEATHERSTON | Western | REVANS ST | 2024-10-30 | 9:15 | 2024-10-30 | 13:10 | 0.00064767 | 2.759e-06 | 1 | 235 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | change 11kv arms @ 798504 On re-livening transformer T2245 after work was completed on NAPA 113697, the fuse on transformer T2245 blow straight away, Crew suspect transformer to be faulty as is more than 50 years old. There is attached switching to replace T2245. Transformer T2245 was isolated again at Fuses 7271 and the transformer was replaced - Scanpower has also spoken to the projects manager Gavin Paget about the problem. | .
1962 |  | JE24036659 | 385 HEREFORD ROAD OROPI TAURANGA | Eastern | WAIMAPU | 2024-10-30 | 9:07 | 2024-10-30 | 15:05 | 0.033582 | 9.3805e-05 | 34 | 12172 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles and/or crossarms 211055 to 211061 | .
1963 |  | JE24036730 | BRISTOL RD | Western | BRISTOL RD | 2024-10-30 | 9:15 | 2024-10-30 | 11:43 | 0.023683 | 0.00016002 | 58 | 8584 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Vegetation Clearance in between poles 759748 - 759749 | .
1964 |  | JE24036912 | 32 SAPPHIRE DRIVE HAIRINI TAURANGA | Eastern | POIKE | 2024-10-30 | 9:46 | 2024-10-30 | 14:01 | 0.086671 | 0.00033935 | 123 | 31414 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - S4521-S4523 | .
1965 |  | JE24037193 | 2497 COAST ROAD PONGAROA PONGAROA | Western | COAST ROAD | 2024-10-30 | 8:43 | 2024-10-30 | 14:10 | 0.11084 | 0.00033935 | 123 | 40176 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Coast Road FFT - Akitio Execute cross arm replacement and resag between P04503, P04506 & P04510 and P01102 & P04432 and P26712-P04630 also pole straightening, fill in cattle ruts. | .
1966 |  | JE24039949 | WAITOTARA | Western | WAITOTARA | 2024-10-30 | 5:30 | 2024-10-30 | 7:15 | 0.0043585 | 4.1384e-05 | 15 | 1580 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 2715 No. Fuses: 2 Fuse Amp Size:10A TIME CLOSED: 0715 Cause: Unknown Weather (wind/rain): rain Follow up required (select advisory)? None Restored | .
1967 |  | JE24039966 | POOLES RD | Eastern | POOLES RD | 2024-10-30 | 8:30 | 2024-10-30 | 9:57 | 0.00047942 | 5.5179e-06 | 2 | 174 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Incorrect Job Location Correct Location is TFR T4954 LV Bus Isolator, blue phase tension ring had broken, causing the contacts to over heat, then arcing occurred between the contacts and then other LV phases, causing an explosion which blow open the TFR door Isolated at Sw/Gear S5921 Replaced LV Bus Isolator, Fuses & Solid links on TFR T4954, Full power restored | .
1968 |  | JE24040018 | PIRINOA | Western | PIRINOA | 2024-10-30 | 10:55 | 2024-10-30 | 22:48 | 0.048755 | 0.00049661 | 100 | 17671 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB C926 Protection flags (nil where none): A ph E/F CAUSE: Cable damage Location: Fuses 7003 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: Operational Weather (wind/rain): light wind LFI (Y/N + Comments): Y at pole 848476 & Sw/Gear 7017/3 - Sw/Gear one might have been from an old fault, it was reset Follow up Required (select advisory)? N Additional fault restoration comments: Fuses 7003 isolated to repair cable damage | .
1969 |  | JE24040019 | HORAHORA | Eastern | HORAHORA | 2024-10-30 | 14:20 | 2024-10-30 | 15:28 | 0.0079124 | 0.00011588 | 42 | 2868 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: Aged / Rotten Location: M0809 Isolations: 1187 & 1271 Back feed: 1314 What was replaced? HV Crossarm & Hardware Weather: Windy Additional Info: | .
1970 |  | JE24040077 | 572 WESTERN LAKE ROAD WESTERN LAKE FEATHERSTON | Western | REVANS ST | 2024-10-30 | 13:58 | 2024-10-30 | 15:05 | 0.00018398 | 2.759e-06 | 1 | 67 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | On re-livening transformer T2245 after work was completed on NAPA 113697, the fuse on transformer T2245 blow straight away, Crew suspect transformer to be faulty as is more than 50 years old. There is attached switching to replace T2245. Transformer T2245 was isolated again at Fuses 7271 and the transformer was replaced - Scanpower has also spoken to the projects manager Gavin Paget about the problem. | .
1971 |  | JE24037350 | 456 LINCOLN ROAD EVERETT PARK INGLEWOOD | Western | WAITARA RD | 2024-10-29 | 9:06 | 2024-10-29 | 11:00 | 0.0099505 | 0.00014071 | 51 | 3607 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Tap realignment area shut 13 - refer to methodology for TX' no's | .
1972 |  | JE24037744 | 238 OHANGAI ROAD HAWERA HAWERA | Western | MANAWAPOU RD | 2024-10-29 | 9:01 | 2024-10-29 | 14:22 | 0.059003 | 0.00018485 | 67 | 21386 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11KV ABS WH284 on existing pole 725440 | .
1973 |  | JE24038063 | NO 3 ROAD | Eastern | NO 3 ROAD | 2024-10-29 | 11:01 | 2024-10-29 | 12:28 | 0.0011949 | 1.3795e-05 | 5 | 433 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Confirm phasing , Re-instate jumpers at pole 393791 & restore network back to normal configuration | .
1974 |  | JE24039785 | BIDEFORD | Western | BIDEFORD | 2024-10-29 | 10:30 | 2024-10-29 | 11:48 | 0.00085859 | 1.1036e-05 | 4 | 311 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolate DTX T2445 for additional safety to repair LV crossarm at Pole 836838 Repalce 1 x 3A fuse. | .
1975 |  | JE24039859 | TOTMANS RD | Eastern | TOTMANS RD | 2024-10-29 | 12:49 | 2024-10-30 | 3:31 | 0.17679 | 0.0011864 | 430 | 64079 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV Recloser 13260 Protection flags (nil where none): E/F CAUSE: Car V Pole Location: Pole E13027 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: curse Weather (wind/rain): Wind Rain LFI (Y/N + Comments): ? Follow up Required (select advisory)? Additional fault restoration comments: HV - LV Clash also, 1 house left off, Disconnect # A39494 Service Cable Failed Tests, 11m Busck installed, Replaced damaged 3 phase 30kVA DTX SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
1976 |  | JE24039862 | SPRINGDALE | Eastern | SPRINGDALE | 2024-10-29 | 17:57 | 2024-10-29 | 18:19 | 0.00030303 | 1.3795e-05 | 5 | 110 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: LV Neutral Fault What was replaced? LV repairs on Neutral Bushing Where was it replaced. Transformer)? Is 2R required? Y 2R Y - What is the timeframe for repairs? Additional Info: Opened HV fuses @ 17:57 and closed 18:19 To be able to carry out repairs at transformer No Fuses replaced | .
1977 |  | JE24039914 | INLAND COAST | Western | INLAND COAST | 2024-10-29 | 16:07 | 2024-10-29 | 17:01 | 0.00044939 | 8.2769e-06 | 3 | 163 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 1370 No. Fuses: 2 Fuse Amp Size: 3 Amp TIME CLOSED: 17:00 hrs Cause: Lightning Weather (wind/rain): Heavy Rain Follow up required (select advisory)? | .
1978 |  | JE24039919 | INLAND COAST | Western | INLAND COAST | 2024-10-29 | 16:16 | 2024-10-29 | 17:47 | 0.0012572 | 1.3795e-05 | 5 | 456 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 817 No. Fuses: 3 Fuse Amp Size: 2 Amp TIME CLOSED: 17:46 hrs Cause: Lightning Weather (wind/rain): Heavy Rain Follow up required (select advisory)? | .
1979 |  | JE24039922 | CLOTON RD NORTH | Western | CLOTON RD NORTH | 2024-10-29 | 17:08 | 2024-10-30 | 0:32 | 0.056388 | 0.00012691 | 46 | 20438 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: Sectionaliser 12733/2 Protection flags (nil where none): Opened by Control CAUSE: Car V Pole, People in car Location: Pole 466757 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): rain LFI (Y/N + Comments): N/A Follow up Required (select advisory)? N Additional fault restoration comments: | .
1980 |  | JE24039924 | LOCKINGTON ROAD | Eastern | LOCKINGTON ROAD | 2024-10-29 | 16:52 | 2024-10-29 | 19:02 | 0.096741 | 0.00089942 | 326 | 35064 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | REGULATORY INFORMATION Voltage & Device ID: CB 5 Protection flags (nil where none): A,B,C O/C E/F CAUSE: Transformer TC2170 Branch blown onto Transformer Bushings, Blowing 1 x 6A D/Out Fuse Location: TC2170 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: curse Weather (wind/rain): High Winds LFI (Y + Comments): LFI at pole 201612 LIT .LFIs at pole 204990 not LIT suggesting fault should be between the two LFIs and recloser 9865 Follow up Required (select advisory)? Additional fault restoration comments: Sectionaliser 9865 saw the fault & Never Opened. But also could not be opened or Closed from NOC to be able to close CB 5 TO RESTORE PART OF FEEDER, SEC 9865 Faulty SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): No Circuit that tripped: N/A DTF (KM):N/A Trees in the lines near 178 Wright road @ DTX TC2170 Site | .
1981 |  | JE24039925 | INLAND COAST | Western | INLAND COAST | 2024-10-29 | 19:22 | 2024-10-30 | 14:30 | 0.0094997 | 8.2769e-06 | 3 | 3443 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Transformer 1843N found to be faulty Isolated at Transformer Fuses Truck got stuck trying to access site 2R - Left open for transformer replacement FM to return in morning. Crew returned next day and replaced Transformer 1843N due to lightning. 15/11/3ph | .
1982 |  | JE24039938 | PARIHAKA | Western | PARIHAKA | 2024-10-29 | 21:46 | 2024-10-30 | 12:20 | 0.0072359 | 8.2769e-06 | 3 | 2623 | Unplanned | LIGHTNING - LIGHTNING STRIKE | TX replacement Fuses Location: PU442 No. Fuses: 2x 8Amp (PU442), 2x 3Amp (P4370) Fuse Amp Size: TIME CLOSED: 12:20 hrs Cause: Lightning Weather (wind/rain): Raining, Lightning Follow up required (select advisory)? Y Fuses or Transformer P4370 blew on livening Transformer Faulty Isolated at Fuses for Transformer P4370 2R Left open for replacement FM to return in morning to replace Return next day and replaced 30/11/3ph Transformer | .
1983 |  | JE24039939 | INLAND COAST | Western | INLAND COAST | 2024-10-29 | 17:11 | 2024-10-29 | 18:25 | 0.00061249 | 8.2769e-06 | 3 | 222 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 6792 No. Fuses: 2 Fuse Amp Size: 6 Amp TIME CLOSED: 18:25 Cause: Lightning Weather (wind/rain): Lightning, Rain Follow up required (select advisory)? N Fuses Location: 1974N No. Fuses: 1 Fuse Amp Size: 2 Amp TIME CLOSED: 18:52 Cause: Lightning Weather (wind/rain): Lightning, Rain Follow up required (select advisory)? N | .
1984 |  | JE24039695 | RONGOTEA | Western | RONGOTEA | 2024-10-28 | 6:48 | 2024-10-28 | 11:47 | 0.0082179 | 0.00066491 | 241 | 2979 | Unplanned | LIGHTNING - LIGHTNING STRIKE | REGULATORY INFORMATION Voltage & Device ID: San CB 8 Protection flags (nil where none): E/F CAUSE: Relivening Fuses O82, faulty transformer Location: O82 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Lightning LFI (Y/N + Comments): NIL Follow up Required (select advisory)? No Additional fault restoration comments: fuses O82 isolated for transformer Replacement | .
1985 |  | JE24039703 | RONGOTEA | Western | RONGOTEA | 2024-10-28 | 7:35 | 2024-10-28 | 9:11 | 0.00052947 | 5.5179e-06 | 2 | 192 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T1/92 No. Fuses: 3 Fuse Amp Size: 2A TIME CLOSED: 0910 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? | .
1986 |  | JE24039706 | PUTORINO | Western | PUTORINO | 2024-10-28 | 5:58 | 2024-10-28 | 8:11 | 0.0091759 | 6.8974e-05 | 25 | 3326 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 495 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 0811 Cause: Unknown but suspect bird strike Weather (wind/rain): raining and windy Follow up required (select advisory)? | .
1987 |  | JE24039717 | TIKORANGI | Western | TIKORANGI | 2024-10-28 | 11:44 | 2024-10-28 | 14:50 | 0.0035844 | 1.9313e-05 | 7 | 1299 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 5169 No. Fuses: 3 Fuse Amp Size: 6A and candles TIME CLOSED: 1449 Cause: Unknown Weather (wind/rain): Windy, rain Follow up required (select advisory)? | .
1988 |  | JE24039724 | OROUA DOWNS | Western | OROUA DOWNS | 2024-10-28 | 17:35 | 2024-10-28 | 17:59 | 6.5203e-05 | 2.759e-06 | 1 | 24 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Line has corroded and pulled out of Transformer T1/508 Fuses in strong winds. Isolate at Fuses L58 to repair | .
1989 |  | JE24039729 | STRATHMORE | Western | STRATHMORE | 2024-10-28 | 17:30 | 2024-10-28 | 19:55 | 0.0043961 | 3.0349e-05 | 11 | 1593 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: 5453 No. Fuses: 2 Fuse Amp Size: 8 Amp TIME CLOSED: 19:55 Cause: Possible Line Clash Weather (wind/rain): Windy, Raining Follow up required (select advisory)? N | .
1990 |  | JE24039730 | KAKARIKI | Western | KAKARIKI | 2024-10-28 | 18:02 | 2024-10-28 | 19:30 | 0.0048859 | 5.5179e-05 | 20 | 1771 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | Fuses Location: M31 No. Fuses: 2 Fuse Amp Size: 10 Amp TIME CLOSED: 19:30 Cause: Tree branch blown onto lines Weather (wind/rain): Windy Follow up required (select advisory)? N | .
1991 |  | JE24039744 | 44 OTARAOA ROAD, WAITARA, 4383 | Western | PRINCESS ST | 2024-10-28 | 20:55 | 2024-10-29 | 1:02 | 0.0034124 | 1.3795e-05 | 5 | 1237 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 33kv Cross arm found broken at Pole 847782 33kV line close to 11kV Lines, 33kV De-energized 11kV Isolated at ABS 511 & Links 12414 Links 12414 not on e-map so line break installed create outage 33kV Isolated at ABS's 614, 3541, & 3179 Cross arm Replaced Old cross arm rotten | .
1992 |  | JE24039750 | PARIHAKA | Western | PARIHAKA | 2024-10-28 | 23:20 | 2024-10-29 | 14:02 | 0.0072948 | 8.2769e-06 | 3 | 2644 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cross arm for transformer 5385 E Broken Isolated at fuses PU402 FM to return in morning to do repairs Powerworx returned 29/10/24 and replaced HV Crossarm | .
1993 |  | JE24039755 | POHANGINA | Western | POHANGINA | 2024-10-28 | 23:00 | 2024-10-29 | 1:23 | 0.037072 | 0.0003697 | 134 | 13437 | Unplanned | WILDLIFE - POSSUM | REGULATORY INFORMATION Voltage & Device ID: 11kV Recloser F26 Protection flags (nil where none): A, B, C Ph O/C E/F CAUSE: Possum Location: Pole P13584 Temp generation (state details when used): no PERFORMANCE DETAIL DNO (number or state No): no Circuit patrolled and type: Cursory Weather (wind/rain): Raining, Windy LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: | .
1994 |  | JE24039756 | FEATHERSTON No 1 33kV | Western | FEATHERSTON No 1 33kV | 2024-10-28 | 23:38 | 2024-10-28 | 23:41 | 0.0016598 | 0.00052972 | 192 | 602 | Unplanned | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | Voltage & Device ID: 33kVRec 3141/2, CB C885 Protection flags (nil where none): E/F, O/C B Weather (wind/rain): unknown Follow up required (select advisory): n LFI Activation: N Noc Closed Rec 3141/2 as each side of Recloser was live | .
1995 |  | JE24039640 | 516 TAIKATU ROAD, MANAIA, 4678 | Western | OTAKEHO | 2024-10-27 | 8:07 | 2024-10-27 | 12:08 | 0.024654 | 0.00010208 | 37 | 8936 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Pole 719053 damaged and requiring replacement Isolated at Fuses TA868 Pole 719053 Replaced | .
1996 |  | JE24039645 | TURAKINA | Western | TURAKINA | 2024-10-27 | 9:45 | 2024-10-27 | 13:56 | 0.0041498 | 1.6554e-05 | 6 | 1504 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Broken cross arm found at pole 793824 Isolated at Fuses 1401 Cross arm deteriorated replaced, and power restored | .
1997 |  | JE24039671 | MANAIA COROMANDEL | Eastern | MANAIA COROMANDEL | 2024-10-27 | 13:42 | 2024-10-27 | 16:16 | 0.00042347 | 2.759e-06 | 1 | 153 | Unplanned | THIRD PARTY INTERFERENCE - TREES | Fuses Location: Transformer number not visible but ends with 96.Pole number given V13127 also not on EMAP or GIS No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 15:55 Cause: Customer felling trees Weather (wind/rain): Calm Follow up required (select advisory)? No | .
1998 |  | JE24039674 | dtx_T4426 | Western | TUTURUMURI | 2024-10-27 | 17:25 | 2024-10-27 | 19:25 | 0.0023227 | 1.9313e-05 | 7 | 842 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Check Nikorima Repeater AC Mains Fail-Transformer T4426 Broken binder/burnt cross arm at pole 848532(onsite), (Emap has pole as 848321) Isolated at Fuses 7318 Noc advised Ben Taylor that 33kV Line to wind farm had to be de-energised for safety (Genesis rep) due to work location & weather conditions Faulty cross arm replaced, full power restored Noc advised Ben Taylor full power restored to wind farm | .
1999 |  | JE24039675 | WAITOTARA | Western | WAITOTARA | 2024-10-27 | 14:30 | 2024-10-28 | 16:32 | 0.054803 | 0.00036418 | 69 | 19863 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV Reclosure 1406 Protection flags (nil where none): A, B Ph O/C, E/F CAUSE: Tree bought 3 x lines down Location: Pole 850995 Temp generation (state details when used): no Fault past fuses 781. Due to comms issues control of network past these fuses handed over to FM Found 1 Span down at pole 850995 ( 100m + ) Put in temp line Break at Pole 780698 Will return in morning to Fix PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Raining LFI (Y/N + Comments): N/A Follow up Required (select advisory)? No Additional fault restoration comments: NDR to follow | .
2000 |  | JE24039678 | CLOTON RD NORTH | Western | CLOTON RD NORTH | 2024-10-27 | 16:26 | 2024-10-27 | 19:49 | 0.019983 | 0.00017933 | 65 | 7243 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Reclosure 6616 A/R & Sectionaliser 12740 Protection flags (nil where none): A Ph O/C, E/F CAUSE: Floating Conductor & replaced 1 x 100 X 100 3 Pin Crossarm as well Location: Pole 761661 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Weather (wind/rain): Raining, Windy LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Isolated at Fuses 5516 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2001 |  | JE24039686 | RONGOTEA | Western | RONGOTEA | 2024-10-27 | 18:40 | 2024-10-27 | 19:45 | 0.028394 | 0.00056007 | 203 | 10291 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11KV Rec O67 Protection flags (nil where none): C Phase O/C CAUSE: Bird Location: ?? No pole number given Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2002 |  | JE24039691 | TAINUI | Eastern | TAINUI | 2024-10-27 | 22:39 | 2024-10-28 | 1:55 | 0.0026923 | 1.3795e-05 | 5 | 976 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: SE7-004 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 01:54 Cause: unknown Weather (wind/rain): calm Follow up required (select advisory)?n Line patrolled | .
2003 |  | JE24039575 | OAONUI | Western | OAONUI | 2024-10-26 | 9:22 | 2024-10-26 | 10:28 | 0.0075072 | 0.00011312 | 41 | 2721 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | CB TA3 has tripped. Line to STOS. Non Outage Broken binder at Pole 851258. Duel Circuit Pole Required to Isolate section of TA7. Isolated at ABS"s 6661, TA720, & TA719. Back feeds installed TA3 Isolated at Links 12300, & CB TA3 Binders all replaced | .
2004 |  | JE24039581 | OMOKOROA RD | Eastern | OMOKOROA RD | 2024-10-26 | 11:36 | 2024-10-26 | 12:21 | 0.0060013 | 0.00013243 | 48 | 2175 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | This job was not at this Tfr TC3-026 but at the Child Job. Faultman found a art of the center phase screen was a bit damaged due to it rubbing on the pole causing arcing. Cable was isolated at Fuses SC 3-049 and screen was repaired and move away to stop it rubbing on the pole. | .
2005 |  | JE24039619 | TIKORANGI | Western | TIKORANGI | 2024-10-26 | 17:46 | 2024-10-26 | 21:30 | 0.098388 | 0.0012167 | 441 | 35661 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11KV CB U40 Protection flags (nil where none): B Phase O/C E/F CAUSE: Floating Jumper Location: Transformer 3887T Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Weather (wind/rain): Windy LFI (Y/N + Comments): Yes But Could not find Them on Site Follow up Required (select advisory)? No Additional fault restoration comments: | .
2006 |  | JE24039624 | pole_487796 | Eastern | GORDON | 2024-10-26 | 22:06 | 2024-10-26 | 23:07 | 0.018534 | 0.00030349 | 110 | 6718 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 6 Protection flags (nil where none): Nil CAUSE: King bolt missing Location: Pole 487796 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4, not patrolled. Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Steve McMillan sent photos of cross arm and pole to Operations email address. New king bolt installed and cross arm straightened. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2007 |  | JE24036410 | 81 CLIFTON GROVE ROAD ADMIRAL HILL MASTERTON | Western | LONGBUSH | 2024-10-25 | 9:01 | 2024-10-25 | 14:48 | 0.046922 | 0.00013519 | 49 | 17007 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles and hardware past S333 | .
2008 |  | JE24036419 | 184 HENDERSONS LINE KELVIN GROVE PALMERSTON NORTH | Western | ASHHURST | 2024-10-25 | 8:31 | 2024-10-25 | 13:26 | 0.05138 | 0.00017381 | 63 | 18623 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles and Xarms between and including P41033 to P41018. Replace TX T2/218 with 30kVA 3phase (number to remain the same) | .
2009 |  | JE24036427 | HUNTERVILLE 22KV | Western | HUNTERVILLE 22KV | 2024-10-25 | 9:15 | 2024-10-25 | 13:32 | 0.0028355 | 1.1036e-05 | 4 | 1028 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Red Tagged pole 807344 | .
2010 |  | JE24036584 | 124 HINE STREET NEW PLYMOUTH NEW PLYMOUTH | Western | BREAKWATER RD | 2024-10-25 | 8:30 | 2024-10-25 | 16:45 | 0.14418 | 0.0007863 | 189 | 52259 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | AP 1 Create a Temporary line break at pole 447961. AP2 replace TX 314 with new ground mount 500kVA TX 2528N & fuse 12773 and change HV arms on poles 700151,700152,700153,700155,700157. AP 3 reinstate temp line break at pole 447961. | .
2011 |  | JE24036924 | 74 HINE STREET NEW PLYMOUTH NEW PLYMOUTH | Western | CITY 5 | 2024-10-25 | 23:00 | 2024-10-25 | 23:55 | 0.066051 | 0.0012608 | 457 | 23941 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Reinstate line break between poles 851401&700165 installed on Napa 110664 | .
2012 |  | JE24037333 | 716 WORTLEY ROAD WAIONGANA INGLEWOOD | Western | WAITARA RD | 2024-10-25 | 9:01 | 2024-10-25 | 10:21 | 0.0081052 | 0.00015174 | 55 | 2938 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Tapping Realignment of Shut area 12 | .
2013 |  | JE24038051 | 8 MCKENZIE ROAD PAENGAROA TE PUKE | Eastern | YOUNG RD | 2024-10-25 | 9:02 | 2024-10-25 | 14:17 | 0.036557 | 0.00011588 | 42 | 13250 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv pole 221606 & remove stub pole 221617 . Note: Re Paengaroa Sub project work line break on CB2 will remain until early December - Backfeed from PGA4 14785/2. | .
2014 |  | JE24039420 | PLUMMERS POINT | Eastern | PLUMMERS POINT | 2024-10-25 | 7:53 | 2024-10-25 | 9:09 | 0.054801 | 0.00098219 | 356 | 19863 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV Sec 9805 Protection flags (nil where none): A,C OC CAUSE: Bird Strike (Pukeko) Location: Between poles 386213 and 384999 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: Cursory Weather (wind/rain): Showers LFI (Y/N + Comments): Yes Pole 464177 Follow up Required (select advisory)? No Additional fault restoration comments: Dead burmt Pukeko found at site. There is a pond in between poles 386213 and 384999 so birds get into the lines when they take off | .
2015 |  | JE24039452 | OROUA DOWNS | Western | OROUA DOWNS | 2024-10-25 | 14:49 | 2024-10-25 | 15:25 | 9.992e-05 | 2.759e-06 | 1 | 36 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Job Was at Cowshed off Transformer T1/531 NOT Transformer T1/398 When i opened The Fuses L64it did not Make a Job repaired all 3 Jumpers as Other looked Bad as well | .
2016 |  | JE24039462 | TE PUNA | Eastern | TE PUNA | 2024-10-25 | 9:42 | 2024-10-25 | 11:48 | 0.00034837 | 2.759e-06 | 1 | 126 | Unplanned | OTHER | Fuses Location: TX TP1566 No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 11:48 Cause: TX Offline for a few years, re livened because customer needs power Weather (wind/rain): sunny Follow up required (select advisory)?TX tested ok | .
2017 |  | JE24039468 | FEILDING-KIMBOLTON 33KV | Western | FEILDING-KIMBOLTON 33KV | 2024-10-25 | 10:24 | 2024-10-25 | 11:22 | 0.16885 | 0.0031976 | 1159 | 61201 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 33KV CB X20 Protection flags (nil where none): B & C Phase O/C Zone 1 CAUSE: Bit of tree over Conductor Location: Pole P19557 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): 2410012 Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Yes and working Follow up Required (select advisory)? Look into Getting Switch Gear 10275/3 Fixed and we could have had Kimbolton Sub Back on in About 3 Minutes not over an HOUR Also DTF is there but we do not see it Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Kimbolton Circuit that tripped: CB X20 & CB X70 DTF (KM):14 Km But we do not see this | .
2018 |  | JE24039477 | GOLF RD | Eastern | GOLF RD | 2024-10-25 | 14:14 | 2024-10-25 | 18:08 | 0.056825 | 0.00024279 | 88 | 20596 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: Recloser 13102/2 Protection flags (nil where none): None-Did not trip CAUSE: Car versus Pole Location: 214459 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Pole replaced, power restored 18:07 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): N/A Circuit that tripped: N/A DTF (KM): N/A | .
2019 |  | JE24039507 | PARIHAKA | Western | PARIHAKA | 2024-10-25 | 17:21 | 2024-10-29 | 14:11 | 0.015367 | 2.759e-06 | 1 | 5570 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Faulty TFR 5436E (possible damage from past lightning strikes) Isolated at Fuses 6993 Weather: Windy TFR Replaced (30/11/3), 6x 2A HV fuse links, 3x LV fuse holders & 63A fuse links. Upon relivening of Fuses 6993, 1x HV fuse blew. Fuses 6993 left open overnight. Will return to find line fault asap. Line ownership currently under discussion. 29/10/24 Crew returned to locate cause of HV fault. Found and replaced a broken insulator at Pole 854803. Relivened ok. Powerco have claimed ownership of this line now according to Downer. | .
2020 |  | JE24039519 | SOMERSET RD | Western | SOMERSET RD | 2024-10-25 | 16:12 | 2024-10-25 | 17:13 | 0.004166 | 6.8974e-05 | 25 | 1510 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Jumper out at Fuses 7627 Isolated and Repaired Jumper | .
2021 |  | JE24039520 | HUNTERVILLE 22KV | Western | HUNTERVILLE 22KV | 2024-10-25 | 16:50 | 2024-10-25 | 18:43 | 0.0052796 | 4.6902e-05 | 17 | 1914 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Floating conductor and insulator at Pole 807383 due to rotten cross arm Isolated at Fuses 057 Cross arm and hardware replaced Full power restored Weather: Windy | .
2022 |  | JE24039521 | COLVILLE | Eastern | COLVILLE | 2024-10-25 | 14:56 | 2024-10-25 | 16:25 | 0.00024735 | 2.759e-06 | 1 | 90 | Unplanned | WILDLIFE - POSSUM | Fuses Location: Transformer TC4695 No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 16:25 Cause: Possum Weather (wind/rain): Calm Follow up required (select advisory)?No | .
2023 |  | JE24039548 | RAWHITIROA | Western | RAWHITIROA | 2024-10-25 | 19:50 | 2024-11-27 | 12:25 | 0.38964 | 8.2769e-06 | 3 | 141226 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | NAPA 117043 Fuses Location: 6074 No. Fuses: Fuse Amp Size: TIME CLOSED: Planned NAPA 117043 27/11/24 Cause: Faulty Transformer 2351T Weather (wind/rain): Calm Follow up required (select advisory)? Additional Info: Transformer is too wet to access, and home is a holiday home currently unused. 2R left open for tranny replacement 04/11 - Followed up with Hub , waiting reply. 27/11/24 Transformer replaced under NAPA 117043 Power restored 12:25 | .
2024 |  | JE24039555 | WARDVILLE | Eastern | WARDVILLE | 2024-10-25 | 17:36 | 2024-10-25 | 19:40 | 0.011979 | 9.6564e-05 | 35 | 4342 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | CAUSE: Broken jumper and rotten cross arm Location: Pole H3056 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Repaired jumper and replaced cross arm 1 x HV pin cross arm complete assembly replaced 1 x HV Fuse cross arm complete assembly replaced 3 x 3A HV fuses | .
2025 |  | JE24036327 | 591 RIDGE ROAD NORTH MANGAMUTU PAHIATUA | Western | MANGATAINOKA | 2024-10-24 | 9:30 | 2024-10-24 | 12:29 | 0.020219 | 0.00011312 | 41 | 7329 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Xarms & fuses R15 restrain 11KV P18227 & P18234 replace stay P18238 | .
2026 |  | JE24036329 | 132 MT HOLDSWORTH ROAD MOUNT HOLDSWORTH CARTERTON | Western | HOLDSWORTH | 2024-10-24 | 9:01 | 2024-10-24 | 14:06 | 0.017654 | 5.7938e-05 | 21 | 6399 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 826734 | .
2027 |  | JE24036383 | 86 TASMAN DRIVE TOKOROA TOKOROA | Eastern | KAURI ST | 2024-10-24 | 9:16 | 2024-10-24 | 13:40 | 0.078053 | 0.00029521 | 107 | 28291 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9175/1/2/3 | .
2028 |  | JE24036582 | 76 CUTFIELD ROAD NEW PLYMOUTH NEW PLYMOUTH | Western | BREAKWATER RD | 2024-10-24 | 23:01 | 2024-10-24 | 23:47 | 0.054974 | 0.0012608 | 457 | 19926 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install temporary line break between poles 851401 and 700165 for TX upgrade | .
2029 |  | JE24036654 | WAIMAPU | Eastern | WAIMAPU | 2024-10-24 | 9:01 | 2024-10-24 | 14:52 | 0.097682 | 0.00027866 | 101 | 35405 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles and/or crossarms T4938, 211186 to 316908 | .
2030 |  | JE24036687 | 175 RUAHIHI ROAD LOWER KAIMAI TAURANGA | Eastern | KAIMAI DRIVE | 2024-10-24 | 8:48 | 2024-10-24 | 14:56 | 0.0050721 | 1.3795e-05 | 5 | 1838 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv /400vt pole 211646. Replace 11kv cross arms @ poles 211647. Replace 11kv overhead conductors between poles 211642 & 211647 with AAC Fluorine | .
2031 |  | JE24036888 | LEPPERTON | Western | LEPPERTON | 2024-10-24 | 9:46 | 2024-10-24 | 12:56 | 0.027291 | 0.00021796 | 79 | 9892 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Shut 11. Refer to methodology supplied for tapping of downstream transformer. (De-energise 18 TX's, put Reg 12760/2 in service, Liven feeder back bone, give operation control to Downer to liven TX's and tap as required. Check sheets to be complied.) | .
2032 |  | JE24039231 | COLOGNE ST | Western | COLOGNE ST | 2024-10-24 | 3:46 | 2024-10-24 | 13:11 | 0.093321 | 0.0021216 | 719 | 33825 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | REGULATORY INFORMATION Voltage & Device ID: 11KV Rec8156 Protection flags (nil where none): C Phase E/F CAUSE: Line Down Due to wind Location: Pole 817052 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Weather (wind/rain): Windy LFI (Y/N + Comments): No Follow up Required (select advisory)? Additional fault restoration comments: | .
2033 |  | JE24039239 | CORNFOOT ST | Western | CORNFOOT ST | 2024-10-24 | 7:26 | 2024-10-24 | 13:09 | 0.26857 | 0.0027617 | 1001 | 97343 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Cause: car v pole What was replaced? Pole complete with Crossarms etc Where was it replaced (pole/TX/pillar box)? 7770184 Is 2R required? Y/N 2R Y - What is the timeframe for repairs? Done Additional Info: 2R to be use to complete repairs | .
2034 |  | JE24039275 | COLYTON | Western | COLYTON | 2024-10-24 | 9:36 | 2024-10-24 | 13:15 | 0.015713 | 7.1733e-05 | 26 | 5695 | Unplanned | WILDLIFE - BIRD | Fuses Location: E29 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 13-15 Cause: Duck Weather (wind/rain): Fine Follow up required (select advisory)? | .
2035 |  | JE24039277 | PONATAHI | Western | PONATAHI | 2024-10-24 | 9:39 | 2024-10-24 | 13:45 | 0.043398 | 0.00017657 | 64 | 15730 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Repair / Replace Conductor called in by Tree trimmer at Pole 844261 To 815881 Isolated at CB C955 ABS S378 & ABS S379 Back feed in at ABS S556 & ABS S344 | .
2036 |  | JE24039326 | REVANS ST | Western | REVANS ST | 2024-10-24 | 8:41 | 2024-10-24 | 12:36 | 0.0077633 | 3.3108e-05 | 12 | 2814 | Unplanned | ADVERSE WEATHER - WIND | Fuses Location: Fuses 7261 No. Fuses: 2 Fuse Amp Size: 15A TIME CLOSED: 12:35 Cause: WIND Weather (wind/rain): WINDY Follow up required (select advisory)? FULL POWER Created new job because Fuses 7261 are shown in EMAP as links, will not see as a extent | .
2037 |  | JE24039345 | MANGAWEKA | Western | MANGAWEKA | 2024-10-24 | 14:37 | 2024-10-24 | 16:55 | 0.0019002 | 1.3795e-05 | 5 | 689 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Fuses Location: Transformer X595 No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 16:55 Cause: Truck hitting LV Lines at Pole 769705 Weather (wind/rain): Calm Follow up required (select advisory)? No Replaced 10M of 10mm LV Aerial conductor, & x3 Sleeves | .
2038 |  | JE24039369 | MANGAPAKEHA | Western | MANGAPAKEHA | 2024-10-24 | 16:14 | 2024-10-24 | 19:36 | 0.022957 | 0.0001545 | 56 | 8321 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kv CB C844 Protection flags (nil where none): B & C Phase trip flags CAUSE: Broken Crossarm Location: Pole 841507 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): no Circuit patrolled and type: Cursory Weather (wind/rain): Windy LFI (Y/N + Comments): n/a Follow up Required (select advisory)? n/a Additional fault restoration comments: Cause by Tree | .
2039 |  | JE24039392 | KOPANE | Western | KOPANE | 2024-10-24 | 20:17 | 2024-10-24 | 22:21 | 0.0013692 | 1.1036e-05 | 4 | 496 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: C27 No. Fuses: 2 Fuse Amp Size: 5 Amp TIME CLOSED: 22:20 hrs Cause: Unk Weather (wind/rain): Calm Follow up required (select advisory)? NOTE: Also replaced 1x HV fuse carrier | .
2040 |  | JE24039398 | NO 3 LINE | Western | NO 3 LINE | 2024-10-24 | 22:31 | 2024-10-25 | 11:57 | 0.0615 | 0.00021796 | 53 | 22291 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV, Rec 177/2 Protection flags (nil where none): E/F, O/C A-B phase CAUSE: Conductor Down due to wind & trees Location: Pole 790870 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Windy LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: FM could not find fault at night. Suspect it may be where lines go through Pine plantation which is difficult to access at night. Will return in the morning. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2041 |  | JE24039399 | HUNTERVILLE 22KV | Western | HUNTERVILLE 22KV | 2024-10-24 | 19:53 | 2024-10-24 | 23:14 | 0.0083129 | 4.1384e-05 | 15 | 3013 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 748 No. Fuses: 2x 10 Amp Fuse Amp Size: 10 Amp TIME CLOSED: 23:13 hrs Cause: Unk Weather (wind/rain): Windy Follow up required (select advisory)? | .
2042 |  | JE24036077 | ARAWA ST | Eastern | ARAWA ST | 2024-10-23 | 9:31 | 2024-10-23 | 13:26 | 0.093211 | 0.00039729 | 144 | 33785 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - IC1495-FC3313-IC1476 | .
2043 |  | JE24036084 | TUTAENUI | Western | TUTAENUI | 2024-10-23 | 9:24 | 2024-10-23 | 12:05 | 0.005756 | 3.5867e-05 | 13 | 2086 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Red tagged Pole 804009 | .
2044 |  | JE24036310 | 158 HENDERSONS LINE KELVIN GROVE PALMERSTON NORTH | Western | ASHHURST | 2024-10-23 | 8:30 | 2024-10-23 | 14:57 | 0.067214 | 0.00017381 | 63 | 24362 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles and Xarms between and including P41028 and P41030. Replace TX T2/535 with 50kVA 3ph (Number to remain) | .
2045 |  | JE24036388 | 54 NO 1 LINE TAUHERENIKAU FEATHERSTON | Western | DAIRY FACTORY | 2024-10-23 | 8:46 | 2024-10-23 | 13:25 | 0.047078 | 0.0001683 | 61 | 17064 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace S501. Line Crew found a recently installed Transformer T1914 (Pole 946643) inside the shutdown area that was leaking oil. This transformer was replaced during the shutdown with no extra outage required. Approx 2 litres of oil was lost, so the contaminated dirt has been removed & replaced. | .
2046 |  | JE24036399 | 202 PORT ROAD WHANGAMATA WHANGAMATA | Eastern | OPOUTERE | 2024-10-23 | 9:00 | 2024-10-23 | 15:00 | 0.044713 | 0.00012415 | 45 | 16207 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Stringing fibre between poles R12889& R12572. Installing new pole 6 between poles R0702 & R12869. | .
2047 |  | JE24036853 | 458 AHIPAIPA ROAD, OKAIAWA | Western | MATAPU | 2024-10-23 | 8:35 | 2024-10-23 | 14:54 | 0.080437 | 0.00021244 | 77 | 29155 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | work @ poles 720290,720291, 721055, 721057, 721058, 720304, 720305, 720306, 720310, 720311, 720302 | .
2048 |  | JE24038980 | MANGATARATA | Eastern | MANGATARATA | 2024-10-23 | 9:53 | 2024-10-23 | 11:00 | 0.008097 | 0.00012139 | 44 | 2935 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | ### RED DEFECT ### Isolation: ABS IC511 Broken HV pin insulator replaced at Pole O3843 | .
2049 |  | JE24039069 | RUAWHATA | Western | RUAWHATA | 2024-10-23 | 6:28 | 2024-10-23 | 7:41 | 0.00080251 | 1.1036e-05 | 4 | 291 | Unplanned | WILDLIFE - BIRD | Fuses Location: Q87 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 07:40 Cause: BIRD Weather (wind/rain): OVERCAST Follow up required (select advisory)? FULL POWER | .
2050 |  | JE24039090 | TIKORANGI 33kV | Western | TIKORANGI 33kV | 2024-10-23 | 8:52 | 2024-10-23 | 9:06 | 0.031128 | 0.0068146 | 2470 | 11283 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 33kV TPWR Huirangi CB 1342 (Tikorangi) Protection flags (nil where none): O/C Neutral, E/F on B Ø ( TPWR) CAUSE: Unknown Location: Unknown Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Light rain in the morning and then rain stopped. LFI (Y/N + Comments): Yes, two LFI's operated at Pole 760621 & Pole 760322 Follow up Required (select advisory)? Yes Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): WAE S/S , Mangahewa S/S (Todd Energy) , MCK S/S & MOK S/S CB 225 ( Manawa Energy ) Circuit that tripped: 33kV TPWR Huirangi CB 1342 (Tikorangi) DTF (KM): Unknown Called SMC and advised them to send FM to RIMUTAUTEKA RD - ABS 166 33kV HUI CB 1342 Tripped at 08:52 on O/C Neutral, E/F on B Ø ( TPWR) MOK CB 210 Tripped at 08:52 and Manawa Energy Generation went offline. ING S/S Auto Changer operated and supply was changed from HUI GXP to SFD GXP NOC concentrated on getting supply restored to WAE S/S by opening CB 615 and closing CB 613 at 08:56 LFI's operated past ABS 153 ( Pole 760621 & Pole 760322 ) NOC Opened MCK CB 191 NOC requested with TPWR to close in HUI CB 1342 at 09:03 ( Successful) At MOK S/S NOC closed in MABS 253 | .
2051 |  | JE24039121 | TURAKINA | Western | TURAKINA | 2024-10-23 | 10:14 | 2024-10-23 | 12:35 | 0.072647 | 0.00093529 | 339 | 26331 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 4217/2 Protection flags (nil where none): Auto reclosed earlier at 09:27 CAUSE: HV Lines down on the ground & a fire on site. Location: Pole 318 294 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Light Rain LFI (Y/N + Comments): No Follow up Required (select advisory)? Yes Additional fault restoration comments: REC 4217/2 Auto reclosed at 09:27 (Protection: A B C Ø Trip Flag) HAZARD report came in of HV Lines down and a fire on site near 48 Ratana Road. Field Switcher was dispatched to site and confirmed HV Lines were on the ground and still energized. NOC immediately opened REC 4217/2 at 10:14 Field Switcher then Isolated at ABS 030 NOC then closed in REC 4217/2 at 10:29 Further Isolation and Earthing is being carried out. All repairs were made under AP 9121-01 Full Power restored at 12:35 SAFETY MANAGER | .
2052 |  | JE24039146 | TREMAINE AVE | Western | TREMAINE AVE | 2024-10-23 | 11:35 | 2024-10-23 | 12:40 | 0.0030221 | 4.6902e-05 | 17 | 1095 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Cause: Car v Pole What was replaced? All Broken Binders on 11kV & 33kV were replaced Where was it replaced (pole/TX/pillar box)? P42270 Is 2R required? Y 2R Y - What is the timeframe for repairs? Complete Additional Info:FM sighted that every binder was broken on Pole P42270. Debris around the pole made it very likely a vehicle hit the pole and left the scene. A 3 Amp HV fuse link was also replaced at Transformer T6/403 which had possibly fallen out with the impact from the crash. | .
2053 |  | JE24039218 | KAURI ST | Eastern | KAURI ST | 2024-10-23 | 17:06 | 2024-10-23 | 19:28 | 0.0039029 | 2.759e-05 | 10 | 1415 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses FC2166 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 19:27 Cause: unknown Weather (wind/rain): calm Follow up required (select advisory)? N | .
2054 |  | JE24035410 | 386 PUKETUI VALLEY ROAD HIKUAI HIKUAI | Eastern | HIKUAI | 2024-10-22 | 9:27 | 2024-10-22 | 16:13 | 0.044761 | 0.00011036 | 40 | 16224 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE 11KV XARMS AT POLES U12707, U12727, U12732, U0721 AND REPLACE 11KV POLE U0701 | .
2055 |  | JE24035891 | 7 WARNER ROAD OROPI TAURANGA | Eastern | WAIMAPU | 2024-10-22 | 9:01 | 2024-10-22 | 16:37 | 0.12725 | 0.00027866 | 101 | 46122 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles and/or crossarms 211173 (TE4-016) to 211185 | .
2056 |  | JE24035994 | BAINESSE | Western | BAINESSE | 2024-10-22 | 8:31 | 2024-10-22 | 12:16 | 0.019901 | 9.3805e-05 | 34 | 7213 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | HV reconductor of 11 spans from P45223 - 367997 | .
2057 |  | JE24036008 | 768 WESTERN LAKE ROAD WESTERN LAKE FEATHERSTON | Western | REVANS ST | 2024-10-22 | 9:16 | 2024-10-22 | 16:01 | 0.06692 | 0.00017381 | 63 | 24255 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Change 11kV arms between 798461 & 848141 Western Lake Rd | .
2058 |  | JE24036087 | 296 STATE HIGHWAY 1 BULLS BULLS | Western | RACECOURSE | 2024-10-22 | 9:26 | 2024-10-22 | 13:37 | 0.022798 | 9.1046e-05 | 33 | 8263 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace defect X arms on poles 809897, 809895, 809971, 809899 | .
2059 |  | JE24036089 | 1158 EAST ROAD TOKO STRATFORD | Western | TOKO | 2024-10-22 | 9:00 | 2024-10-22 | 14:00 | 0.0033159 | 1.1036e-05 | 4 | 1202 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace TX pole 759206 & straighten + block pole 759208 | .
2060 |  | JE24036234 | 614 LINCOLN ROAD EVERETT PARK INGLEWOOD | Western | LEPPERTON | 2024-10-22 | 9:38 | 2024-10-22 | 15:16 | 0.033507 | 9.9323e-05 | 36 | 12145 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Shut 10 to replace TX structures TX 1104 + TX816 | .
2061 |  | JE24036236 | LONGBUSH | Western | LONGBUSH | 2024-10-22 | 9:00 | 2024-10-22 | 14:56 | 0.048161 | 0.00013519 | 49 | 17456 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles and hardware past S333 | .
2062 |  | JE24036334 | 173 RUAHIHI ROAD LOWER KAIMAI TAURANGA | Eastern | KAIMAI DRIVE | 2024-10-22 | 8:45 | 2024-10-22 | 14:25 | 0.034662 | 0.00010208 | 37 | 12563 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv /400vt poles (new pole 2) 211639, 211640 & 211642 . Replace 11kv cross arms @ pole s 211637 & 211638. Replace 11kv conductors between new pole 2 with new 400 amp links & pole 211638 with AAAC Iodine. Replace 11kv conductors between poles 211640 & 211642 with AAAC Fluorine. | .
2063 |  | JE24036929 | 1377 OPAKI KAIPARORO ROAD MAURICEVILLE MASTERTON | Western | MAURICEVILLE | 2024-10-22 | 9:30 | 2024-10-22 | 15:12 | 0.091303 | 0.00026762 | 97 | 33093 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace rotton 11KV pole P45495 | .
2064 |  | JE24038247 | 40 CENTENNIAL AVENUE TE AROHA TE AROHA | Eastern | MOUNTAIN | 2024-10-22 | 9:30 | 2024-10-22 | 14:06 | 0.12026 | 0.00043592 | 158 | 43590 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - IC3139/IC3140/IC3123/IC3151 | .
2065 |  | JE24038892 | PUHUNGA ISLAND RD | Eastern | PUHUNGA ISLAND RD | 2024-10-22 | 6:41 | 2024-10-22 | 8:21 | 0.00083103 | 8.2769e-06 | 3 | 301 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses FC817 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 0820 Cause: unknown Weather (wind/rain): fine Follow up required (select advisory)? no | .
2066 |  | JE24038928 | REVANS ST | Western | REVANS ST | 2024-10-22 | 9:39 | 2024-10-22 | 10:50 | 0.00039315 | 5.5179e-06 | 2 | 143 | Unplanned | WILDLIFE - BIRD | Fuses Location: 7144 No. Fuses: 2 Fuse Amp Size: 10 Amp TIME CLOSED: 10:50 hrs Cause: Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? Additional Info: FM also replaced a binder at Pole 463031 where the bird contacted the line. Note Fault was in a planned shutdown area. Power went off befoe start of shutdown and fault was repaired before the end of the shutdown | .
2067 |  | JE24038934 | JUNCTION RD | Western | JUNCTION RD | 2024-10-22 | 9:58 | 2024-10-22 | 13:03 | 0.080281 | 0.001545 | 560 | 29098 | Unplanned | THIRD PARTY INTERFERENCE - TREES | REGULATORY INFORMATION Voltage & Device ID: 11kV MAN CB 6777/5 Protection flags (nil where none): A Ø , E/F CAUSE: Tree contractors chain snapped and brought down HV Lines. Location: Poles 747 821 & 747 824 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Clear LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: After the initial tripping, NOC tried to open Sw/Gear 12026/1 whic came back as Control Failed. No LFI's were flashing at this Sw/Gear which indicated that the fault was before this device. To try and restore supply to some of the ICP's, NOC then opened REC 499/2 and then closed in the back feed via BBK8 by closing SEC 12247/2 at 10:22 A phone call then came into NOC explaining that Tree work was being carried out and the Tree had fallen across the HV Lines, address given was 202 Alfred Road, this information was given to the Controller on Desk. NOC then informed the two field switcher's who were assigned to this feeder fault. Upon arrival at the given address, field switcher confirmed the fault and NOC gave instructions to Isolate at Fuses 8194 ( 1 x HV Fuse was blown ) After this NOC then closed in MAN CB 6777/5 at 10:46 ( Power restored to the | .
2068 |  | JE24038939 | ROTOEHU | Eastern | ROTOEHU | 2024-10-22 | 12:01 | 2024-10-22 | 12:27 | 0.00021823 | 8.2769e-06 | 3 | 79 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Fuses Location: Transformer TF8-009 No. Fuses: 1 Fuse Amp Size: No fuses replaced only the jumper TIME CLOSED: 12:27 Cause: Broken Jumper Weather (wind/rain): Calm Follow up required (select advisory)? No Took AP to repair jumper, Power restored 1t 12:27 | .
2069 |  | JE24038943 | OXFORD ST | Western | OXFORD ST | 2024-10-22 | 11:06 | 2024-10-22 | 11:51 | 0.0036887 | 8.2769e-05 | 30 | 1337 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: Deterioration What was replaced? 2x Binders Where was it replaced (pole/TX/pillar box)? Pole 834332 Is 2R required? Y 2R Y - What is the timeframe for repairs? Completed Additional Info: Isolated at Fuses 8181 to make repairs | .
2070 |  | JE24039064 | KATERE 5 | Western | KATERE 5 | 2024-10-22 | 23:24 | 2024-10-23 | 0:31 | 0.00092276 | 1.3795e-05 | 5 | 334 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: FABS 8642 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 0031 Cause: Unknown Weather (wind/rain): fine Follow up required (select advisory)? | .
2071 |  | JE24035768 | 840 MORRINSVILLE-TAHUNA ROAD MANGATEPARU MORRINSVILLE | Eastern | MANGATEPARU | 2024-10-21 | 8:31 | 2024-10-21 | 13:36 | 0.029479 | 9.6564e-05 | 35 | 10685 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Pole K12543: Replace existing pole with a busck 11m Remove existing ABS 621 Level 1: (9.124m) B2Â²/T2 - (6 x Racoon deadends) Level 2: (8.514m) A2 Fuse arm - 3 x DDOs with 300A Solid Links. Install 95mmÂ² Cu PVC leads from the top of the fuse carriers to the OH line. Fuse arm to be installed on side of the pole toward pole K0799 Level 3: Install a manually operated front mount ENTEC LBS. Surge arrestors to be fitted on both sides of the switch. Remove existing stay wire + screw anchor | .
2072 |  | JE24035821 | TURAKINA | Western | TURAKINA | 2024-10-21 | 9:04 | 2024-10-21 | 12:52 | 0.010061 | 4.4143e-05 | 16 | 3647 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV poles 802371 & 802372. Replace 11kV crossarm, re-sag LV conductors and install EOL earth on pole 802367. | .
2073 |  | JE24035874 | 9 HASSARD STREET MANAIA MANAIA | Western | MANAIA | 2024-10-21 | 8:52 | 2024-10-21 | 15:18 | 0.12709 | 0.00052696 | 151 | 46066 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace DNO ABS pole MA513 719624 | .
2074 |  | JE24038780 | FEILDING-KIMBOLTON 33KV | Western | FEILDING-KIMBOLTON 33KV | 2024-10-21 | 6:44 | 2024-10-21 | 7:28 | 0.12442 | 0.0032004 | 1160 | 45097 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: CB X20 Protection flags (nil where none): B phase EF CAUSE: Birds nest on top of bird spikes against center phase insulator. Removed with hot sticks Location: Pole P19557 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: cursory Weather (wind/rain): Calm LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Donor feeders from KEG8 has 2 sets of regulators with set points of 11kV but KEG sub has a set point of 11.2kV. I believe that there are setting corrections issued from protection to correct this. Can we follow up to check when this will be done as it affects the back feed of Apiti. I have created several urgent jobs (JE24038783, JE24038786, JE24038792) due to multiple tech related issues when supply to the sub was lost. These faults caused the back feed to be inoperable and delayed restoration of most customers. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): KIM Circuit that tripped: X20 DTF (KM): N/A | .
2075 |  | JE24038816 | RONGOTEA | Western | RONGOTEA | 2024-10-21 | 11:48 | 2024-10-21 | 13:49 | 0.046881 | 0.00056007 | 203 | 16992 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: REC O67 Protection flags (nil where none): EF CAUSE: tree branch Location: 1 x line down at Pole P35861 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: N/A Weather (wind/rain): calm LFI (Y/N + Comments): N Follow up Required (select advisory)? Additional fault restoration comments: | .
2076 |  | JE24038829 | WAIHI NORTH | Eastern | WAIHI NORTH | 2024-10-21 | 12:51 | 2024-10-21 | 14:00 | 0.00038365 | 5.5179e-06 | 2 | 139 | Unplanned | WILDLIFE - BIRD | Fuses Location: FP1628 No. Fuses: 3 Fuse Amp Size: 6A TIME CLOSED: 14:00 Cause: BIRDS Weather (wind/rain): FINE Follow up required (select advisory)? FULL POWER | .
2077 |  | JE24038833 | HETHERINGTON RD | Eastern | HETHERINGTON RD | 2024-10-21 | 13:30 | 2024-10-21 | 15:18 | 0.090566 | 0.00094908 | 344 | 32826 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: Sectionaliser 13503 Protection flags (nil where none): Phase A,C OC CAUSE: Unknown Location: Unknown Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: Cursory Weather (wind/rain): Clear LFI (Y/N + Comments): Yes at Sw/Gear 13530/1 Flashing Follow up Required (select advisory)? No Additional fault restoration comments: Patrolled, nothing found, sectionalised & power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): No Circuit that tripped: N/A DTF (KM): N/A | .
2078 |  | JE24038851 | MAKETU | Eastern | MAKETU | 2024-10-21 | 19:13 | 2024-10-25 | 15:00 | 0.00058568 | 5.5179e-06 | 1 | 212 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: Failed 11kV Cable, From Fuses SE6-121 Protection flags (nil where none): CAUSE: Failed 11kV Cable, From Fuses SE6-121 Location: Failed 11kV Cable, From Fuses SE6-121 Temp generation (state details when used): YES Generator connected 21/10/24 @ 21:45 PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: No Patrol U/G NETWORK Weather (wind/rain): Calm LFI (Y/N + Comments): Nil Follow up Required (select advisory)? No Additional fault restoration comments: Cable repaired 25/10 24 Generator Removed 14:00 Power rstored 14;50 400V Transformer Fuses at TE6-182 closed at 15:00Hrs SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): N/A Circuit that tripped: N/A DTF (KM):N/A | .
2079 |  | JE24038859 | BROOKLANDS 6 | Western | BROOKLANDS 6 | 2024-10-21 | 16:52 | 2024-10-21 | 17:07 | 0.0077746 | 0.00053248 | 193 | 2818 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 8372 No. Fuses: 1 (Replaced all three) Fuse Amp Size: 40 Amp ( Actual size is 50 Amp, Field Switcher only had 40 Amp) TIME CLOSED: 17:06 Cause: Unknown Weather (wind/rain): Clear Follow up required (select advisory)? No | .
2080 |  | JE24038743 | BEACH RD WAIHI BEACH | Eastern | BEACH RD WAIHI BEACH | 2024-10-20 | 9:10 | 2024-10-20 | 9:43 | 0.0070836 | 0.0002152 | 78 | 2568 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Cause: Failed 400V Andelic Fuse Holder in DTX TC3987 11kV Isolated to repair. What was replaced? 400V Andelic Fuse Holder Where was it replaced (pole/TX/pillar box)? DTX TC3987 Is 2R required? Y/N Yes 2R Y - What is the timeframe for repairs? Additional Info: | .
2081 |  | JE24038763 | MVILLE NORTH | Eastern | MVILLE NORTH | 2024-10-20 | 16:22 | 2024-10-20 | 19:35 | 0.031346 | 0.00016278 | 59 | 11361 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV Tfr TC5954 Protection flags (nil where none): N/A CAUSE: Car hit GM Transformer Location: TC5954 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: Weather (wind/rain): calm LFI (Y/N + Comments): N Follow up Required (select advisory)? N Additional fault restoration comments: Faultman moved GM transformer TC5954 back onto it's foundations and replaced 2 X 200 amp lv fuses | .
2082 |  | JE24038772 | 17 MATAROA ROAD, TAIHAPE, 4720 | Western | MOAWHANGO | 2024-10-20 | 18:34 | 2024-10-23 | 11:53 | 0.043136 | 0.0015892 | 393 | 15635 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Car V 11kV Sw/Gear 16107 Feeder de-energized to enable quicker isolation due to non automated Regulator R6 & No Links on cable to Sw/Gear Isolated at ABS's 222, 490, 112 and CB 8 Line break made at Pole 789124 to make Sw/Gear safe 2R left open for replacement of Sw/Gear on 21/10/2024 22/10/2024 New Sw/Gear 16107 was installed. Outage required to close TLB at Pole 789124 NOC Note: Do not use the back feed point via Gas/Sw 4706 (TPE7). The Voltage drops way below the regulated limit. ABS 258 is advised to be used as a back feed option. 23/10/2024 TLB at Pole 789124 was closed and Power was restored to the new Sw/Gear that was installed. Transformer 6579W - Voltage & Phase Rotation was checked and confirmed correct. SAFETY MANAGER | .
2083 |  | JE24038388 | BRYCE ST | Western | BRYCE ST | 2024-10-19 | 10:01 | 2024-10-19 | 10:28 | 0.00014733 | 5.5179e-06 | 2 | 53 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 80A 11kv fuses and 400v fuses for X3200 after fault | .
2084 |  | JE24038679 | MVILLE SOUTH | Eastern | MVILLE SOUTH | 2024-10-19 | 2:34 | 2024-10-19 | 11:09 | 0.41872 | 0.0022541 | 817 | 151766 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB2 Protection flags (nil where none): O/C A- B - C Ø CAUSE: Car V Pole Location: Pole I0923 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Fire Service rung Weather (wind/rain): LFI (Y/N + Comments): Nil Follow up Required (select advisory)? Protection on Recloser 14721/2 Additional fault restoration comments: Recloser 14721/2 Never Opened, Recloser 14721/2 Protection saw the event and showed on the SCADA events page !!!! 79 Minutes Event number F4070362 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2085 |  | JE24038691 | WAIONE | Western | WAIONE | 2024-10-19 | 12:41 | 2024-10-19 | 14:42 | 0.005701 | 4.6902e-05 | 17 | 2066 | Unplanned | THIRD PARTY INTERFERENCE - TREES | Tree through lines near Transformer T9/103 Isolated at Fuses V33 Cause tree felling Lines repaired | .
2086 |  | JE24038710 | PURIRI | Eastern | PURIRI | 2024-10-19 | 16:46 | 2024-10-19 | 17:45 | 0.0022989 | 3.8625e-05 | 14 | 833 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV ABS IC374 Section, Broken 7/16cu wire, Cause Dererioration Protection flags (nil where none): nil CAUSE: Deterioration Location: Pole SO101 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Calm LFI (Y/N + Comments): nil Follow up Required (select advisory)? Additional fault restoration comments: Copper Conductor Rotten 7/16 Failed next to Insulator on Pole SO101, Line Annealed Wire on ground alive (back fed) SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2087 |  | JE24038711 | JUNCTION RD | Western | JUNCTION RD | 2024-10-19 | 17:31 | 2024-10-19 | 18:28 | 0.006311 | 0.00011588 | 42 | 2287 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Broken Dead ends at Pole 747077 Isolated at ABS's 548 & 229 , plus fuse for Transformer 1170 Dead ends replaced | .
2088 |  | JE24038719 | POHANGINA | Western | POHANGINA | 2024-10-19 | 18:24 | 2024-10-19 | 23:39 | 0.059329 | 0.00060697 | 220 | 21504 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11KV REC F55 Protection flags (nil where none): A, B & C ph O/C CAUSE: Big Willow tree through lines Location: Pole P14492 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: cursory Weather (wind/rain): calm LFI (Y/N + Comments): N Follow up Required (select advisory)? N Additional fault restoration comments: Received a call of tree through lines, line was isolated at ABS's F59 & F61 to remove the tree and repair the lines. | .
2089 |  | JE24038728 | CHERRYWOOD DRIVE | Eastern | CHERRYWOOD DRIVE | 2024-10-19 | 20:34 | 2024-10-19 | 21:29 | 0.094422 | 0.0017299 | 627 | 34224 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 1 Protection flags (nil where none): E/F, O/C 1 CAUSE: Cable fault Location: Between CB 1 and Sw/Gear SD4-281 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): 2410011 Circuit patrolled and type: Cursory Weather (wind/rain): calm LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Back feeds put into place, fault cable has been I & E Called SMC for ETA for completion of work going to locate fault 22.10.24 Job to be completed under Napa | .
2090 |  | JE24033148 | 40 GRAY AVENUE KUAOTUNU WEST WHITIANGA | Eastern | BUFFALO BEACH | 2024-10-18 | 8:30 | 2024-10-18 | 13:57 | 0.005404 | 1.6554e-05 | 6 | 1959 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Level TP308. Install LV switchgear. Replace and relocate pillar and LV cabling due to flooding | .
2091 |  | JE24035513 | 182 MT CURL ROAD HUNTERVILLE HUNTERVILLE | Western | HUNTERVILLE 22KV | 2024-10-18 | 9:01 | 2024-10-18 | 13:11 | 0.010323 | 4.1384e-05 | 15 | 3742 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Red Tagged Pole 804582 | .
2092 |  | JE24035719 | 62 GIBBON ROAD HUNTERVILLE HUNTERVILLE | Western | HUNTERVILLE 22KV | 2024-10-18 | 9:01 | 2024-10-18 | 11:56 | 0.0028939 | 1.6554e-05 | 6 | 1049 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 2 X Red Tagged poles 807079 & 807078 | .
2093 |  | JE24035723 | WAIHI NORTH | Eastern | WAIHI NORTH | 2024-10-18 | 9:30 | 2024-10-18 | 13:00 | 0.020267 | 9.6564e-05 | 35 | 7346 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | String fibre between poles P1572 & P13737. Replace pole P13736 | .
2094 |  | JE24035726 | 237 HUBBARD ROAD PAEROA PAEROA | Eastern | RAILWAY ST | 2024-10-18 | 9:16 | 2024-10-18 | 12:27 | 0.010011 | 5.242e-05 | 19 | 3629 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv Xarms at pole's N0763,N0761,N0756 and N0750. | .
2095 |  | JE24035731 | 71 MOTUMAOHO ROAD, MORRINSVILLE | Eastern | MOTUMAOHO | 2024-10-18 | 9:00 | 2024-10-18 | 14:54 | 0.022412 | 6.3456e-05 | 23 | 8123 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 400v conductor between I0759 & I0768 | .
2096 |  | JE24035752 | 105 NO 1 ROAD TE PUKE TE PUKE | Eastern | RANGIURU | 2024-10-18 | 9:45 | 2024-10-18 | 12:20 | 0.0008527 | 5.5179e-06 | 2 | 309 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Rotten Crossarms at pole 220970 | .
2097 |  | JE24036042 | 29 JACKEYTOWN ROAD TIAKITAHUNA PALMERSTON NORTH | Western | BAINESSE | 2024-10-18 | 7:30 | 2024-10-18 | 12:10 | 0.020016 | 9.3805e-05 | 34 | 7255 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | HV reconductor of 22 spans from P45242 - P45221 | .
2098 |  | JE24037501 | BUCKLAND RD | Eastern | BUCKLAND RD | 2024-10-18 | 9:30 | 2024-10-18 | 11:10 | 0.00055299 | 5.5179e-06 | 2 | 200 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE HV BARRELS AND TEST TRANSFORMER TP569, AS CUSTOMER IS HAVING VOLTAGE PROBLEMS. MAY REQUIRE REPLACEMENT | .
2099 |  | JE24038622 | MOUNT BRUCE | Western | MOUNT BRUCE | 2024-10-18 | 12:18 | 2024-10-18 | 13:13 | 0.001944 | 3.5867e-05 | 13 | 705 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Floating Conductor found at Pole 834273 Isolated at Fuses 7028 Floater repaired FM stated 2R no Required | .
2100 |  | JE24038661 | WAITARA RD | Western | WAITARA RD | 2024-10-18 | 18:32 | 2024-10-18 | 19:02 | 0.0034463 | 0.00011312 | 41 | 1249 | Unplanned | THIRD PARTY INTERFERENCE - OTHER | Faultman isolated line between ABS's 347 & 355 for safety, so a digger could be recovered that had fallen over while been unloaded from transporter. | .
2101 |  | JE24038675 | TOTMANS RD | Eastern | TOTMANS RD | 2024-10-18 | 21:16 | 2024-10-18 | 23:53 | 0.027804 | 0.00017657 | 64 | 10078 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 3 Protection flags (nil where none): Nil CAUSE: Broken cross arm Location: Pole E1594 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4, not patrolled. Weather (wind/rain): Calm LFI (Y/N + Comments): No. LFIs installed. Follow up Required (select advisory)? No Additional fault restoration comments: Double HV pin cross arm broken Replaced Double HV pin cross arm complete assembly SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2102 |  | JE24035352 | 285 TOKO ROAD TOKO STRATFORD | Western | TOKO | 2024-10-17 | 9:46 | 2024-10-17 | 15:57 | 0.095053 | 0.00025658 | 93 | 34452 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 740258, 740240, 740238, Replace xarms 740233, 740232, 740230 | .
2103 |  | JE24035408 | 200 HIKUAI SCHOOL ROAD HIKUAI HIKUAI | Eastern | HIKUAI | 2024-10-17 | 8:45 | 2024-10-17 | 14:27 | 0.037698 | 0.00011036 | 40 | 13664 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE 11KV XARMS AT POLE U12749, U0759, U0767,U12754, | .
2104 |  | JE24035551 | 946 BRISTOL ROAD WAITUI INGLEWOOD | Western | BRISTOL RD | 2024-10-17 | 9:02 | 2024-10-17 | 14:48 | 0.011441 | 3.3108e-05 | 12 | 4147 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Vegetation clearance in between poles 759771 - 759774 | .
2105 |  | JE24035571 | WAIMAPU | Eastern | WAIMAPU | 2024-10-17 | 9:03 | 2024-10-17 | 14:36 | 0.022063 | 6.6215e-05 | 24 | 7997 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles and / or crossarms 211158 to 211165 | .
2106 |  | JE24035668 | 280 BATTERSEA ROAD MORRISONS BUSH GREYTOWN | Western | MOROA | 2024-10-17 | 9:01 | 2024-10-17 | 13:53 | 0.061188 | 0.00020968 | 76 | 22178 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles and hardware between S502 and S596 | .
2107 |  | JE24035682 | 29 RANGATAHI ROAD RATANA WANGANUI | Western | MARTON | 2024-10-17 | 8:48 | 2024-10-17 | 12:17 | 0.0069084 | 3.3108e-05 | 12 | 2504 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT: Re-sag 11kV conductor at multiple sites and install bird diverters between 794799 - 794800. | .
2108 |  | JE24035705 | 138 LINCOLN ROAD INGLEWOOD INGLEWOOD | Western | LEPPERTON | 2024-10-17 | 9:45 | 2024-10-17 | 15:47 | 0.012984 | 3.5867e-05 | 13 | 4706 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To Replace TX structures TX 570 and TX 1044 | .
2109 |  | JE24035706 | 1711 WAIHI WHANGAMATA ROAD WHIRITOA WHANGAMATA | Eastern | WHIRITOA | 2024-10-17 | 10:39 | 2024-10-17 | 14:35 | 0.00065181 | 2.759e-06 | 1 | 236 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 3m LV arm and mount transformer | .
2110 |  | JE24035707 | OHAKEA | Western | OHAKEA | 2024-10-17 | 9:47 | 2024-10-17 | 14:25 | 0.18483 | 0.00066491 | 241 | 66994 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove hedge from 400v and 11kv at 4 Punga st, Tangimoana. Replace badly spalling pole P34091 2078 Tangimoana rd | .
2111 |  | JE24035709 | 48 PAHIATUA MANGAHAO ROAD MANGAMUTU PAHIATUA | Western | MANGATAINOKA | 2024-10-17 | 9:36 | 2024-10-17 | 13:56 | 0.0057408 | 2.2072e-05 | 8 | 2081 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To Replace 11kv arms at P01260,11kv insulators at P00010 , tigthen bolts and nuts at P04702,P04704 | .
2112 |  | JE24035881 | 106 TIRAU STREET PUTARURU PUTARURU | Eastern | BENT ST | 2024-10-17 | 8:32 | 2024-10-17 | 13:30 | 0.03862 | 0.00012967 | 47 | 13998 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install new RMU 14944 beside TC3738 at 106 Tirau Street, Putaruru Feeder not left in normal config, to check phasing at Sw/Gear 14944/3 Sw/Gear IC3152 was closed, as Sw/Gear IC3152 is a ABB series 1, to open will require a back feeds to be put in place and a small outage for TFR TC316 & TC2666 Sw/Gear 14944/3 left as the open point until feeder back to normal | .
2113 |  | JE24035902 | 2 MICHAEL WAY JUDEA TAURANGA | Eastern | SUMMIT | 2024-10-17 | 9:31 | 2024-10-17 | 14:02 | 0.046493 | 0.00017106 | 62 | 16852 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install automation retrofit kit on ABB Safelink 13424 | .
2114 |  | JE24038432 | WAITOTARA | Western | WAITOTARA | 2024-10-17 | 9:54 | 2024-10-17 | 11:15 | 0.00044695 | 5.5179e-06 | 2 | 162 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: X1258 No. Fuses: 1 Fuse Amp Size: 3 Amp TIME CLOSED: 22:05 hrs Cause: Unk Weather (wind/rain): Calm Follow up required (select advisory)? Additional Info: FM is awre of this Transformer blowing HV fuses. Replaced 63A LV fuses with 32A to provide proper discrimination as Tx is only 15kVA. FM will contact customer in the morning to check if power is ok. If Yes will close off 2R. If No and HV fuse has blown he will replace Tx tomorrow using 2R. 17/10/2024 Isolation: TX X1258 Fuses CAUSE: Internal Fault on Transformer X1258 Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Clear Follow up required (select advisory)? No Additional fault restoration comments: 1 x HV Fuse was always failing.(Blowing) Transformer is currently being replaced under AP 8432-01 New Transformer has been installed. Power ON at 11:15 Voltage tests correct on site. | .
2115 |  | JE24038441 | MANAIA | Western | MANAIA | 2024-10-17 | 2:20 | 2024-10-17 | 4:44 | 0.015339 | 0.00023727 | 86 | 5560 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV, Rec 8762 Protection flags (nil where none): E/F, O/C A-B phase CAUSE: Lines Down Location: 718618 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Yes / Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Repair HV lines down SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2116 |  | JE24038446 | MALEME EXPRESS | Eastern | MALEME EXPRESS | 2024-10-17 | 6:27 | 2024-10-17 | 14:38 | 0.099613 | 0.00058766 | 213 | 36105 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: GMCB 14316/4 Protection flags (nil where none): OC Phase A & B CAUSE: Truck Versus Pole, reversed into pole Location: Pole 263426 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): n/a Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Pole replaced Links TEMP060 could not be closed to energize Transformers as Transformer were all above 200kVA, hence transformers had to be individually energised SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): No Circuit that tripped: DTF (KM): 15-20min ETA - Firecomms advised | .
2117 |  | JE24038453 | PUTORINO | Western | PUTORINO | 2024-10-17 | 7:35 | 2024-10-17 | 9:46 | 0.00071814 | 5.5179e-06 | 2 | 260 | Unplanned | WILDLIFE - BIRD | Fuses Location: X2897 No. Fuses: 3 Fuse Amp Size: 2 Amp TIME CLOSED: 09:45 Cause: Bird strike Weather (wind/rain): Clear Follow up required (select advisory)? No | .
2118 |  | JE24038495 | MOUNT BRUCE | Western | MOUNT BRUCE | 2024-10-17 | 10:48 | 2024-10-17 | 12:03 | 0.01535 | 0.00020416 | 74 | 5564 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC C223/2 (Did not trip) Protection flags (nil where none): Nil CAUSE: Deterioration Location: Pole 834 246 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Clear LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Broken binder at Pole 834 246 Nearest Isolation point is back at REC C223/2 Repairs have been made. Full Power restored at 12:03 Field Switcher confirmed Power is restored at/near work site. | .
2119 |  | JE24038498 | 10 LEAMINGTON STREET, CASTLECLIFF, WANGANUI, 4501 | Western | BEACH RD | 2024-10-17 | 12:32 | 2024-10-17 | 12:46 | 3.6602e-05 | 2.759e-06 | 1 | 13 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV Sw/Gear 4681/1 (Feeder did not trip) Protection flags (nil where none): Nil CAUSE: Truck vs Pole Location: Pole 771103 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Clear LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Truck made contacted with HV Cable at Pole 771103 Cable was pulled away from the Pole and the clips were broken. (No electrical damage) Power was turned off to re-secure the Cable to the Pole. Field Switcher made arrangements with Cavalier Spinners Ltd for 12:30pm (Lunch break) Job was carried out and Power restored at 12:45 SAFETY MANAGER | .
2120 |  | JE24038532 | ARAHINA 33KV | Western | ARAHINA 33KV | 2024-10-17 | 16:09 | 2024-10-17 | 23:43 | 0.98196 | 0.0030293 | 1098 | 355915 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 33kV CB 3086, 22kV CB 1133 Protection flags (nil where none): E/F, O/C B, E/F, O/C A CAUSE: Car V pole Location: Pole 805053 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): calm LFI (Y/N + Comments): na Follow up Required (select advisory)? n Additional fault restoration comments: fire at crash site, could not be put out until network I & E Isolated 33kV ABS 3008, 3016, 3012, Links 3007, 22kV ABS 16085 & 796 Car V Pole 805053, unable to back feed Rata as the circuits that is isolated is the back feed feeder SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Rata Circuit that tripped: Arahina CB 3086 DTF (KM):na | .
2121 |  | JE24038537 | STATION RD | Eastern | STATION RD | 2024-10-17 | 17:10 | 2024-10-17 | 18:41 | 0.00024969 | 2.759e-06 | 1 | 91 | Unplanned | WILDLIFE - BIRD | Fuses Location: FC2122 No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 18:40 Cause: Bird strike Weather (wind/rain): Calm Follow up required (select advisory)? No | .
2122 |  | JE24038548 | BBK Sub - CB 1 | Western | DE HAVILLAND NORTH | 2024-10-17 | 20:33 | 2024-10-18 | 5:24 | 0.047793 | 0.00035315 | 128 | 17323 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV, CB 1 Protection flags (nil where none): O/C B-C phase CAUSE: Car vs Pole Location: Pole 743615 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Calm LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Replaced Pole & Hardware at Pole 743615. 11kV cable supplying that pole has been disconnected to allow ongoing repairs to cable. 11kV Crossarm & Hardware was also replaced at Pole 743616 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2123 |  | JE24035450 | 128 JACKEYTOWN ROAD TIAKITAHUNA PALMERSTON NORTH | Western | BAINESSE | 2024-10-16 | 8:30 | 2024-10-16 | 11:45 | 0.018278 | 9.3805e-05 | 34 | 6625 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | LV reconductor P43233-372413 | .
2124 |  | JE24035453 | 84 WAUGHS ROAD AORANGI FEILDING | Western | WORKS | 2024-10-16 | 9:01 | 2024-10-16 | 13:25 | 0.0036405 | 1.3795e-05 | 5 | 1320 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace HV and LV arms on P37554 | .
2125 |  | JE24035512 | 83 JELLICOE STREET MARTINBOROUGH MARTINBOROUGH | Western | DYERVILLE | 2024-10-16 | 8:45 | 2024-10-16 | 14:48 | 0.27733 | 0.00076699 | 278 | 100518 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV ABS S574 at Pole 813712. | .
2126 |  | JE24035517 | WHAKAMARAMA | Eastern | WHAKAMARAMA | 2024-10-16 | 9:31 | 2024-10-16 | 12:10 | 0.00044047 | 2.759e-06 | 1 | 160 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace HT arm & DDO's + arm | .
2127 |  | JE24035522 | 23 THE CRESCENT WAIHI BEACH WAIHI BEACH | Eastern | WILSON RD | 2024-10-16 | 9:45 | 2024-10-16 | 14:02 | 0.055277 | 0.0002152 | 78 | 20036 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | CREATE 11KV LINE BREAK AT POLE 346188 USING GB1,GB3 & GB27, REPLACE 11KV XARM AT POLE 874964, REPLACE LV PIN INSULATORS AT POLE Q0298, CLOSE 11KV LINE BREAK AT POLE 346188 USING GB1,GB3 & GB25 | .
2128 |  | JE24035549 | 71 MOTUMAOHO ROAD, MORRINSVILLE | Eastern | MOTUMAOHO | 2024-10-16 | 9:00 | 2024-10-16 | 13:47 | 0.018202 | 6.3456e-05 | 23 | 6598 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv conductor between I0759 & I0768 | .
2129 |  | JE24035550 | 87 MILLERS ROAD BROOKFIELD TAURANGA | Eastern | CENTRAL OTUMOETAI | 2024-10-16 | 23:31 | 2024-10-17 | 3:28 | 0.060118 | 0.00025382 | 92 | 21790 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9115/1/2/3 | .
2130 |  | JE24035567 | 596 MAUNGARANGI ROAD PAENGAROA TE PUKE | Eastern | MAUNGARANGI RD | 2024-10-16 | 9:19 | 2024-10-16 | 14:32 | 0.046617 | 0.00014898 | 54 | 16897 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv overhead conductors between poles 263437 & 230055 with ACSR Ferret | .
2131 |  | JE24037322 | TAIRUA NORTH | Eastern | TAIRUA NORTH | 2024-10-16 | 8:31 | 2024-10-16 | 15:02 | 0.045256 | 0.00011588 | 42 | 16403 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Helicopter stringing fibre between poles W13420 & W13550 / W13549 | .
2132 |  | JE24038089 | 20 MAY STREET MOUNT MAUNGANUI TAURANGA | Eastern | TAWA ST | 2024-10-16 | 23:00 | 2024-10-17 | 0:39 | 0.03644 | 0.0003697 | 134 | 13208 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | disconnect generator at TC4-258 connect new 11kv cable at TC4-258 & TC4-199 L2 "Will remove DNO" | .
2133 |  | JE24038326 | GULLIVER RD | Eastern | GULLIVER RD | 2024-10-16 | 3:56 | 2024-10-16 | 5:31 | 0.00078601 | 8.2769e-06 | 3 | 285 | Unplanned | WILDLIFE - BIRD | Fuses Location: FP894 No. Fuses: 2 Fuse Amp Size: 8 TIME CLOSED: 05:30 Cause: Bird Strike Weather (wind/rain): calm Follow up required (select advisory)? N | .
2134 |  | JE24038384 | NGARUA | Eastern | NGARUA | 2024-10-16 | 11:55 | 2024-10-16 | 13:31 | 0.0007886 | 8.2769e-06 | 3 | 286 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: TX TC878 Protection flags (nil where none): CAUSE: Tractor took down LV Lines, blew HV Fuses not LV Fuses, 2 X 3A HV FUSES AT TX TC878 REPLACED AT 13:30, LV Line repaired, crimps and conductor used. Location: Temp generation (state details when used): N Lines not live on arrival, full power restored PERFORMANCE DETAIL NA DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL NA LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): Job upgraded with Hazard and Emergency due to lines down. SMC informed Fire are attending, Event No: F4068479 - ETA 16mis, Fire Comms have been advised | .
2135 |  | JE24038386 | 144 TORA FARM SETTLEMENT ROAD, TORA, MARTINBOROUGH, 5782 | Western | TUTURUMURI | 2024-10-16 | 13:31 | 2024-10-16 | 14:25 | 0.0040164 | 7.4492e-05 | 27 | 1456 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Found Floating Conductor at Pole isolated at ABS S546 | .
2136 |  | JE24038445 | RANGITIKEI | Western | RANGITIKEI | 2024-10-16 | 22:15 | 2024-10-17 | 2:08 | 0.024441 | 0.00010484 | 38 | 8859 | Unplanned | THIRD PARTY INTERFERENCE - OVERHEAD CONTACT | Cause: House Moving Truck reported to have contacted HV & LV lines bringing down LV road crossing & blowing 2x HV Fuses at Fuses D24. What was replaced? 30metres of 16mm conductor & 2 conductor joints. 2x 15A HV fuse links & 1x HV fuse carrier reloaded at 02:08 Where was it replaced (pole/TX/pillar box)? P33880 Is 2R required? Y 2R Y - What is the timeframe for repairs? Completed Additional Info: Traffic Management called to site for SH3. NDR to follow | .
2137 |  | JE24034517 | 17 KAWEORA ROAD OPUNAKE OPUNAKE | Western | TE KIRI | 2024-10-15 | 9:30 | 2024-10-15 | 15:03 | 0.02384 | 7.1733e-05 | 26 | 8641 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove ABS TA930. install new entec 12759 structure at pole site 714134 | .
2138 |  | JE24035294 | 1756 WAIHI VALLEY ROAD PONGAROA | Western | HOROEKA | 2024-10-15 | 9:49 | 2024-10-15 | 15:46 | 0.10762 | 0.00030073 | 109 | 39006 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace 11kV ABS V7 and 11kV ABS V15. | .
2139 |  | JE24035350 | 201 BLACK ROAD PAENGAROA TE PUKE | Eastern | OLD COACH RD | 2024-10-15 | 8:49 | 2024-10-15 | 14:27 | 0.056831 | 0.0001683 | 61 | 20599 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv overhead conductors with 3W Squirrel between poles 221712 & 221721. Isolation point @ ABS 14861.Issuer earths @ Pole 221711(221712 side) | .
2140 |  | JE24035383 | 83 PORTSIDE DRIVE MOUNT MAUNGANUI TAURANGA | Eastern | NEWTON ST | 2024-10-15 | 23:30 | 2024-10-16 | 4:29 | 0.063371 | 0.00021244 | 77 | 22969 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9156/1/2/3/4 | .
2141 |  | JE24035390 | KEREONE | Eastern | KEREONE | 2024-10-15 | 9:45 | 2024-10-15 | 14:31 | 0.0047308 | 1.6554e-05 | 6 | 1715 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | at poles 878199 and I2246 replace with new 11m buscks at pole I12594 replace all arms and hardware - replace TX earthing and stays | .
2142 |  | JE24035396 | 137 PUKETUI VALLEY ROAD HIKUAI HIKUAI | Eastern | HIKUAI | 2024-10-15 | 9:40 | 2024-10-15 | 15:45 | 0.040248 | 0.00011036 | 40 | 14588 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE 11KV XARMS AT POLES U0754, U0755, U0756, U0757, | .
2143 |  | JE24035399 | 813 WORTLEY ROAD WAIONGANA INGLEWOOD | Western | LEPPERTON | 2024-10-15 | 9:31 | 2024-10-15 | 14:19 | 0.043783 | 0.00015174 | 55 | 15869 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To Replace structure tx 1137 + change Tx's 1434 + 384 | .
2144 |  | JE24035413 | 280 BATTERSEA ROAD MORRISONS BUSH GREYTOWN | Western | MOROA | 2024-10-15 | 9:00 | 2024-10-15 | 13:35 | 0.057718 | 0.00020968 | 76 | 20920 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles and hardware between S502 and S596 | .
2145 |  | JE24035416 | 1 HENDERSONS LINE KELVIN GROVE PALMERSTON NORTH | Western | ASHHURST | 2024-10-15 | 8:30 | 2024-10-15 | 14:01 | 0.057414 | 0.00017381 | 63 | 20810 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Poles and Xarms between and including P41027 & P41049. | .
2146 |  | JE24035516 | WAIMAPU | Eastern | WAIMAPU | 2024-10-15 | 9:04 | 2024-10-15 | 15:31 | 0.037375 | 9.6564e-05 | 35 | 13547 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 1) Replace poles 211219 to 211229. 2) Remove UG 11kV Cable 211222 - 211223. 3) Install new UG HV Cable with LA's on pole 211222 and joint to existing UG cable feeding TE4-212 4) Install new UG HV Cable with LA's on pole 211229 and joint to existing UG Cable feeding TE4-139 | .
2147 |  | JE24035757 | 338 WESTERN LAKE ROAD WESTERN LAKE FEATHERSTON | Western | KUMENGA | 2024-10-15 | 9:15 | 2024-10-15 | 14:15 | 0.052996 | 0.00017657 | 64 | 19209 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Change 11kv arms between 798533 & 372980 Western Lake Rd . Relocate 11kV fuses 7272 to Pole 372980. | .
2148 |  | JE24038157 | TE ARAKURA | Western | TE ARAKURA | 2024-10-15 | 9:05 | 2024-10-15 | 11:36 | 0.00041568 | 2.759e-06 | 1 | 151 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: CAUSE: Lightning Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: Weather (wind/rain): lightning Follow up required (select advisory)? Additional fault restoration comments: Tried to re-liven, TX damaged, will be replaced under 2R, TX T2/388. Tx T2/388 replaced | .
2149 |  | JE24038193 | HUKANUI | Western | HUKANUI | 2024-10-15 | 5:45 | 2024-10-15 | 7:52 | 0.0010504 | 8.2769e-06 | 3 | 381 | Unplanned | WILDLIFE - BIRD | Fuses Location: 10412 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 07:52 Cause: BIRDS Weather (wind/rain): RAIN Follow up required (select advisory)? 2R Left open, Downer to follow up with Network performance if defect or 2R, this happen a lot according to customers due to birds on river, To help the river crossing could be changed to 3m xarms and/ or delta configuration. Full power restored. Finn advised 2R can be completed. Fault has been actioned | .
2150 |  | JE24038195 | HAURAKI RD | Eastern | HAURAKI RD | 2024-10-15 | 6:09 | 2024-10-15 | 7:00 | 0.0015454 | 3.0349e-05 | 11 | 560 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: FP1882 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 07:00 Cause: Unknown lines patrolled Weather (wind/rain): Calm Follow up required (select advisory)? No | .
2151 |  | JE24038197 | MAKIRIKIRI | Western | MAKIRIKIRI | 2024-10-15 | 6:40 | 2024-10-15 | 9:41 | 0.021422 | 0.00011864 | 43 | 7764 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: 586 No. Fuses: 2 Fuse Amp Size: 15A TIME CLOSED: 09:40 Cause: UNKNOWN Weather (wind/rain): RAIN Follow up required (select advisory)? FULL POWER | .
2152 |  | JE24038200 | WESTMERE GLADSTONE | Western | WESTMERE GLADSTONE | 2024-10-15 | 6:55 | 2024-10-15 | 9:10 | 0.0014895 | 1.1036e-05 | 4 | 540 | Unplanned | WILDLIFE - POSSUM | Fuses Location: T1969 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 09:10 Cause: POSSUM Weather (wind/rain): RAIN Follow up required (select advisory)? Address correct but assigned tx not, have emailed AI admin | .
2153 |  | JE24038219 | POHANGINA | Western | POHANGINA | 2024-10-15 | 8:48 | 2024-10-15 | 14:07 | 0.0026407 | 8.2769e-06 | 3 | 957 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T4/102 No. Fuses: 3 Fuse Amp Size: 3 Amp TIME CLOSED: 14:07 hrs Cause: Lightning Weather (wind/rain): Heavy Rain Follow up required (select advisory)? Additional Info: Incorrect Transformer supplied | .
2154 |  | JE24038237 | MEREMERE | Western | MEREMERE | 2024-10-15 | 10:15 | 2024-10-15 | 14:05 | 0.001267 | 5.5179e-06 | 2 | 459 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: LV Meterboard on fire Tag no: A42573 Customer advised? Yes Disco safety register + emailed retailer: N/A (Repaired on site with a private Electrician) Is 2R required? Yes Additional Info: LV Meterboard has been replaced and re-livened. Transformer 5396E Fuses blown due to LV fault Fuses Location: TX 5396E No. Fuses: 1 Fuse Amp Size: 3 Amp TIME CLOSED: Failed twice at 09:40 & 10:09 Cause: LV Meterboard fault Weather (wind/rain): Clear Follow up required (select advisory)? No Reload + Re-liven failed at 09:40 Field Switcher to remove LV Fuses and then try Reloading HV Fuses again. Reload + Re-liven failed at 10:09 (LV Fuses open) Transformer 5396E is faulty and needs to be replaced. Transformer has now been replaced with a new one. Full Power restored at 14:05 Voltage tests and Loop Test were all good. | .
2155 |  | JE24038249 | 1497 State Highway 2, Kiriwhakapapa, Masterton, 5881 | Western | MOUNT BRUCE | 2024-10-15 | 11:36 | 2024-10-15 | 12:39 | 0.012962 | 0.00020416 | 74 | 4698 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: C223 Protection flags (nil where none): CAUSE: Floating Conductor Location: 834063 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Calm LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Replaced broken copper binder SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2156 |  | JE24038268 | PIHAMA | Western | PIHAMA | 2024-10-15 | 11:25 | 2024-10-15 | 11:35 | 2.8969e-05 | 2.759e-06 | 1 | 11 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: TX T5325 No. Fuses: 3 & 2 barrels Fuse Amp Size: 3 Amp TIME OPEN: 11:24 TIME CLOSED: 11:35 Cause: Deteriorated on the barrels causing high impedance. Weather (wind/rain): Clear Follow up required (select advisory)? No High Loop Impedance Test results: Test results were all good after barrels were replaced. | .
2157 |  | JE24038274 | MEREMERE | Western | MEREMERE | 2024-10-15 | 13:45 | 2024-10-15 | 15:22 | 0.00053754 | 5.5179e-06 | 2 | 195 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: TX W1190 Fuses CAUSE: Defective Transformer W1190 Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Clear Follow up required (select advisory)? No Additional fault restoration comments: Transformer keeps blowing fuses, going back several weeks. Field Switcher is busy with the Isolation and Earthing Transformer will be replaced under an AP Transformer W1190 has now been replaced. Full Power restored at 15:22 | .
2158 |  | JE24038276 | TAIHAPE A 33KV | Western | TAIHAPE A 33KV | 2024-10-15 | 12:44 | 2024-10-16 | 14:09 | 0.087773 | 0.0025079 | 894 | 31814 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 4 Protection flags (nil where none): A & B Ø O/C CAUSE: Truck vs Pole Location: Pole 789 399 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes, only Hazard site. Weather (wind/rain): Clear LFI (Y/N + Comments): Yes at TPE S/S on Sw/Gear 4537/1 Follow up Required (select advisory)? Yes Additional fault restoration comments: Truck vs Pole caused the feeder fault at TPE CB 4 Field Switcher was informed of the Hazard at 2 Kuku Street, arrived on site and confirmed a Truck had damaged the Pole, all the HV O/H Lines were up in the air and it was safe to re-liven AT TPE S/S CB 4 Power restored at 13:14 - Awaiting further details if the Pole must be replaced today? Live Line Truck is supporting Pole 789 399 for the interim. 24 Hr Work Notice Form will be sent to NOC for repairs on 16/10/2024 16/10/24 - Pole replaced under Switching E00155, Line break cut under LLP, pole replaced under AP, Line break closed under LLP, Full power restored SAFETY MANAGER on closure | .
2159 |  | JE24038278 | MCCABE ROAD | Eastern | MCCABE ROAD | 2024-10-15 | 18:36 | 2024-10-15 | 18:47 | 0.0012599 | 0.00011036 | 40 | 457 | Unplanned | THIRD PARTY INTERFERENCE - OTHER | Faultman de-energized lines at ABS 1257 to remove rolled up old electric fence wire with hot line sticks between poles C13707 & 482768. | .
2160 |  | JE24038296 | TAWHITI RD | Western | TAWHITI RD | 2024-10-15 | 16:04 | 2024-10-15 | 16:51 | 0.00064123 | 1.3795e-05 | 5 | 232 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses CA465 No. Fuses: 2 Fuse Amp Size: 8 Amp TIME OPEN: 16:04 (Opened remaining HV Fuse) TIME CLOSED: 16:50 Cause: Unknown - No fault found. Weather (wind/rain): Clear Follow up required (select advisory)? No Busy with a Line Patrol Line Patrol carried out and nothing abnormal was sighted. Full Power restored at 16:50 | .
2161 |  | JE24038314 | STATION RD | Eastern | STATION RD | 2024-10-15 | 18:32 | 2024-10-15 | 19:50 | 0.0077306 | 9.9323e-05 | 36 | 2802 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | solation: 11kV ABS IC1346 CAUSE: Deterioration (Old age) Location: Pole G0403 Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: No, reported by a member of public. Weather (wind/rain): Calm Follow up required (select advisory)? No Additional fault restoration comments: FM has spoken to Network controller to set up for a crew and traffic management to attend for replacement, FM also advised that he has taken photos and NC has arranged for switch writing for job to be done. FM advised this is HV and he is only pre planning and can be taken off the 1R Rotten cross-arm and king bolt is cracked at Pole G0403 Materials and field crew are being arranged at the moment. Repairs will be carried out this evening. Line was isolated at ABS IC1346 & Links 14557/4 to replace rotten cross arm and king bolt due to deuteriation. Safety Manager Required? No | .
2162 |  | JE24038323 | PURIRI ST | Western | PURIRI ST | 2024-10-15 | 22:50 | 2024-10-16 | 0:13 | 0.0070155 | 8.5528e-05 | 31 | 2543 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuse/Sw 16026/2 No. Fuses: 3 Fuse Amp Size: 25A TIME CLOSED: 00:12 Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)? | .
2163 |  | JE24035197 | POHANGINA | Western | POHANGINA | 2024-10-14 | 8:50 | 2024-10-14 | 9:52 | 0.028166 | 0.00045799 | 166 | 10209 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Collect oil sample from regulator 10081 | .
2164 |  | JE24035274 | 859 HALCOMBE ROAD HALCOMBE FEILDING | Western | MT STEWART | 2024-10-14 | 11:56 | 2024-10-14 | 13:10 | 0.0045199 | 6.0697e-05 | 22 | 1638 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Collect oil sample from regulator 10112 | .
2165 |  | JE24035276 | 108 JACKEYTOWN ROAD TIAKITAHUNA PALMERSTON NORTH | Western | BAINESSE | 2024-10-14 | 8:31 | 2024-10-14 | 14:55 | 0.036076 | 9.3805e-05 | 34 | 13076 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | LV reconductor P43226 to P43233 - site 1 LV reconductor P45232 to P45236 - site 2 | .
2166 |  | JE24035282 | 71 MOTUMAOHO ROAD, MORRINSVILLE | Eastern | MOTUMAOHO | 2024-10-14 | 9:00 | 2024-10-14 | 14:00 | 0.019006 | 6.3456e-05 | 23 | 6889 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Poles I13097. I0765, I0767, I13098, I13099, I0768. Replace 400V Road Crossing | .
2167 |  | JE24037978 | WEST ST | Western | WEST ST | 2024-10-14 | 1:57 | 2024-10-14 | 2:28 | 0.014256 | 0.00044971 | 163 | 5167 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | REGULATORY INFORMATION Voltage & Device ID: Recloser C430 Protection flags (nil where none): None CAUSE: broken JUMPER Location: Pole 818420 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): Rainy LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Recloser had earlier tripped twice at 23:04 and 23:11 on Phase BC OC SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2168 |  | JE24037982 | MAKETU | Eastern | MAKETU | 2024-10-14 | 5:18 | 2024-10-14 | 8:12 | 0.32828 | 0.0026762 | 970 | 118987 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: CB4 Protection flags (nil where none): Ph A, B Fault CAUSE: Branch on lines Location: Pole 396005 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: cursory Weather (wind/rain): wind LFI (Y/N + Comments): Y - Poles 221621 & 381912 Follow up Required (select advisory)? n Additional fault restoration comments: Faultman cut away branch as much as possible so we no line contact and will defect tree to have it cut away by tree contractor under a planned CAC. | .
2169 |  | JE24037988 | IRIRANGI | Western | IRIRANGI | 2024-10-14 | 6:45 | 2024-10-14 | 9:32 | 0.0041525 | 2.4831e-05 | 9 | 1505 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 154 No. Fuses: 2 Fuse Amp Size: 6 Amp TIME CLOSED: 09:32 Cause: Unknown (Suspect bird strike) Weather (wind/rain): Calm Follow up required (select advisory)? No | .
2170 |  | JE24037992 | INLAND COAST | Western | INLAND COAST | 2024-10-14 | 6:51 | 2024-10-14 | 9:19 | 0.022841 | 0.0001545 | 56 | 8279 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 8470 No. Fuses: 2 Fuse Amp Size: 20 Amp TIME CLOSED: 09:18 Cause: Unknown (Suspect bird strike) Weather (wind/rain): Windy Follow up required (select advisory)? Yes, response time for a field switcher was very slow. | .
2171 |  | JE24038005 | MIRO ST | Western | MIRO ST | 2024-10-14 | 7:22 | 2024-10-14 | 9:46 | 0.004764 | 3.3108e-05 | 12 | 1727 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 7153 No. Fuses: 1 Fuse Amp Size: 10 Amp TIME CLOSED: 09:45 Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)? No Please check JE24038023 on completion | .
2172 |  | JE24038033 | KOPANE | Western | KOPANE | 2024-10-14 | 11:23 | 2024-10-14 | 12:20 | 0.0056846 | 9.9323e-05 | 36 | 2060 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: Aged Location: T2/907 Isolation: ABS C7 What was replaced? HV fuse holder, carrier, & 3A link Weather:Calm Additional Info: Fuse broke when FM was attempting a close at Transformer T2/907. Isolated at C7 to make repairs | .
2173 |  | JE24038052 | MATAPU | Western | MATAPU | 2024-10-14 | 11:47 | 2024-10-14 | 20:45 | 0.0014852 | 2.759e-06 | 1 | 538 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: TX K4192 Fuses CAUSE: Internal Fault on Transformer K4192 Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Calm Follow up required (select advisory)? No Additional fault restoration comments: Field Switcher busy Isolating and Earthing worksite to replace the faulty Transformer K4192 Update @ 14:35 - Spare 30kVA Transformer is not available at the depot. Awaiting further details to be provided. 17:11 - Transformer is being replaced under AP 8052-02 | .
2174 |  | JE24038088 | BAINESSE | Western | BAINESSE | 2024-10-14 | 14:16 | 2024-10-14 | 14:56 | 0.0055908 | 0.00014071 | 51 | 2026 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | When carrying out planned switching, Fuses B48 arced and flashed over causing feeder reclose (NAPA 113299). This caused damage to 2x HV fuseholders & 1x Polymer Insulator. Shutdown via ABS B44, and 2x fuseholders with 40A links, and 1x polymer insulator were replaced. This work was completed by Omexom who were the onsite Switching Operators. This has been put into safety manager under a different OMS job JE24038020 Safety Manager 1408508 | .
2175 |  | JE24038097 | GONVILLE AVE | Western | GONVILLE AVE | 2024-10-14 | 16:06 | 2024-10-14 | 18:23 | 0.0026587 | 1.9313e-05 | 7 | 964 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Cause: lighting What was replaced? TX X1575 Where was it replaced (pole/TX/pillar box)? X1575 Is 2R required? Y 2R Y - What is the timeframe for repairs? Complete Additional Info: Replaced 100/11/3phase Transformer 2R work will be to replace the TX which has been damaged by lighting. | .
2176 |  | JE24038123 | MT STEWART | Western | MT STEWART | 2024-10-14 | 16:09 | 2024-10-14 | 18:00 | 0.000922 | 8.2769e-06 | 3 | 334 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Transformer T3/57 No. Fuses: 3 Fuse Amp Size: 2A TIME CLOSED: 18:00 Cause: Lightning Weather (wind/rain): Stormy Follow up required (select advisory)? | .
2177 |  | JE24038129 | KETEMARAE RD | Western | KETEMARAE RD | 2024-10-14 | 17:07 | 2024-10-14 | 22:24 | 0.00087565 | 2.759e-06 | 1 | 317 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: Transformer 5053E Fuses CAUSE: Internal fault on Transformer 5053E Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Rain Follow up required (select advisory)? No Additional fault restoration comments: 11kV REC 12418/2 auto-reclosed twice at approximately 16:18 & 16:19 Job came through for No Power, field switcher found 1x HV fuse blown on arrival at Transformer 5053E Isolated faulty Transformer 5053E 17:53 - Awaiting spare Transformer to arrive on site - ETA is several hours at this time. 18:26 - SMC Requested to have Jacob offsite, a crew is being organised to come back later this evening | .
2178 |  | JE24038131 | TE ARAKURA | Western | TE ARAKURA | 2024-10-14 | 16:36 | 2024-10-14 | 17:46 | 0.0019126 | 2.759e-05 | 10 | 693 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Transformer T1/210 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 17:45 Cause: Lightning Weather (wind/rain): Stormy Follow up required (select advisory)? | .
2179 |  | JE24038135 | WORKS | Western | WORKS | 2024-10-14 | 16:51 | 2024-10-14 | 18:06 | 0.001232 | 1.6554e-05 | 6 | 447 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T2/921 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 18:05hrs Cause: Lightning Weather (wind/rain): Heavy Rain Follow up required (select advisory)? | .
2180 |  | JE24038139 | CHURCH ST | Western | CHURCH ST | 2024-10-14 | 17:10 | 2024-10-14 | 17:45 | 0.0010809 | 3.0349e-05 | 11 | 392 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | Fuses Location: 7651 No. Fuses: 2 Fuse Amp Size: 8 Amp TIME CLOSED: 17:45 hrs Cause: Tree branch sitting on lines. Removed using Hot Stick Weather (wind/rain): Windy / Heavy Rain Follow up required (select advisory)? | .
2181 |  | JE24038142 | POHANGINA | Western | POHANGINA | 2024-10-14 | 17:17 | 2024-10-14 | 20:32 | 0.0037706 | 1.9313e-05 | 7 | 1367 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T4/187 No. Fuses: 3 Fuse Amp Size: 6A & 2 x carriers TIME CLOSED: 2032 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? | .
2182 |  | JE24038152 | TE ARAKURA | Western | TE ARAKURA | 2024-10-14 | 17:40 | 2024-10-15 | 9:40 | 0.031796 | 3.3108e-05 | 12 | 11525 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T2/184 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 09:40 Cause: LIGHTNING Weather (wind/rain): RAIN Follow up required (select advisory)? FULL POWER | .
2183 |  | JE24038160 | PUTORINO | Western | PUTORINO | 2024-10-14 | 18:08 | 2024-10-14 | 21:10 | 0.009145 | 6.8974e-05 | 25 | 3315 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Fuses 495 No. Fuses: 1 Fuse Amp Size: 2A TIME CLOSED: 20:08 Cause: Lightning Weather (wind/rain): Stormy Follow up required (select advisory)? Fuses Location: Transformer X1834 No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 21:10 Cause: Lightning Weather (wind/rain): Stormy Follow up required (select advisory)? 2R used for the time taken patrolling the line checking all the Fuses due to the lightning. | .
2184 |  | JE24038161 | WORKS | Western | WORKS | 2024-10-14 | 18:16 | 2024-10-14 | 18:35 | 0.00016076 | 8.2769e-06 | 3 | 58 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T2/445 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 18:35hrs Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? | .
2185 |  | JE24038170 | MT STEWART | Western | MT STEWART | 2024-10-14 | 20:47 | 2024-10-15 | 0:11 | 0.0039298 | 1.9313e-05 | 7 | 1424 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: DTX T1/6 Fuses CAUSE: Lightning Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: Weather (wind/rain): Lightning Follow up required (select advisory)? Additional fault restoration comments: 3 Phase 50KVA | .
2186 |  | JE24038175 | POHANGINA | Western | POHANGINA | 2024-10-14 | 19:19 | 2024-10-14 | 21:00 | 0.00027801 | 2.759e-06 | 1 | 101 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T4/340 No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 2100 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? | .
2187 |  | JE24038181 | TE ARAKURA | Western | TE ARAKURA | 2024-10-14 | 20:10 | 2024-10-15 | 10:15 | 0.023975 | 0.00051317 | 183 | 8690 | Unplanned | LIGHTNING - LIGHTNING STRIKE | REGULATORY INFORMATION Voltage & Device ID: REC D77 Protection flags (nil where none): A & B phase EF CAUSE: Lightning Location: Tfr 7357P Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: N Weather (wind/rain): Lightning LFI (Y/N + Comments): N Follow up Required (select advisory)? Additional fault restoration comments: On livening Tfr 7357P REC D77 tripped. 7357P isolated and LV back feeds put in place at 2150. Replaced 15/11/3 phase transformer the following day | .
2188 |  | JE24034727 | COOK DRIVE | Eastern | COOK DRIVE | 2024-10-13 | 8:45 | 2024-10-13 | 15:07 | 0.16343 | 0.00042764 | 155 | 59237 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace inline H pole W12366/W12367 with double 12.5m Busck. Replace 100kVA pole mounted transformer. | .
2189 |  | JE24037107 | 886 BIDWILLS CUTTING ROAD MORRISONS BUSH GREYTOWN | Western | TAWAHA | 2024-10-13 | 9:01 | 2024-10-13 | 12:09 | 0.0036401 | 1.9313e-05 | 7 | 1319 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replce 33kv cross arm and insulators at pole 815338 / 815337 | .
2190 |  | JE24037256 | 5 MILSON LINE ROSLYN PALMERSTON NORTH | Western | FAIRS RD | 2024-10-13 | 13:27 | 2024-10-20 | 16:55 | 0.10064 | 0.0008608 | 156 | 36477 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE LEAKING RMU 152/153 | .
2191 |  | JE24037937 | TE PUNINGA | Eastern | TE PUNINGA | 2024-10-13 | 5:12 | 2024-10-13 | 6:20 | 0.0011293 | 1.6554e-05 | 6 | 409 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: FC2111 No. Fuses: 2 Fuse Amp Size: 25 TIME CLOSED: 06-19 Cause: Unknown Weather (wind/rain): Fine & cold Follow up required (select advisory)? | .
2192 |  | JE24037949 | MAURICEVILLE | Western | MAURICEVILLE | 2024-10-13 | 6:28 | 2024-10-13 | 9:02 | 0.0050912 | 3.3108e-05 | 12 | 1845 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses U19 No. Fuses: 2 and 1 x carrier Fuse Amp Size: 6A TIME CLOSED: 0901 Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)? | .
2193 |  | JE24035169 | COOK DRIVE | Eastern | COOK DRIVE | 2024-10-12 | 8:47 | 2024-10-12 | 16:52 | 0.045489 | 9.3805e-05 | 34 | 16488 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole W12966 with double 12.5m Busck. Replace 100kVA pole mounted transformer TC3660. JE24037916 created soon after this NAPA WAS COMPLETED | .
2194 |  | JE24035575 | 11 DUNLOP ROAD WAHAROA WAHAROA | Eastern | FACTORY RD | 2024-10-12 | 13:00 | 2024-10-12 | 16:17 | 0.0010871 | 5.5179e-06 | 2 | 394 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | CT Metering Checks on Metering unit supplying TC2155 and TC4617. Icepak | .
2195 |  | JE24037874 | 4 MELODY PLACE, MARTON, MARTON, 4710 | Western | MARTON | 2024-10-12 | 1:11 | 2024-10-12 | 2:16 | 0.011454 | 0.00017657 | 64 | 4151 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Loud Bang from pole just down the road and NO POWER now Faultman found that 1 x DDO had blown at Fused ABS 2550 Line/cable isolated at Fused ABS 2550 Line, cable terminations & HV side of TFR's inspected, no faults found, full power restored | .
2196 |  | JE24037895 | JOAN GASKELL DR | Eastern | JOAN GASKELL DR | 2024-10-12 | 8:47 | 2025-04-12 | 16:52 | 0.0013379 | 5.5179e-06 | 1 | 485 | Unplanned | OTHER | Job related to NAPA 114732, | .
2197 |  | JE24037896 | TAIRUA NORTH | Eastern | TAIRUA NORTH | 2024-10-12 | 11:51 | 2024-10-12 | 12:41 | 0.0057629 | 0.00011588 | 42 | 2089 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Dead ends loose at Regulator 9669 pole 332594.Please repair. Strands broken and conductor can snap anytime. Noticed by crew installing fibre. Unsafe for crew working near live lines in case it breaks. Urgent job to replace dead end Dead End replaced, was not broken but had slipped and conductors sagging -Conductors retensioned Power off 11:51 Power ON 12:40 | .
2198 |  | JE24037912 | STATION RD | Eastern | STATION RD | 2024-10-12 | 14:49 | 2024-10-12 | 16:51 | 0.0067023 | 5.5179e-05 | 20 | 2429 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: Fuses 1342 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 16:50 Cause: Wind Weather (wind/rain): Windy Follow up required (select advisory)? No | .
2199 |  | JE24037916 | COOK DRIVE | Eastern | COOK DRIVE | 2024-10-12 | 16:12 | 2024-10-12 | 16:25 | 0.017448 | 0.0012884 | 467 | 6324 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | REGULATORY INFORMATION Voltage & Device ID: Recloser 9519 Protection flags (nil where none): OC CAUSE: Line clash Location: Pole W12956 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: N/A Weather (wind/rain): Windy LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Part of NAPA 114732.Line sagged while under extra weight from Issuer Earths at Pole W12956. Soon after taking Issuer Earths off. Powr was restored at 16:10 . Recloser 9515 Autoreclosed at 16:11 then tripped to lock out at 16:13. On realising line clash, Field switcher opened the links Temp090 at 16:23. Power restored after checking with switcher Recloser was closed by NOC after checking with Field Switcher at 16:25 Access Permit was Issued to restrain sagging Centre phase. Power finally restored at 1652 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2200 |  | JE24037917 | WAVERLEY | Western | WAVERLEY | 2024-10-12 | 16:20 | 2024-10-12 | 22:17 | 0.11925 | 0.00033383 | 121 | 43224 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: REC 2680 Protection flags (nil where none): C Phase EF CAUSE: Line Down Location: Pole 771833 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Unable to isolate Fuses 1257, Fuses faulty Isolated at Links 2857 & ABS 873 Line repaired & Fuses 1257 also replaced SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2201 |  | JE24037927 | CLOTON RD NORTH | Western | CLOTON RD NORTH | 2024-10-12 | 19:41 | 2024-10-12 | 21:41 | 0.0019874 | 1.6554e-05 | 6 | 720 | Unplanned | WILDLIFE - BIRD | Fuses Location: 5482 No. Fuses: 2 Fuse Amp Size: 10 Amp TIME CLOSED: 21:41 Cause: Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? N | .
2202 |  | JE24037930 | 178 GILL STREET, STRANDON, NEW PLYMOUTH, 4312 | Western | CITY 3 | 2024-10-12 | 23:50 | 2024-10-13 | 4:31 | 0.054873 | 0.0012857 | 466 | 19889 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | On Arrival FM requested feed be de-energized CB 3 Opened Isolation installed at Sw/Gear 940/3, CB 3 Closed 23:59 Fire put out Transformer 2005N HV & LV Panels Damaged due to a fire Isolated at Fuse/Sw 297/4 Remainder of feeder restored 00:40 FM looking into what LV back feeds can be installed Then look into where a generator can be connected Generator in service 04:30 Voltage source on Emap (remove once repaired ) 16/10/24 - Generator removed under LV Napa 116421 TFR 2005N has been replaced, full power restored, Still a small amount of LV work to be completed | .
2203 |  | JE24034017 | MAUNGARANGI RD | Eastern | MAUNGARANGI RD | 2024-10-11 | 9:18 | 2024-10-11 | 16:50 | 0.049837 | 0.00011036 | 40 | 18064 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 230378 to 230382. 230382 to 339708: Install UG 11kV cable & remove OH 11kV line. 230378 to 339708: Install 11kV UG Cable, existing OH 230378 - 339708 to remain. Install new 33kV pole "New pole 1" between 339708 and 388766, transfer 33kV over to "New Pole 1" . Relocate 33kV LFI's from 339708 to "New Pole 1". Remove stay poles 481987 & 390891 | .
2204 |  | JE24034503 | 3 TITOKI PLACE MOUNT MAUNGANUI TAURANGA | Eastern | ARATAKI | 2024-10-11 | 9:30 | 2024-10-11 | 17:46 | 0.1436 | 0.00028969 | 105 | 52047 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install automation retrofit kit on 13156. | .
2205 |  | JE24034721 | 3 SEABREEZE PLACE PAPAMOA BEACH TAURANGA | Eastern | GLOUCESTER RD | 2024-10-11 | 8:31 | 2024-10-11 | 12:04 | 0.047556 | 0.00022348 | 81 | 17237 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9090/1/2/3 | .
2206 |  | JE24034725 | 143 HAKAKINO ROAD WAINUIORU MASTERTON | Western | WESTMERE GLADSTONE | 2024-10-11 | 9:16 | 2024-10-11 | 13:37 | 0.0086505 | 3.3108e-05 | 12 | 3135 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re sag 11kv lines at 2 sites past fuses 7037 | .
2207 |  | JE24034744 | 6 OPUKEKO ROAD PAEROA PAEROA | Eastern | RAILWAY ST | 2024-10-11 | 9:01 | 2024-10-11 | 14:45 | 0.055025 | 0.00016002 | 58 | 19944 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles N0349, N0336, N0348 & 400v pole N0336 | .
2208 |  | JE24035227 | WILLOUGHBY ST | Eastern | WILLOUGHBY ST | 2024-10-11 | 8:55 | 2024-10-11 | 17:13 | 0.13946 | 0.00083872 | 196 | 50546 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re-Level TC3719. Connect LV generator at main switch for Tamariki Station Daycare. | .
2209 |  | JE24035254 | 30 KAIMATIRA ROAD OKOIA WANGANUI | Western | NO 3 LINE | 2024-10-11 | 10:04 | 2024-10-11 | 11:35 | 0.0022761 | 2.4831e-05 | 9 | 825 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | install line break at pole 790701 GB1, 3 &27. Replace glass disc on ABS 039 pole 790705. Remove line break pole 790701 GB1, 3 & 25. | .
2210 |  | JE24037769 | TE KAPUA ROAD, MANGAWEKA, 4797 | Western | MANGAWEKA | 2024-10-11 | 10:41 | 2024-10-11 | 13:13 | 0.0096348 | 6.3456e-05 | 23 | 3492 | Unplanned | VEGETATION - OUTSIDE ZONE | Faultman found tree on lines after report from customer, line isolated at Fuses 2813 to remove tree at pole 812096. | .
2211 |  | JE24037781 | 606 MATAHIWI ROAD, MASTERTON, 5888 | Western | MOUNT BRUCE | 2024-10-11 | 12:36 | 2024-10-11 | 12:50 | 0.0013271 | 0.00010208 | 37 | 481 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Floating Conductor confirmed Isolated at Sw/Gear 11417/1 Binder replaced | .
2212 |  | JE24037850 | MANGAWEKA | Western | MANGAWEKA | 2024-10-11 | 19:46 | 2024-10-11 | 22:00 | 0.003703 | 2.759e-05 | 10 | 1342 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | 2 x blown Fuses at 2664, Line patrolled, twisted lines found past Pole 812119, due to wind Isolated at Fuses 2664 Lines untwisted with a hot stick, full power restored | .
2213 |  | JE24034323 | 2083 SKEET ROAD AUROA HAWERA | Western | AUROA | 2024-10-10 | 9:57 | 2024-10-10 | 15:43 | 0.021923 | 6.3456e-05 | 23 | 7946 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace Various x- arms in between poles 716779 - 716824 | .
2214 |  | JE24034483 | 696 STATE HIGHWAY 53 TAUHERENIKAU FEATHERSTON | Western | DAIRY FACTORY | 2024-10-10 | 9:02 | 2024-10-10 | 12:57 | 0.012999 | 5.5179e-05 | 20 | 4712 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Tx pole T478, replace pole 799843 and replace hardware at poles 848977 and 799855 | .
2215 |  | JE24034504 | BAINESSE | Western | BAINESSE | 2024-10-10 | 8:31 | 2024-10-10 | 14:31 | 0.033792 | 9.3805e-05 | 34 | 12248 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Change poles & crossarms P45229, P45232, P45235, P45236, P45233, P43236 | .
2216 |  | JE24034537 | 2 FLOWER STREET BULLS BULLS | Western | PAREWANUI | 2024-10-10 | 10:01 | 2024-10-10 | 14:41 | 0.1314 | 0.00046902 | 170 | 47628 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | AP for HV and LV arm replacement at poles 803607, 803609, 803784, 803788, 803792, 803795 | .
2217 |  | JE24034627 | HIKUAI | Eastern | HIKUAI | 2024-10-10 | 9:33 | 2024-10-10 | 15:15 | 0.037765 | 0.00011036 | 40 | 13688 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE 11KV XARMS AT U0685, U0688, 248606, 389207 AND REPLACE 11KV POLE U12697 | .
2218 |  | JE24034630 | 521 MAUNGARANGI ROAD PAENGAROA TE PUKE | Eastern | MAUNGARANGI RD | 2024-10-10 | 9:00 | 2024-10-10 | 14:37 | 0.050083 | 0.00014898 | 54 | 18153 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv overhead conductors between poles 221896 & 230055 with ACSR Ferret | .
2219 |  | JE24034631 | 26 KESTREL AVENUE WELCOME BAY TAURANGA | Eastern | VICTORY STREET | 2024-10-10 | 9:46 | 2024-10-10 | 13:12 | 0.039894 | 0.00019313 | 70 | 14460 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9128/3/2/1 | .
2220 |  | JE24034632 | 28 HEREFORD ROAD OROPI TAURANGA | Eastern | WAIMAPU | 2024-10-10 | 9:05 | 2024-10-10 | 16:22 | 0.04216 | 9.6564e-05 | 35 | 15281 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 211205 (TE4-12) to 211218 | .
2221 |  | JE24034692 | 713 PLYMOUTH ROAD KORU NEW PLYMOUTH | Western | PIONEER RD | 2024-10-10 | 10:16 | 2024-10-10 | 12:27 | 0.032077 | 0.00024555 | 89 | 11626 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Relocate the existing HV fuses 6465 onto the front take off arm up pole 755278 for easier access during switching. | .
2222 |  | JE24034728 | KATERE 8 | Western | KATERE 8 | 2024-10-10 | 8:46 | 2024-10-10 | 15:28 | 0.23527 | 0.00059042 | 214 | 85275 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | ELE020712 ECP34 Tx Program FY24 Replacement of Transformer 424 with a 500kVA Ground Mounted Transformer 14 Kauri Street, New Plymouth | .
2223 |  | JE24035142 | 895 TAIRUA WHITIANGA ROAD WHENUAKITE WHITIANGA | Eastern | TAIRUA NORTH | 2024-10-10 | 9:17 | 2024-10-10 | 15:40 | 0.053903 | 0.00014071 | 51 | 19537 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Helicopter stringing fibre between poles W1920 & W1901 | .
2224 |  | JE24035179 | 570 WAITARA ROAD HUIRANGI NEW PLYMOUTH | Western | LEPPERTON | 2024-10-10 | 9:45 | 2024-10-10 | 15:41 | 0.025555 | 7.1733e-05 | 26 | 9263 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To Replace Twisted pole HV 742486 | .
2225 |  | JE24035218 | 1 SANTA MONICA DRIVE PAPAMOA BEACH TAURANGA | Eastern | GRAVATT RD | 2024-10-10 | 10:10 | 2024-10-10 | 15:09 | 0.081586 | 0.00027314 | 99 | 29571 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Disconnect cable between S4570 & S4568 Test cable for this circuit Swing cable at S4568 and terminate to 14908/4 Transfer all LV circuits from T4519 to TP4463 Pre-commission cable and liven, phasing check across 14908/4 and phase rotation at TP4463 Remove old RMU & T4519 | .
2226 |  | JE24036450 | 1208 WHANGAEHU VALLEY ROAD WHANGAEHU VALLEY MASTERTON | Western | BIDEFORD | 2024-10-10 | 9:15 | 2024-10-10 | 15:29 | 0.022692 | 6.0697e-05 | 22 | 8225 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Isolation for Vegetation cutting between poles 372135 and 836962 | .
2227 |  | JE24037560 | CARDIFF RD | Western | CARDIFF RD | 2024-10-10 | 6:32 | 2024-10-10 | 7:41 | 0.00038122 | 5.5179e-06 | 2 | 138 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses 5661 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 07:40 Cause: Bird Strike Weather (wind/rain): Rain Follow up required (select advisory)? No | .
2228 |  | JE24037655 | CR MATAHIWI ROAD and TE HAU MASTERTON, 5888 | Western | EDITH ST | 2024-10-10 | 14:16 | 2024-10-10 | 15:05 | 0.0022779 | 4.6902e-05 | 17 | 826 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Floating Conductors at Pole 836329 Isolated at Fuses 7705 Binders replaced Power restored 15:04 | .
2229 |  | JE24037664 | CROFTON | Western | CROFTON | 2024-10-10 | 18:38 | 2024-10-10 | 19:43 | 0.0090967 | 0.00014071 | 51 | 3297 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Old rotten cross arm, pin had fallen over causing tracking and Burning of the cross arm at Pole 806064 Isolated at ABS 962 Cross arm and hardware replaced, full power restored | .
2230 |  | JE24037671 | TAIRUA NORTH | Eastern | TAIRUA NORTH | 2024-10-10 | 15:45 | 2024-10-10 | 18:22 | 0.0060648 | 3.8625e-05 | 14 | 2198 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | ETA 60min - Police comms advised Firecomms now attending, have also advised them the ETA Line down at transformer TP692 Joint failure Isolated at Switch gear 13389-1 No Back feed | .
2231 |  | JE24037677 | WAITOTARA | Western | WAITOTARA | 2024-10-10 | 14:45 | 2024-10-10 | 15:48 | 0.00034699 | 5.5179e-06 | 2 | 126 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 032 No. Fuses: 3 Fuse Amp Size: 5 Amp TIME CLOSED: 15:48 Cause: Unknown Weather (wind/rain): Unknown Not sure when they blew Follow up required (select advisory)? N | .
2232 |  | JE24034365 | 305 WAWIRI ROAD TOKO STRATFORD | Western | HUIROA | 2024-10-09 | 8:50 | 2024-10-09 | 15:45 | 0.022898 | 5.5179e-05 | 20 | 8299 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 759398, 759397, 759390, 759394. Replace hv pin arms at pole 759393, 759392 Remove redundant lv arms and conductor from poles 759393, 753392, 759391. Remove stud pole 759390 | .
2233 |  | JE24034442 | PURANGI | Eastern | PURANGI | 2024-10-09 | 10:16 | 2024-10-09 | 12:22 | 0.0090575 | 7.1733e-05 | 26 | 3283 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | For Franklin Trees to cut between poles W13705 & W13799 | .
2234 |  | JE24034443 | WERAITI | Western | WERAITI | 2024-10-09 | 9:19 | 2024-10-09 | 14:50 | 0.095223 | 0.00028693 | 104 | 34514 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Isolation for vegetation cutting at poles 827475-827478,827498-827499,377237-827603,376506-827598,827621-848547 | .
2235 |  | JE24034445 | 52 WAIKITE ROAD WELCOME BAY TAURANGA | Eastern | KAITEMAKO RD | 2024-10-09 | 10:01 | 2024-10-09 | 13:45 | 0.03905 | 0.00017381 | 63 | 14154 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - S5758/S5756/S5754 | .
2236 |  | JE24034452 | 117 MCKINLEY ROAD TE AROHA WEST TE AROHA | Eastern | MAUNGAKAWA ROAD | 2024-10-09 | 10:30 | 2024-10-09 | 15:45 | 0.01478 | 4.6902e-05 | 17 | 5357 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace Poles C419, C478 and arms on Pole C418, C13256, C484 on McKinley Rd Defects | .
2237 |  | JE24034459 | 5 BLACK ROAD PAENGAROA TE PUKE | Eastern | OLD COACH RD | 2024-10-09 | 8:46 | 2024-10-09 | 14:13 | 0.056839 | 0.00017381 | 63 | 20602 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace HV conductor with 3W Squirrel between poles 221659 & 221690. | .
2238 |  | JE24034465 | 280 BATTERSEA ROAD MORRISONS BUSH GREYTOWN | Western | MOROA | 2024-10-09 | 9:01 | 2024-10-09 | 14:16 | 0.066154 | 0.00020968 | 76 | 23978 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles and hardware between S502 and S596 | .
2239 |  | JE24034467 | MOTUMAOHO | Eastern | MOTUMAOHO | 2024-10-09 | 9:01 | 2024-10-09 | 15:02 | 0.022936 | 6.3456e-05 | 23 | 8313 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Poles I0760,I0761, I13094, I0763, I13096, I0764. Replace arms on 390023. Replace 400v Road crossing. | .
2240 |  | JE24037391 | BELVEDERE | Western | BELVEDERE | 2024-10-09 | 3:57 | 2024-10-09 | 6:59 | 0.025614 | 0.00014071 | 51 | 9284 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: 7570 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 06:59 Cause: Line clash Weather (wind/rain): windy Follow up required (select advisory)?n Line patrolled | .
2241 |  | JE24037398 | DYERVILLE | Western | DYERVILLE | 2024-10-09 | 6:00 | 2024-10-09 | 7:50 | 0.0042705 | 3.8625e-05 | 14 | 1548 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: 7395 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 07:50 Cause: Wind, possible wind blow debris or line clash Weather (wind/rain): Windy Follow up required (select advisory)?n Line patrolled | .
2242 |  | JE24037441 | RANGITANUKU RD | Eastern | RANGITANUKU RD | 2024-10-09 | 9:10 | 2024-10-09 | 10:45 | 0.022896 | 0.0012802 | 464 | 8299 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: CB1 Protection flags (nil where none): HLT, Ground Fault, Phase C Fault CAUSE: Unknown, but one fuse blown at Transformer TC5479 Location: Pole E12825 Temp generation (state details when used): No Suspect could be bird into the lines. Reloaded relivened 1 x3A Fuses at Transformer TC5479 at 10:45 PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): Yes, LFIs worked well reduced restoration time Follow up Required (select advisory)? No Additional fault restoration comments: CB 1 had HLT Enabled under CAC NAPA 115896-01. Stood down CAC, Closed CB1 and resumed work on CAC. LFII lit at ABS 1083 Pole E12826.Time to restore took a few minutes longer due to standing down CAC crew on 115586-01 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): N/A Circuit that tripped: N/A DTF (KM):N/A | .
2243 |  | JE24037487 | 161 CORBETT ROAD, BELL BLOCK, NEW PLYMOUTH, 4312 | Western | WAITARA RD | 2024-10-09 | 17:03 | 2024-10-09 | 18:36 | 0.00051777 | 5.5179e-06 | 2 | 188 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Cause: Faulty Main Switch at Industrial Customer Tag no: N/A Customer advised? N/A Disco safety register + emailed retailer: N/A Is 2R required? Y Additional Info: FM had to Isolate HV at Fuses 8162 & Issue Assurance for customers electrician to replace LV main switch. FM waited onsite & re connected property at completion of works. | .
2244 |  | JE24037550 | CHURCH ST | Western | CHURCH ST | 2024-10-09 | 17:58 | 2024-10-09 | 19:23 | 0.033343 | 0.00053524 | 194 | 12085 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec C279/2 Protection flags (nil where none): E/F CAUSE: Unknown Location: Unknown Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: op Weather (wind/rain): Strong winds LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Network has been patrolled and re-livened one section at a time. Field staff suspect strong winds caused the initial trip, since then the wind has calmed down. Full Power restored at 19:23 | .
2245 |  | JE24032163 | 848 PYES PA ROAD PYES PA TAURANGA | Eastern | PYES PA | 2024-10-08 | 9:31 | 2024-10-08 | 14:39 | 0.0033981 | 1.1036e-05 | 4 | 1232 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace leaking 30-11-3 transformer (no oil in sight glass) at kiosk TE4-109. Clean out kiosk and cables, cover holes in kiosk. | .
2246 |  | JE24034225 | 3 FAIRVIEW TERRACE PAEROA PAEROA | Eastern | SHAW AVE | 2024-10-08 | 9:15 | 2024-10-08 | 16:01 | 0.074879 | 0.00018485 | 67 | 27140 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE 11KV POLE N12503 AND INSTALL NEW 100KVA TRANSFORMER. ALSO REPLACE LV POLE'S N1181 & N1182 | .
2247 |  | JE24034231 | 1415 MOKAU ROAD URUTI URENUI | Western | MAIN RD MOTONUI | 2024-10-08 | 10:00 | 2024-10-08 | 14:35 | 0.09691 | 0.00035315 | 128 | 35125 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Vegetation removal in between poles 762882 - 762886 | .
2248 |  | JE24034234 | MANGATAINOKA | Western | MANGATAINOKA | 2024-10-08 | 9:30 | 2024-10-08 | 13:12 | 0.039855 | 0.00017933 | 65 | 14446 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace 11kv cross arms at pole P16644,P16651,P44738,P44737 and resag at P16654 | .
2249 |  | JE24034288 | 202 KAIKAHU ROAD KEREPEHI PAEROA | Eastern | AWAITI | 2024-10-08 | 10:04 | 2024-10-08 | 12:36 | 0.0016767 | 1.1036e-05 | 4 | 608 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE 11KV XARM AT POLE O1754 | .
2250 |  | JE24034316 | 2083 SKEET ROAD AUROA HAWERA | Western | AUROA | 2024-10-08 | 9:35 | 2024-10-08 | 15:04 | 0.02087 | 6.3456e-05 | 23 | 7564 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace Various x- arms in between poles 716779 - 716824 | .
2251 |  | JE24034320 | 635 STATE HIGHWAY 1 MARTON MARTON | Western | CROFTON | 2024-10-08 | 9:36 | 2024-10-08 | 13:59 | 0.037626 | 0.00014347 | 52 | 13638 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install Links 16117/6 on Entec Switch & replace defected poles & X-Arms between 806138, 806132 & 806130 replace ABS 492 | .
2252 |  | JE24034339 | 20 TE ARANGA DRIVE PAPAMOA BEACH TAURANGA | Eastern | GRENADA ST | 2024-10-08 | 9:46 | 2024-10-08 | 14:19 | 0.051277 | 0.00018761 | 68 | 18586 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9361/1/2/3/4/5 | .
2253 |  | JE24034349 | CORNWALL ST | Western | CORNWALL ST | 2024-10-08 | 8:45 | 2024-10-08 | 13:27 | 0.090246 | 0.00032004 | 116 | 32710 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Worksite - replace/repair poles and hardware in isolated area including pole 822905. | .
2254 |  | JE24034357 | 436 MAUNGARANGI ROAD PAENGAROA TE PUKE | Eastern | MAUNGARANGI RD | 2024-10-08 | 8:50 | 2024-10-08 | 14:53 | 0.054126 | 0.00014898 | 54 | 19618 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv overhead conductors between poles 221896 & 221860 with ACSR Ferret | .
2255 |  | JE24034368 | 888 OROPI ROAD OROPI TAURANGA | Eastern | WAIMAPU | 2024-10-08 | 9:02 | 2024-10-08 | 15:22 | 0.0041877 | 1.1036e-05 | 4 | 1518 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 211136 to 211141 (TE4-107) | .
2256 |  | JE24034441 | 338 WESTERN LAKE ROAD WESTERN LAKE FEATHERSTON | Western | REVANS ST | 2024-10-08 | 9:00 | 2024-10-08 | 15:50 | 0.070062 | 0.00017933 | 65 | 25394 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Change 11kv arms between 798603 & 798539 Western Lake Rd | .
2257 |  | JE24034447 | 258 CORONATION AVENUE WELBOURN NEW PLYMOUTH | Western | BROOKLANDS 10 | 2024-10-08 | 8:46 | 2024-10-08 | 16:31 | 0.092433 | 0.00019865 | 72 | 33503 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | ELE020712 ECP34 Tx Program FY24 Replacement of Transformer 1193 with a 500kVA Ground Mounted Transformer | .
2258 |  | JE24034646 | ASHHURST | Western | ASHHURST | 2024-10-08 | 8:45 | 2024-10-08 | 14:11 | 0.080799 | 0.00024831 | 90 | 29286 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Poles, Xarms and LV conductor between and including P41776 to P41771. Replace ABS E68 on pole P41776 (number to remain) | .
2259 |  | JE24037239 | MAHOE | Western | MAHOE | 2024-10-08 | 5:30 | 2024-10-08 | 8:50 | 0.041123 | 0.0010539 | 294 | 14905 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: CB Q21 Protection flags (nil where none): EF CAUSE: lines down due to age Location: Pole 730825 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: cursory Weather (wind/rain): fine LFI (Y/N + Comments): LFI's at ABS 5878 indicating correctly Follow up Required (select advisory)? Additional fault restoration comments: LINES REPAIRED. Also replaced 2x40A Fuses at Fuses 6330 due to same fault | .
2260 |  | JE24037241 | LEEDSTOWN 22KV | Western | LEEDSTOWN 22KV | 2024-10-08 | 6:27 | 2024-10-08 | 8:03 | 0.0018552 | 1.9313e-05 | 7 | 672 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses 875 No. Fuses: 2 Fuse Amp Size: 8A TIME CLOSED: 08:03 Cause: Bird strike Weather (wind/rain): Calm Follow up required (select advisory)? No | .
2261 |  | JE24037269 | ROBERTS LINE | Western | ROBERTS LINE | 2024-10-08 | 8:45 | 2024-10-08 | 14:10 | 0.00089703 | 2.759e-06 | 1 | 325 | Planned | OTHER | PART OF HV NAPPA113374 - JE24037259- CONFIRMED THAT ADRESS HAS BEEN ADVERTISED | .
2262 |  | JE24037315 | NO 3 LINE | Western | NO 3 LINE | 2024-10-08 | 12:28 | 2024-10-08 | 16:23 | 0.020531 | 0.00014898 | 53 | 7441 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 177/2 Protection flags (nil where none): E/F, O/C A & B CAUSE: Tree through lines Location: 840997 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: op Weather (wind/rain): windy LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Customer had there LV service line isolated Tag-A46518, Customer was cutting the tree down and the wind has blown the tree into the HV line, multiple lines down past Pole 840997, faultman have repaired the lines and restored power, tag removed customers power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2263 |  | JE24037356 | MIRO ST | Western | MIRO ST | 2024-10-08 | 16:35 | 2024-10-08 | 17:41 | 0.0023618 | 3.5867e-05 | 13 | 856 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Twisted cross arm due to missing nut off king bolt, wind has caused cross arm to vibrate and king bolt has come out of the pole 449865 Isolated at Fused ABS 11097 Cross arm straightened, king bolt re-installed and double nutted, full power restored | .
2264 |  | JE24037365 | GULLIVER RD | Eastern | GULLIVER RD | 2024-10-08 | 16:25 | 2024-10-08 | 17:50 | 0.00070695 | 8.2769e-06 | 3 | 256 | Unplanned | WILDLIFE - BIRD | Fuses Location: FP894 No. Fuses: 2 Fuse Amp Size: 6 Amp TIME CLOSED: 17:50 Cause: Bird Strike Weather (wind/rain): Overcast. Follow up required (select advisory)? Yes Note: Owner stated that this has happened several times already. Investigate if bird diverters need to be installed in this area. Farmer's Power gets affected in the morning and then is unable to milk the cows. | .
2265 |  | JE24037382 | DUTHIE RD | Western | DUTHIE RD | 2024-10-08 | 18:56 | 2024-10-08 | 20:16 | 0.00021907 | 2.759e-06 | 1 | 79 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: 8725 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 20:15 hrs Cause: Unk suspect bird Weather (wind/rain): Light Rain / Windy Follow up required (select advisory)? | .
2266 |  | JE24037386 | ASHWORTH ST | Eastern | ASHWORTH ST | 2024-10-08 | 20:34 | 2024-10-08 | 22:11 | 0.0002678 | 2.759e-06 | 1 | 97 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses FP986 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 22:10 Cause: unknown Weather (wind/rain): calm Follow up required (select advisory)? This job at the parent of this job | .
2267 |  | JE24033605 | 304 NO 1 LINE TAUHERENIKAU FEATHERSTON | Western | DAIRY FACTORY | 2024-10-07 | 9:00 | 2024-10-07 | 12:56 | 0.0019488 | 8.2769e-06 | 3 | 706 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace T1914 | .
2268 |  | JE24034023 | TUTAENUI | Western | TUTAENUI | 2024-10-07 | 9:30 | 2024-10-07 | 12:45 | 0.0021524 | 1.1036e-05 | 4 | 780 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace multiple 11KV Defects past 11KV Fuses 865 | .
2269 |  | JE24034059 | 525A RUAKIWI ROAD KOURARAU HILL MASTERTON | Western | WESTMERE GLADSTONE | 2024-10-07 | 9:30 | 2024-10-07 | 12:56 | 0.0068091 | 3.3108e-05 | 12 | 2468 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv xarms and re sag 11kv lines past fuses 7841 | .
2270 |  | JE24034129 | 335 FERRY ROAD KEREPEHI PAEROA | Eastern | AWAITI | 2024-10-07 | 9:46 | 2024-10-07 | 13:26 | 0.025367 | 0.00012139 | 44 | 9194 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | INSTALL TEMPORARY POLE BETWEEN POLES O125 & O124 AND DIVERT 11KV O/H LINES, FOR CONSTRUCTION OF REGULATOR SITE. | .
2271 |  | JE24034224 | 2200 STATE HIGHWAY 26 MOTUMAOHO MORRINSVILLE | Eastern | MOTUMAOHO | 2024-10-07 | 9:03 | 2024-10-07 | 15:30 | 0.075753 | 0.00019589 | 71 | 27457 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Poles I0698. I0755, I0756, 857093, 857094, I0759. Replace 11kv conductor from I0698 to I0759. | .
2272 |  | JE24034311 | 34 CAMERON ROAD EAST WESTMERE WANGANUI | Western | WESTMERE PEAT ST | 2024-10-07 | 9:01 | 2024-10-07 | 15:05 | 0.065163 | 0.00017933 | 65 | 23619 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Isolation for vegetation cutting, hedge trimming between poles 769446 and 769438 | .
2273 |  | JE24036441 | WAIPUNA | Eastern | WAIPUNA | 2024-10-07 | 23:00 | 2024-10-08 | 5:27 | 0.058256 | 0.0001545 | 56 | 21115 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | O/H to U/G of HV and LV network from Poles 395510 to 481053. Install new 11kV switchgear CFC 14964, CFCF 14979 & CFCF 14977 & new G/M TX TP4459. Install new 11kV U/G cable & remove existing O/H lines between Poles 395510 to 481053. Transfer existing TXs to new switchgear & remove P/M TX TD3-028. | .
2274 |  | JE24037076 | RANGIKURA | Western | RANGIKURA | 2024-10-07 | 6:50 | 2024-10-07 | 8:51 | 0.0033328 | 2.759e-05 | 10 | 1208 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 999 No. Fuses: 2 Fuse Amp Size: 25A TIME CLOSED: 08:50 Cause: Unknown Weather (wind/rain): Rain Follow up required (select advisory)? No | .
2275 |  | JE24037133 | OVERDALE RD | Eastern | OVERDALE RD | 2024-10-07 | 10:43 | 2024-10-07 | 12:20 | 0.0026607 | 2.759e-05 | 10 | 964 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: Fuses FP1405 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 12:19 Cause: Weather, wind Weather (wind/rain): windy Follow up required (select advisory)? No | .
2276 |  | JE24037154 | TAWHITI RD | Western | TAWHITI RD | 2024-10-07 | 12:05 | 2024-10-07 | 13:37 | 0.0012762 | 1.3795e-05 | 5 | 463 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses CA465 No. Fuses: 2 Fuse Amp Size: 8A TIME CLOSED: 13:37 Cause: Unknown Weather (wind/rain): Rain Follow up required (select advisory)? No | .
2277 |  | JE24037155 | IRIRANGI | Western | IRIRANGI | 2024-10-07 | 12:08 | 2024-10-08 | 15:35 | 0.10645 | 0.00059594 | 188 | 38582 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 142 Protection flags (nil where none): A,B,C Fault CAUSE: Tree through the lines Location: Pole 358175 Temp generation (state details when used): Yes PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Rain & Strong wind LFI (Y/N + Comments): Nil Follow up Required (select advisory)? Additional fault restoration comments: Multiple spans of conductor down. Temp line breaks made at poles 358174 and 376133 , power restored except 5 transformers on generators(non network) Generations supplied to transformers left off over night. Line crews are coming back in the morning to straighten poles & pull up conductor. Generators supplied to customers not network connected. Line repaired power restored 16:01. Break before switching at Sectionaliser 4621 and Recloser 142, (only 19 seconds) | .
2278 |  | JE24037185 | MATAKANA RD | Eastern | MATAKANA RD | 2024-10-07 | 14:43 | 2024-10-08 | 12:11 | 0.0071071 | 5.5179e-06 | 2 | 2576 | Unplanned | WILDLIFE - POSSUM | Fuses Location: Transformer TC3-185 Fuses No. Fuses: 3 Fuse Amp Size: 3 A TIME CLOSED: 12:10 Cause: Possum Weather (wind/rain): Overcast Follow up required (select advisory)? No No more barges today, job will be attended tomorrow morning (8/10). SMC will advise customer. x3 Barrels Replaced and Vegetation Creeper removed from Pole | .
2279 |  | JE24037210 | TAWAHA | Western | TAWAHA | 2024-10-07 | 16:25 | 2024-10-07 | 16:35 | 0.00021851 | 2.2072e-05 | 8 | 79 | Unplanned | ADVERSE WEATHER - WIND-BLOWN DEBRIS (NOT TREES) | REGULATORY INFORMATION Cause: Weather balloon on HV lines Location: T2420 Isolation: S599 Weather (wind/rain): Windy Follow up Required (select advisory)? Additional fault restoration comments: Balloon removed from lines using Hot Stick | .
2280 |  | JE24034515 | 75 LONDON STREET ELTHAM ELTHAM | Western | MANGATOKI | 2024-10-06 | 8:05 | 2024-10-06 | 16:10 | 0.0013388 | 2.759e-06 | 1 | 485 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Complete remaining maintenance at asset 4963 | .
2281 |  | JE24037064 | STONEY CREEK | Western | STONEY CREEK | 2024-10-06 | 19:02 | 2024-10-07 | 0:54 | 0.072215 | 0.00095184 | 281 | 26175 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: CB 11, Z140 Protection flags (nil where none): C phase EF CAUSE: Cable at Pole 858947 has burnt from the crutch to the ground Location: Pole 858947 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): 2410004 Circuit patrolled and type: N Weather (wind/rain): fine LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Secondary fault with a blown jumper at Pole P41711 discovered after power restored. Isolated new fault area to repair. | .
2282 |  | JE24036066 | KATERE 7 | Western | KATERE 7 | 2024-10-05 | 8:09 | 2024-10-05 | 11:13 | 0.00050825 | 2.759e-06 | 1 | 184 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 10 Yearly 11kV metering unit calibration | .
2283 |  | JE24036948 | CLOTON RD NORTH | Western | CLOTON RD NORTH | 2024-10-05 | 1:35 | 2024-10-05 | 6:58 | 0.21049 | 0.0036667 | 927 | 76292 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 5 Protection flags (nil where none): A, B Ph O/C CAUSE: 2 x line down due to age Location: Pole 741366 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: cursory Weather (wind/rain): Calm LFI (Y/N + Comments): Y at Sw/Gear 12507 Follow up Required (select advisory)? Additional fault restoration comments: Unable to Open Recloser 12155 due to comms failure on loss of power (Battery failure JE24034166 in system for replacement of) Feeder sectionalised from Sub Recloser 12155 was found to be open when checked No coms to LFI's at pole 741404, when checked these were not active. Back feed install up to ABS 5477 via Sectionaliser 12593 Lines down found at pole 741366, Isolated at ABS's 5620 & 12155/1 and Links 12155/6. Back feed installed via Sectionaliser 12591 | .
2284 |  | JE24036949 | AUROA | Western | AUROA | 2024-10-05 | 5:40 | 2024-10-05 | 8:57 | 0.022265 | 0.00011312 | 41 | 8070 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2 x lines down at Pole 717763 due to age | .
2285 |  | JE24036951 | TAWA ST | Eastern | TAWA ST | 2024-10-05 | 8:17 | 2024-10-05 | 12:56 | 0.068178 | 0.00083321 | 134 | 24711 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Fuses Location: Fuse Switch 9945/2 No. Fuses: 3 Fuse Amp Size: 31.5A TIME CLOSED: 08:40 Cause: lv Fault at meter board at Number 98 Maunganui Rd. Weather (wind/rain): Calm Follow up required (select advisory)? No On re energising the fuses blew again and created another job JE24036956. Tested HV cables and all passed, hoever Isolated LV CIRCUITS WHICH WERE FAULTY. Replaced Fuses into 9945/2 with 3X40A as there were no more 31.5 Amps Still voltages issues at TC4-258. Cable disconnected at TC4-199/L2 and TC4-258, DNO2410003 Generator connected at 12:56 05/10/24 TC4-258 | .
2286 |  | JE24036961 | CROFTON | Western | CROFTON | 2024-10-05 | 9:20 | 2024-10-05 | 10:30 | 0.00057911 | 8.2769e-06 | 3 | 210 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses 970 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 10:30 Cause: Duck in the lines Weather (wind/rain): calm Follow up required (select advisory)? | .
2287 |  | JE24036979 | RANGIKURA | Western | RANGIKURA | 2024-10-05 | 9:48 | 2024-10-05 | 12:07 | 0.0038234 | 2.759e-05 | 10 | 1386 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 999 No. Fuses: 2 Fuse Amp Size: 25A TIME CLOSED: 1206 Cause: Unknown Weather (wind/rain): Windy Follow up required (select advisory)? | .
2288 |  | JE24036987 | TAWHITI RD | Western | TAWHITI RD | 2024-10-05 | 9:28 | 2024-10-05 | 12:28 | 0.0019815 | 1.1036e-05 | 4 | 718 | Unplanned | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses CA432 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 1227 Cause: Unknown Weather (wind/rain): Follow up required (select advisory)? | .
2289 |  | JE24037009 | HAURAKI RD | Eastern | HAURAKI RD | 2024-10-05 | 18:01 | 2024-10-05 | 22:05 | 0.0096047 | 0.00010208 | 37 | 3481 | Unplanned | WILDLIFE - BIRD | Fuses Location: FC802 No. Fuses: 2 Fuse Amp Size: 20 TIME CLOSED: 19:30 Cause: Duck Strike Weather (wind/rain): Light wind & Rain Follow up required (select advisory)? | .
2290 |  | JE24037011 | WAINGAWA RD | Western | WAINGAWA RD | 2024-10-05 | 18:41 | 2024-10-05 | 19:25 | 0.00072423 | 1.6554e-05 | 6 | 263 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Low lines at Pole 855031 at 4.3m, Squirrel Wires restrained to 5.6M | .
2291 |  | JE24037019 | TE MATAI RD | Eastern | TE MATAI RD | 2024-10-05 | 20:03 | 2024-10-05 | 22:03 | 0.00098965 | 8.2769e-06 | 3 | 359 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: SE5-154 & IP494 total 4 x Fuses No. Fuses: 4 Fuse Amp Size: 2 x 10A & 2 x 6A TIME CLOSED: 22:02 Cause: Lightning Weather (wind/rain): Follow up required (select advisory)? | .
2292 |  | JE24037021 | LONGBUSH | Western | LONGBUSH | 2024-10-05 | 22:01 | 2024-10-06 | 2:51 | 0.0087986 | 3.0349e-05 | 11 | 3189 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV DTX T3935 Protection flags (nil where none): None CAUSE: Car V Ground Mounted Transformer T3935 Location: off FABS 7964 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Wind , Rain LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Unknown Car Hit Ground Mounted Transformer T3935, Breaking 3 x HV Bushings, 3 Phase 30kVA Transformer replaced with 3 Phase 50kVA non fused relying now on FABS 7964! SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2293 |  | JE24037023 | BREAKWATER RD | Western | BREAKWATER RD | 2024-10-05 | 23:42 | 2024-10-06 | 7:49 | 0.4287 | 0.00088011 | 319 | 155385 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Car V Pole Isolated at ABS's 255, 158 & Sw/Gear 6677/3 400 V fuses at transformer 2496N, also Isolated due to LV running through work area. Replaced Pole & all hardware. NDR to follow | .
2294 |  | JE24033602 | 6 NORFOLK ROAD LOWER NORFOLK INGLEWOOD | Western | MOUNTAIN RD | 2024-10-04 | 9:41 | 2024-10-04 | 12:18 | 0.035929 | 0.00022899 | 83 | 13023 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Isolation of ABS 5413 To Cut and remove earths away from the stays | .
2295 |  | JE24033630 | DAIRY FACTORY | Western | DAIRY FACTORY | 2024-10-04 | 9:16 | 2024-10-04 | 12:09 | 0.00047739 | 2.759e-06 | 1 | 173 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 799813 and 799814 | .
2296 |  | JE24033960 | 651A STATE HIGHWAY 53 TAUHERENIKAU FEATHERSTON | Western | DAIRY FACTORY | 2024-10-04 | 9:01 | 2024-10-04 | 12:41 | 0.0018204 | 8.2769e-06 | 3 | 660 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace transformer cross arm at T2669 | .
2297 |  | JE24033966 | 129-302 IRONWORKS ROAD, HUNTERVILLE | Western | HUNTERVILLE 22KV | 2024-10-04 | 9:06 | 2024-10-04 | 11:31 | 0.00085675 | 2.759e-05 | 10 | 311 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Straighten TX arm X395 on pole 807640. Install arm brace on TX arm 1414 on pole 807672 | .
2298 |  | JE24033967 | 29 RIVERBANK ROAD OKOIA WANGANUI | Western | KIWI ST | 2024-10-04 | 8:45 | 2024-10-04 | 15:02 | 0.063456 | 0.0001683 | 61 | 23000 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Isolation for Vegetation cutting between poles 790669 and 482240 | .
2299 |  | JE24034159 | 30 TOTARA STREET TAWHERO WANGANUI | Western | SPRINGVALE | 2024-10-04 | 9:45 | 2024-10-04 | 13:51 | 0.050119 | 0.00020416 | 74 | 18166 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV Pole 458473 that has been hit by a car. | .
2300 |  | JE24034173 | GLOVER RD EAST | Western | GLOVER RD EAST | 2024-10-04 | 9:30 | 2024-10-04 | 15:56 | 0.040465 | 0.00010484 | 38 | 14667 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | DNO 2408001, pole 846555. HV cable term completely blow off jumpers after fault. Replace HV double term arm with pin arm to eliminate all connections. Remove HV cable to re-terminate onto crucifix and re-install. Lower L2 LV crossarm to create clearances for new crucifix. Remove L3 LV crossarm. | .
2301 |  | JE24034222 | 50 PUKETUI VALLEY ROAD | Eastern | HIKUAI | 2024-10-04 | 9:20 | 2024-10-04 | 16:58 | 0.087205 | 0.00019037 | 69 | 31608 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv pole's U0676, U12690. Replace 11kv Xarms U0677, U12692, U12695. Install temp links TEMP036 at pole 387449 | .
2302 |  | JE24035380 | 8 RANGIHAU ROAD COROGLEN WHITIANGA | Eastern | COROGLEN | 2024-10-04 | 8:45 | 2024-10-04 | 11:16 | 0.028338 | 0.00018761 | 68 | 10271 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To rebind conductor at pole W1755 - R2 works. To remove TEMP93 - FFT works. | .
2303 |  | JE24035500 | 194 MILLRICKS LINE LINTON | Western | LINTON | 2024-10-04 | 9:01 | 2024-10-04 | 10:52 | 0.00030408 | 2.759e-06 | 1 | 110 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace TX T2/709 | .
2304 |  | JE24036547 | 310 UPPER PLAIN ROAD UPPER PLAIN MASTERTON | Western | MOUNT BRUCE | 2024-10-04 | 10:05 | 2024-10-04 | 11:44 | 0.00082134 | 8.2769e-06 | 3 | 298 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace damaged 11kv arm at pole 836276 | .
2305 |  | JE24036832 | MAIN RD MOTONUI | Western | MAIN RD MOTONUI | 2024-10-04 | 8:10 | 2024-10-04 | 10:52 | 0.0017962 | 1.1036e-05 | 4 | 651 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 4872T No. Fuses: 2 Fuse Amp Size:2A TIME CLOSED: 10:52 Cause: Lighting from a few weeks ago Weather (wind/rain): Calm Follow up required (select advisory)?N ****No 2R***** | .
2306 |  | JE24036866 | HUKANUI | Western | HUKANUI | 2024-10-04 | 9:37 | 2024-10-04 | 12:00 | 0.0039617 | 2.759e-05 | 10 | 1436 | Unplanned | WILDLIFE - BIRD | Fuses Location: S3 No. Fuses: 2 Fuse Amp Size: 6amp TIME CLOSED: 12:00 Cause: Bird Strike at Transformer T8/186 Weather (wind/rain): Fine Follow up required (select advisory)? No Fuses Location: T8/186 No. Fuses: 2 Fuse Amp Size: 2amp TIME CLOSED: 11:30 Cause: Bird Strike at Transformer T8/186 Weather (wind/rain): Fine Follow up required (select advisory)? No | .
2307 |  | JE24036872 | KUAOTUNU | Eastern | KUAOTUNU | 2024-10-04 | 9:58 | 2024-10-04 | 12:17 | 0.08704 | 0.0018264 | 662 | 31548 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 9226 Opened, Sec 9632 Never Opened, But Protection saw the fault. Protection flags (nil where none): A Phase E/F & O/C CAUSE: Digger Boom struck & Clashed wires @ Pole W1200 Location: Pole W1200 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Curse Weather (wind/rain): Fine LFI (Y/N + Comments): LFI @ Pole 13821 Operated Follow up Required (select advisory)? Additional fault restoration comments: 2nd time the Contractor has been involved in hitting lines, Did this yesterday breaking wires at the same pole W1200 site. Logging Contractor was working under CAC 78374. CAC 78374 immediately Cancelled & Logging Contractors stood down. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2308 |  | JE24036873 | pole_363035 | Western | MOUNT BRUCE | 2024-10-04 | 11:54 | 2024-10-04 | 12:38 | 0.004627 | 0.00010484 | 38 | 1677 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Outage to resecure king bolt at Pole 363035. | .
2309 |  | JE24036887 | KETEMARAE RD | Western | KETEMARAE RD | 2024-10-04 | 9:30 | 2024-10-04 | 15:56 | 0.0010642 | 2.759e-06 | 1 | 386 | Unplanned | OTHER | Cause: Part of HV outage 114199, not included in advertising Is 2R required? N Additional Info: FM confirmed customer feed off correct transformer, not sure why they were not included in advertising | .
2310 |  | JE24036889 | 218 MATANGARA ROAD, HAWERA, 4672 | Western | MEREMERE | 2024-10-04 | 11:59 | 2024-10-04 | 14:19 | 0.00038501 | 2.759e-06 | 1 | 140 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: W2035 No. Fuses: 2 Fuse Amp Size:3 TIME CLOSED: 14:18 Cause: Deuteration Weather (wind/rain): calm Follow up required (select advisory)?N ****No 2R***** | .
2311 |  | JE24036938 | HUIROA | Western | HUIROA | 2024-10-04 | 19:03 | 2024-10-04 | 20:51 | 0.00059377 | 5.5179e-06 | 2 | 215 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: 2290T No. Fuses: 2 Fuse Amp Size: 2 Amp TIME CLOSED: 20:51 Cause: LV Fault Weather (wind/rain): Calm Follow up required (select advisory)? N Also replaced burnt out LV fuse base and carrier | .
2312 |  | JE24033622 | 501 PAHIATUA MANGAHAO ROAD MANGAMUTU PAHIATUA | Western | MANGATAINOKA | 2024-10-03 | 9:34 | 2024-10-03 | 10:26 | 0.00014448 | 2.759e-06 | 1 | 52 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To resag 11kv conductor and clear trees from 11kv lines past Fuses R65 | .
2313 |  | JE24033726 | MANGATAINOKA | Western | MANGATAINOKA | 2024-10-03 | 10:36 | 2024-10-03 | 11:43 | 0.0014711 | 2.2072e-05 | 8 | 533 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11KV Xarm P40578 | .
2314 |  | JE24033751 | 34 GLOUCESTER ROAD MOUNT MAUNGANUI TAURANGA | Eastern | EVERSHAM RD | 2024-10-03 | 23:31 | 2024-10-04 | 2:36 | 0.066228 | 0.00035867 | 130 | 24005 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9206/1/2/3/4 | .
2315 |  | JE24033755 | 50 LONGACRE ROAD OKOIA WANGANUI | Western | MAKIRIKIRI | 2024-10-03 | 9:05 | 2024-10-03 | 9:10 | 0.0003766 | 7.1733e-05 | 26 | 137 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace multiple defected Poles & X-Arms between 790749 & 790776 JE 24036683 not an outage Scada dressed incorrectly | .
2316 |  | JE24033761 | 864 PENNY ROAD SANSON PALMERSTON NORTH | Western | MT STEWART | 2024-10-03 | 8:45 | 2024-10-03 | 15:31 | 0.046971 | 0.00011588 | 42 | 17025 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole and hardware on poles P28369, P31198, 862832, P21765. Remove redundant S/L pole P21767. | .
2317 |  | JE24033946 | 722 KAWEORA ROAD OPUNAKE OPUNAKE | Western | IHAIA RD | 2024-10-03 | 9:14 | 2024-10-03 | 15:22 | 0.043191 | 0.00011864 | 43 | 15655 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove ABS TA110. Install new entec structure at pole site 714260 | .
2318 |  | JE24033965 | BAINESSE | Western | BAINESSE | 2024-10-03 | 8:31 | 2024-10-03 | 13:51 | 0.03003 | 9.3805e-05 | 34 | 10885 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Change poles & crossarms P43231; P43233; P43234; P45223; P45224; P45222/P45221 | .
2319 |  | JE24034136 | 264 MAKIRIKIRI ROAD CROFTON MARTON | Western | LEEDSTOWN 22KV | 2024-10-03 | 9:00 | 2024-10-03 | 12:45 | 0.029154 | 0.00012967 | 47 | 10567 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Isolation to remove vines pole 803515 | .
2320 |  | JE24034533 | 201 LINCOLN ROAD INGLEWOOD INGLEWOOD | Western | LEPPERTON | 2024-10-03 | 9:34 | 2024-10-03 | 15:41 | 0.074909 | 0.00020416 | 74 | 27151 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To Replace Hv TX structures - 1560 + 563 +1159 | .
2321 |  | JE24035843 | 82 CORBETT ROAD WAIHI WAIHI, 33 HIGHLAND ROAD WAIHI | Eastern | WHIRITOA | 2024-10-03 | 9:00 | 2024-10-03 | 14:01 | 0.024731 | 0.00013243 | 48 | 8964 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Arm at poles P1524, P13377, P13376, P1508, 876612, 876611 | .
2322 |  | JE24036633 | PURANGI | Eastern | PURANGI | 2024-10-03 | 1:13 | 2024-10-03 | 11:30 | 0.78091 | 0.0053248 | 1273 | 283043 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV WHT CB5 Protection flags (nil where none): O/C CAUSE: Large tree fell across HV Lines Location: Between Poles W0455/W0454 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Rain/lightning LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Faulty section of the network has been Isolated. Large tree has fallen across HV Lines at Pole W0455/W0454 Repairs to be carried out during daylight hours. Due to Voltage Issues Break before Make made to restore normal tie points!! ***Will require an Inspector for 400/11KV clash ,Downer to organise, may result in damaged installations that will need to be left off***. Inspected & Relivened 03/10/24 @ 11:05 | .
2323 |  | JE24036634 | COOK DRIVE | Eastern | COOK DRIVE | 2024-10-03 | 1:34 | 2024-10-03 | 3:16 | 1.549 | 0.024422 | 8852 | 561438 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | REGULATORY INFORMATION Voltage & Device ID: 11kV WHT CB 19 & CB 17 Protection flags (nil where none): A B C Ø Fault, RES GND, RES O/C CAUSE: Tree branch bridging across two phases. Location: Pole W0011 mid-span Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Rain/wind/lightning. LFI (Y/N + Comments): No Follow up Required (select advisory)? Yes, protection issue. Additional fault restoration comments: Major fault which caused WHT S/S CB 19 & CB 17 To trip and clear the 11kV Busbar. Member of the public called in on the Electrical Emergency line saying they heard a loud bang near 175 South Highway ( TX TC1109 ) Field Switcher first went to WHT S/S to carry out a visual inspection & smell test. All was in order and the Protection Flags were then reset. The 11kV Busbar was re-livened via CB 19 & CB 17 All the feeders were put back one by one except for CB 2 & CB 5 (Tripped earlier) Seems as if the fault which was found on CB 2 Cook Drive feeder caused the 11kV Transformer breakers to clear 11kV busbar. Protection did not operate correctly on CB 2. Field Switcher removed the tree branch with his Hotstick and CB 2 was closed in at 03:15 | .
2324 |  | JE24036638 | TE KIRI | Western | TE KIRI | 2024-10-03 | 2:56 | 2024-10-03 | 8:25 | 0.080468 | 0.00056559 | 161 | 29166 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 12273/2 Protection flags (nil where none): B ph O/C & E/F CAUSE: Pin hole in Insulator Location: 715927 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: cursory Weather (wind/rain): rain LFI (Y/N + Comments): no - comms failure Pole 467127 Follow up Required (select advisory)? n Additional fault restoration comments: Lines was isolated at ABS's TA876 & TA914 & Links 12273/6 to replace insulator. | .
2325 |  | JE24036642 | PUHUNGA ISLAND RD | Eastern | PUHUNGA ISLAND RD | 2024-10-03 | 5:22 | 2024-10-03 | 6:46 | 0.010824 | 0.00012967 | 47 | 3923 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 14813 Protection flags (nil where none): E/F CAUSE: High Winds , Wind Blown Debris Location: 14813/2 Section Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Curse Weather (wind/rain): High Wind Gusts LFI (Y/N + Comments): Nil Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2326 |  | JE24036651 | TE ARAKURA | Western | TE ARAKURA | 2024-10-03 | 7:37 | 2024-10-03 | 8:16 | 0.00031974 | 8.2769e-06 | 3 | 116 | Unplanned | WILDLIFE - BIRD | Fuses Location: D93 No. Fuses: 2 Fuse Amp Size: 5A TIME CLOSED: 08:15 Cause: Bird Strike Weather (wind/rain): Raining Follow up required (select advisory)?N 2R used as one carrier replaced | .
2327 |  | JE24036670 | 72 KUKU ROAD, POHANGINA, ASHHURST, 4884 | Western | POHANGINA | 2024-10-03 | 10:12 | 2024-10-03 | 11:28 | 0.0014726 | 1.9313e-05 | 7 | 534 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolated at Fuses F76 Lines repaired | .
2328 |  | JE24036674 | IRIRANGI | Western | IRIRANGI | 2024-10-03 | 8:52 | 2024-10-03 | 18:15 | 0.016769 | 3.0349e-05 | 11 | 6078 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 2563 & Tfr X790 No. Fuses: 2 & 1 Fuse Amp Size: 8 & 2 TIME CLOSED: 18:00 & 18:15 Cause: unknown Weather (wind/rain): windy Follow up required (select advisory)?n | .
2329 |  | JE24036713 | KUAOTUNU | Eastern | KUAOTUNU | 2024-10-03 | 10:15 | 2024-10-03 | 15:51 | 0.11278 | 0.0018264 | 662 | 40877 | Unplanned | THIRD PARTY INTERFERENCE - TREES | REGULATORY INFORMATION Voltage & Device ID: 11kV Sec 9632 Protection flags (nil where none): A, B, Phase O/C CAUSE: Trees Dropped into lines , Breaking 1 x wire Location: W1200 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Fault Rung in with exact location Weather (wind/rain): Wind , Rain LFI (Y/N + Comments): Yes Pole W13821 Follow up Required (select advisory)? Additional fault restoration comments: Pine Dale Logging , Dropped Trees into Lines 1st Blowing 1 x D/out fuse @ Fuses FC 2327 2nd time Breaking a wire @ Pole W1200 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2330 |  | JE24036721 | CHURCH ST | Western | CHURCH ST | 2024-10-03 | 10:48 | 2024-10-03 | 13:13 | 0.035916 | 0.00052696 | 191 | 13018 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: Recloser C279/2 Protection flags (nil where none): B, C Ph O/C CAUSE: Tree on Lines brought lines down Location: Pole 829537 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Raining, Windy LFI (Y/N + Comments): N/A Follow up Required (select advisory)? N Additional fault restoration comments: Isolated at ABS S74 Lines repaired SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2331 |  | JE24036731 | PAPAKAI | Western | PAPAKAI | 2024-10-03 | 11:39 | 2024-10-03 | 15:25 | 0.050246 | 0.00058766 | 213 | 18212 | Unplanned | ADVERSE WEATHER - WIND-BLOWN DEBRIS (NOT TREES) | REGULATORY INFORMATION Voltage & Device ID: 11Kv cb 7 Protection flags (nil where none): a & b PH o/c CAUSE: Branch on lines Location: Between poles 788282 & 788283 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: cursory Weather (wind/rain): windy LFI (Y/N + Comments): n Follow up Required (select advisory)? Y - CB 7 will not close via Scada or manually, Tech / Suby to investigate. Additional fault restoration comments: REC 4705/2 was opened & Gas/Sw 4706/2 closed. lines was patrolled and branch was found on lines between poles 788282 & 788283 which was removed with hot line sticks. | .
2332 |  | JE24036740 | OPUNAKE 33KV | Western | OPUNAKE 33KV | 2024-10-03 | 12:01 | 2024-10-03 | 12:05 | 0.013092 | 0.0046102 | 1671 | 4745 | Unplanned | DEFECTIVE EQUIPMENT - ZONE SUBSTATION | Shut Tasman Sub down to re-connect earthing at transformer T1. | .
2333 |  | JE24036751 | PURANGI | Eastern | PURANGI | 2024-10-03 | 13:02 | 2024-10-03 | 17:02 | 0.0039693 | 1.6554e-05 | 6 | 1439 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: FC4172 No. Fuses: 2 Fuse Amp Size: 3amp TIME CLOSED: 17:01 Cause: Unknown Weather (wind/rain): Follow up required (select advisory)? also replaced 2 x Fuse Barrels. | .
2334 |  | JE24036785 | IRIRANGI | Western | IRIRANGI | 2024-10-03 | 16:01 | 2024-10-03 | 19:14 | 0.00053266 | 2.759e-06 | 1 | 193 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Incorrect Job location Fuses Location: X1634 No. Fuses: 2 Fuse Amp Size: 2 TIME CLOSED: 19:13 Cause: lightning a few weeks ago, old woolshed at the back of the farm Weather (wind/rain): lightning Follow up required (select advisory)?n | .
2335 |  | JE24036792 | BRYCE ST | Western | BRYCE ST | 2024-10-03 | 17:10 | 2024-10-03 | 18:50 | 0.0005528 | 5.5179e-06 | 2 | 200 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuse found blown in Fuse/Sw 4749/2 Fuse/Sw Isolated and earthed Fuses replaced Fuse/ Sw closed with LV load Isolated Site electrician closed main switch for plant, bring plant on line in one go Fuse blew again. Fuse/Sw Isolated again and fuse replaced LV isolated and transformer livened Main Switch has been repaired, 400V TFR X3200 Fuses have been closed, restoring full power to customer Downer are going to order new 80A HV fuse to install at the Fuse/Sw 4749/2 this week, unplanned short notice outage will be required Fuses will be replaced in the weekend Fuses to be replaced under SIS 116514 on the 19/10/24 | .
2336 |  | JE24036818 | MANGATOKI | Western | MANGATOKI | 2024-10-03 | 21:30 | 2024-10-03 | 23:05 | 0.00078714 | 8.2769e-06 | 3 | 285 | Unplanned | WILDLIFE - BIRD | Fuses Location: 5859 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 23:05 Cause: bird strike Weather (wind/rain): calm Follow up required (select advisory)?n Line patrolled | .
2337 |  | JE24033538 | TE POI | Eastern | TE POI | 2024-10-02 | 9:15 | 2024-10-02 | 14:09 | 0.005666 | 1.9313e-05 | 7 | 2054 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace xarms and upgrade TX structure. Worksite Poles 878352, F1808, F13063 | .
2338 |  | JE24033566 | 56 ANGLAND DRIVE TE RANGA TE PUKE | Eastern | TE MATAI RD | 2024-10-02 | 9:00 | 2024-10-02 | 10:26 | 0.00047086 | 5.5179e-06 | 2 | 171 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Link box maintenance at SF5-009, SF5-037 & SF5-036 | .
2339 |  | JE24033626 | 843 TAIRUA WHITIANGA ROAD WHENUAKITE WHITIANGA | Eastern | TAIRUA NORTH | 2024-10-02 | 8:51 | 2024-10-02 | 12:25 | 0.0053175 | 2.4831e-05 | 9 | 1927 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Clear trees away from 11kV line between poles W1905 & W13414 | .
2340 |  | JE24033698 | 125 POWNALL STREET MASTERTON MASTERTON | Western | CORNWALL ST | 2024-10-02 | 8:47 | 2024-10-02 | 13:15 | 0.28605 | 0.001065 | 386 | 103680 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles 822992 and 822988 and hardware on pole 828127 | .
2341 |  | JE24033727 | 482 OLD TE AROHA ROAD OKAUIA MATAMATA | Eastern | GORDON | 2024-10-02 | 8:45 | 2024-10-02 | 16:14 | 0.065855 | 0.00051041 | 110 | 23869 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Short shut to make breaks (AP1) Replace arms (AP2) Reinstall breaks (AP3) | .
2342 |  | JE24033728 | PAPAMOA BEACH WEST | Eastern | PAPAMOA BEACH WEST | 2024-10-02 | 23:30 | 2024-10-03 | 3:10 | 0.062958 | 0.00028693 | 104 | 22819 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9067/1/2/3/4 | .
2343 |  | JE24033735 | MANAIA | Western | MANAIA | 2024-10-02 | 9:11 | 2024-10-02 | 15:50 | 0.19843 | 0.00049661 | 180 | 71922 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace 11kv pole 719365 | .
2344 |  | JE24033939 | DURIE HILL | Western | DURIE HILL | 2024-10-02 | 9:31 | 2024-10-02 | 13:38 | 0.12563 | 0.00050765 | 184 | 45537 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv X arms on poles 774014 and 767977, carry out maintenance on 33kv ABS 3153 and 367, replace insulator on ABS 392 | .
2345 |  | JE24034035 | 2 WENLOCK STREET WAIHI WAIHI | Eastern | WAIHI NORTH | 2024-10-02 | 8:37 | 2024-10-02 | 14:46 | 0.08639 | 0.00023451 | 85 | 31313 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Create 11kv line break at Pole P1235 using live line proceedures GB1,GB3 & GB27. Replace 11kv & 400v Xarms at Pole P12546 under 11kv Access Permit Close 11kv line break at Pole P1235 using live line proceedures GB1,GB3 & GB25 | .
2346 |  | JE24034040 | 763 RANGIWAHIA ROAD KIMBOLTON KIMBOLTON | Western | RANGIWAHIA | 2024-10-02 | 9:53 | 2024-10-02 | 14:20 | 0.028008 | 0.00010484 | 38 | 10152 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Two sites ,Replace ABS N8 and resag spurline from P02091 and T5/26 | .
2347 |  | JE24036503 | DE HAVILLAND NORTH | Western | DE HAVILLAND NORTH | 2024-10-02 | 6:52 | 2024-10-02 | 9:37 | 0.020978 | 0.00033108 | 120 | 7604 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 1 Protection flags (nil where none): A, B & C ph O/C & E/F CAUSE: Bird Strike Location: 743715 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: cursory Weather (wind/rain): calm LFI (Y/N + Comments): Follow up Required (select advisory)? n Additional fault restoration comments: Received call of seagull hitting lines, lines were isolated at ABS's 310, 358 & 436 to repair the lines. | .
2348 |  | JE24036586 | MATAPU | Western | MATAPU | 2024-10-02 | 14:53 | 2024-10-02 | 15:16 | 0.00057524 | 2.4831e-05 | 9 | 209 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Faultman found jumper had come out of bottom side of Fuses 6924, line was isolated at Fuses 6924 to reconnect the jumper on pole 847702. | .
2349 |  | JE24036625 | MAHOE | Western | MAHOE | 2024-10-02 | 22:07 | 2024-10-02 | 23:34 | 0.00313 | 3.5867e-05 | 13 | 1134 | Unplanned | WILDLIFE - POSSUM | Broken jumper on the top of DDO to TFR 3065T at Pole 731912 Isolated at ABS 5706 & 5996 Connection at the top of the DDO repaired, dead possum removed from between TFR tank and LV Bushings, Replaced 1 x 3A Fuse, Full power restored | .
2350 |  | JE24036631 | COLVILLE | Eastern | COLVILLE | 2024-10-02 | 23:00 | 2024-10-03 | 2:34 | 0.0041274 | 1.9313e-05 | 7 | 1496 | Unplanned | VEGETATION - OUTSIDE ZONE | Fuses Location: TX TP2634 No. Fuses: 2 Fuse Amp Size: 6 Amp TIME CLOSED: 02:34 Cause: Tree fell over and broke LV Pole V13610 Weather (wind/rain): Rain & wind. Follow up required (select advisory)? No Member of public called in on the Electrical Emergency Line Report of a tree that came down over the road & O/H Lines are very low to the ground. Broken LV Pole V13610 TP2634 - 2 X HV Fuses blown Isolated through LV Disconnects Busy creating LV Line break LV Line break Pole at 390225 Partial LV Outage until repairs are completed. 03/10/2024 - Wayde Habib - LV pole replaced, rested and re-livened, full power restored - HM | .
2351 |  | JE24033268 | TOTMANS RD | Eastern | TOTMANS RD | 2024-10-01 | 8:49 | 2024-10-01 | 9:56 | 0.00055359 | 8.2769e-06 | 3 | 201 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REMOVAL OF REDUNDANT HV XARM AT POLE E12973 | .
2352 |  | JE24033286 | 66 DUDDINGS LINE TAUHERENIKAU FEATHERSTON | Western | DAIRY FACTORY | 2024-10-01 | 9:01 | 2024-10-01 | 12:04 | 0.0050613 | 2.759e-05 | 10 | 1835 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles 818790 and | .
2353 |  | JE24033468 | WAIMAPU | Eastern | WAIMAPU | 2024-10-01 | 9:01 | 2024-10-01 | 15:07 | 0.088889 | 0.00024279 | 88 | 32218 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 210996 to pole 211013 | .
2354 |  | JE24033471 | 83 POWNALL STREET MASTERTON MASTERTON | Western | CORNWALL ST | 2024-10-01 | 6:04 | 2024-10-01 | 15:48 | 0.15651 | 0.00070905 | 205 | 56729 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv pole 822965 and install new spur line fuses, remove Temp 38 from network | .
2355 |  | JE24033474 | 1 DAKOTA WAY MOUNT MAUNGANUI TAURANGA | Eastern | AERODROME | 2024-10-01 | 22:01 | 2024-10-02 | 4:47 | 0.036955 | 9.1046e-05 | 33 | 13395 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9034/1/2/3/4/5 | .
2356 |  | JE24033520 | MANGOREWA | Eastern | MANGOREWA | 2024-10-01 | 8:51 | 2024-10-01 | 14:02 | 0.046394 | 0.00014898 | 54 | 16816 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv/400vt poles 230062,263437,230060,230061.Replace 11kv cross arms @ pole 482815 | .
2357 |  | JE24033524 | 91 JACKEYTOWN ROAD TIAKITAHUNA PALMERSTON NORTH | Western | BAINESSE | 2024-10-01 | 8:46 | 2024-10-01 | 14:03 | 0.029692 | 9.3805e-05 | 34 | 10762 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Change poles & crossarms P43227; P43226; P43232; P43225 - LV reconductor from P44998-P43228. | .
2358 |  | JE24033576 | LEPPERTON | Western | LEPPERTON | 2024-10-01 | 9:46 | 2024-10-01 | 15:10 | 0.0035817 | 1.1036e-05 | 4 | 1298 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Tx Pole 742859 Tx 1590 79 lincoln road east - shut 13 | .
2359 |  | JE24033584 | 1 WILSON STREET BULLS BULLS | Western | PAREWANUI | 2024-10-01 | 10:00 | 2024-10-01 | 11:18 | 0.01943 | 0.00028417 | 103 | 7043 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Hardware repairs on pole 803725,803726 | .
2360 |  | JE24033598 | 859 WIREMU ROAD OPUNAKE OPUNAKE | Western | IHAIA RD | 2024-10-01 | 9:00 | 2024-10-01 | 15:19 | 0.032839 | 8.8287e-05 | 32 | 11903 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove ABS pole TA168. install new top mount entec switch pole structure | .
2361 |  | JE24033706 | POLLEN ST | Eastern | POLLEN ST | 2024-10-01 | 21:02 | 2024-10-05 | 0:08 | 0.086366 | 0.0011532 | 208 | 31304 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Switch gear and transformer at site | .
2362 |  | JE24033713 | 1109 TAIRUA WHITIANGA ROAD WHENUAKITE WHITIANGA | Eastern | COROGLEN | 2024-10-01 | 9:18 | 2024-10-01 | 15:50 | 0.059592 | 0.00015174 | 55 | 21599 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install 2x softwood poles between poles W13372 & W13373 for fibre attachment points. Re-hang Transformer TC1743 on 3m steel arm. | .
2363 |  | JE24034158 | 715 CHESTER ROAD WEST TARATAHI CARTERTON | Western | CHESTER RD | 2024-10-01 | 8:50 | 2024-10-01 | 13:03 | 0.082393 | 0.00032556 | 118 | 29864 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Removal of trees near 11kv lines between poles 821863 and 821866 | .
2364 |  | JE24034216 | 74 RANGIWAHIA ROAD KIMBOLTON FEILDING | Western | RANGIWAHIA | 2024-10-01 | 10:01 | 2024-10-01 | 11:10 | 0.0040084 | 5.7938e-05 | 21 | 1453 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace post insulator nut and straighten Pole P03872 | .
2365 |  | JE24036374 | MANGOREWA | Eastern | MANGOREWA | 2024-10-01 | 6:17 | 2024-10-01 | 7:45 | 0.00072264 | 8.2769e-06 | 3 | 262 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses FP894 No. Fuses: 2 Fuse Amp Size: 8A TIME CLOSED: 07:44 Cause: Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? No | .
2366 |  | JE24036429 | TAUPO QUAY1 33kV | Western | TAUPO QUAY1 33kV | 2024-10-01 | 10:25 | 2024-10-01 | 10:35 | 0.063752 | 0.0078989 | 2863 | 23107 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 33kV CB 2232 Protection flags (nil where none): E/F, O/C B CAUSE: cable termination fault Location: Taupo Quay Sub at Pole 483286/483090 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): calm LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: cable fault found, Downer have I & E and are looking for a cable termination kit Isolated at ABS 367, 392 & CB 222 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Taupo Quay Sub & Beach Rd Sub Circuit that tripped: Wanganui GXP CB 2232 DTF (KM): 10.86 then 8.17km 02/10/2024 Cable repair carried out and returned to service. 18:27 Network to be restored to normal configuration under NAPA 113044 02/10/2024 | .
2367 |  | JE24036430 | WAIMAPU | Eastern | WAIMAPU | 2024-10-01 | 9:00 | 2024-10-01 | 15:07 | 0.0010122 | 2.759e-06 | 1 | 367 | Unplanned | UNKNOWN - DATA QUALITY | Cause: Data quality issue HV planned outage 108761 What was replaced? NA Where was it replaced (pole/TX/pillar box)? NA Is 2R required? N 2R Y - What is the timeframe for repairs? NA Additional Info: AI team emailed yes Customer not on HV advertising as incorrect transformer for this icp, correct TX confirmed by FM TE4-115, incorrect transformer TE4-016 | .
2368 |  | JE24036436 | GORDON | Eastern | GORDON | 2024-10-01 | 11:38 | 2024-10-01 | 13:16 | 0.00053965 | 5.5179e-06 | 2 | 196 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: Loose connection What was replaced? Connection, 63A fuse and cut out Where was it replaced (pole/TX/pillar box)? Pole Is 2R required? Y 2R Y - What is the timeframe for repairs? Additional Info: Fuses 1434 Opened at 11:38 and Closed at 13:15. FM Re attached Stay Wire at Ground Level. | .
2369 |  | JE24036462 | 63 Brewer Road, Waitotara, 4592 | Western | WAITOTARA | 2024-10-01 | 16:03 | 2024-10-01 | 17:50 | 0.000297 | 2.759e-06 | 1 | 108 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | A Truck offloading fertiliser from it trailer has hit the lines causing them to fall down Isolated at Fuses 4485 Lines repaired at Pole 356040, full power restored | .
2370 |  | JE24036466 | TIROHIA-KARANGAHAKE | Eastern | TIROHIA-KARANGAHAKE | 2024-10-01 | 14:48 | 2024-10-01 | 16:00 | 0.00020017 | 2.759e-06 | 1 | 73 | Unplanned | WILDLIFE - BIRD | Fuses Location: FC2360 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 16-00 Cause: Bird strike Weather (wind/rain): sunny Follow up required (select advisory)? | .
2371 |  | JE24036494 | KOPANE | Western | KOPANE | 2024-10-01 | 21:15 | 2024-10-01 | 23:15 | 0.014211 | 0.00011864 | 43 | 5151 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Location: P34453 Cause: Corrosion of Cu-Ali conductor joint Isolation: O25 What was replaced? Conductor Joint & line pulled back up. Additional Info: | .
2372 |  | JE24032639 | 42 BEACH ROAD and 109B PARK ROAD KATIKATI KATIKATI | Eastern | MIDDLEBROOK | 2024-09-30 | 13:45 | 2024-09-30 | 13:58 | 0.012497 | 0.00094081 | 341 | 4530 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 10 yearly protection relay maintenance (9516 & 14250). Short Outage required to test Open / Close of Sectionaliser 14250 | .
2373 |  | JE24033271 | 414 BALLANCE ROAD BALLANCE PAHIATUA | Western | MANGATAINOKA | 2024-09-30 | 9:01 | 2024-09-30 | 13:35 | 0.059742 | 0.00021796 | 79 | 21654 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace crossarms & hardware between P26455 and P40356. | .
2374 |  | JE24033342 | 28 CITRUS AVENUE WAIHI BEACH WAIHI BEACH | Eastern | WILSON RD | 2024-09-30 | 9:38 | 2024-09-30 | 14:52 | 0.078885 | 0.00025107 | 91 | 28592 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | CREATE 11KV LINE BREAK AT POLE Q12424 USING GB1,GB3 AND GB27 REPLACE DNO ABS IP50 11KV XARMS AND 400V U/G CABLE CLOSE 11KV LINE BREAK AT POLE Q12424 USING GB1,GB3 AND GB25 | .
2375 |  | JE24033437 | 328 WIREMU ROAD TE KIRI OPUNAKE | Western | IHAIA RD | 2024-09-30 | 9:21 | 2024-09-30 | 12:41 | 0.0071655 | 3.5867e-05 | 13 | 2597 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace HV xarms at poles 715476, 715622, 715602 and 715628 | .
2376 |  | JE24033527 | 446 ST AUBYN STREET MOTUROA NEW PLYMOUTH | Western | BREAKWATER RD | 2024-09-30 | 8:45 | 2024-09-30 | 14:54 | 0.20752 | 0.00056283 | 204 | 75216 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 702453 and replace with a new B11 pole Remove ABS 132 | .
2377 |  | JE24035346 | 247 OLD WEST ROAD LINTON | Western | LINTON | 2024-09-30 | 9:59 | 2024-09-30 | 12:43 | 0.020419 | 0.00013243 | 48 | 7401 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11KV ABS 10116 Switching Incident - JE24036287 Incorrect Earth switch closed causing CB 5 to trip at Massey. While carrying out NAPA 115825, Operation 17 & 18 were carried out incorrectly. Isolator for / was opened & Earth/Sw /3 was closed resulting in GMCB 5 opening & clearing the fault. | .
2378 |  | JE24036267 | TUTURUMURI | Western | TUTURUMURI | 2024-09-30 | 12:21 | 2024-09-30 | 13:45 | 0.0011684 | 1.3795e-05 | 5 | 424 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Floating conductor / broken binder at Pole 371722 due to high winds Isolated at Fuses 7317 Binder replaced, full power restored | .
2379 |  | JE24036293 | APITI | Western | APITI | 2024-09-30 | 11:16 | 2024-09-30 | 12:31 | 0.00020615 | 2.759e-06 | 1 | 75 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T5/247 No. Fuses: 2 Fuse Amp Size: 2 TIME CLOSED: 12:30 Cause: Lightning from a week ago Weather (wind/rain): lightning Follow up required (select advisory)?n old wool shed, not used much, only picked up power was off today | .
2380 |  | JE24036337 | MOUNT BRUCE | Western | MOUNT BRUCE | 2024-09-30 | 15:46 | 2024-09-30 | 16:13 | 0.00029521 | 1.1036e-05 | 4 | 107 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | King Bolt has almost pulled out of Pole 459395 Isolated for safety at Fuses 7693 King bolt put back in pole and full power restored Missing nut off king bolt | .
2381 |  | JE24036343 | UNION LINE | Western | UNION LINE | 2024-09-30 | 15:51 | 2024-10-01 | 15:15 | 0.011622 | 8.2769e-06 | 3 | 4212 | Unplanned | VEGETATION - INSIDE ZONE | Tree dropped through Lines past Fuses 2904 Isolated at Fuses 2904 Returning tomorrow for full repairs, only one customer off who is on a self supplied generator 01/10/24 - Tree removed, Pole 480557 replaced(TFR X1486 reinstalled), HV & LV lines repaired, Full power restored | .
2382 |  | JE24036351 | KINGS AVENUE | Western | KINGS AVENUE | 2024-09-30 | 15:19 | 2024-09-30 | 20:38 | 0.020822 | 6.6215e-05 | 24 | 7547 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION CAUSE: Car v Pole Location: 770986 Isolations: BCH 5: 4518/2, 16125/4, & 1407 TAQ1: 1072 & 2929 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: N/A Weather (wind/rain): Calm Follow up Required (select advisory)? Additional fault restoration comments: Replaced Pole, HV & LV crossarms etc. NDR to follow | .
2383 |  | JE24036177 | RANGITIKEI | Western | RANGITIKEI | 2024-09-29 | 1:21 | 2024-09-29 | 7:12 | 0.03682 | 0.00010484 | 38 | 13346 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: Isolated at Fuses D24 Protection flags (nil where none): CAUSE: Car V Pole P33879 Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Replaced Pole & Hardware. Repaired LV SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2384 |  | JE24036183 | MANGAPAKEHA | Western | MANGAPAKEHA | 2024-09-29 | 9:25 | 2024-09-29 | 15:42 | 0.0031204 | 8.2769e-06 | 3 | 1131 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Bute Repeater Site AC Mains failed. Field Switcher to test for full supply Voltage at Transformer T3011 Fuses 7865 - Reloaded and blew back at 09:25 Isolation: Fuses 7865 CAUSE: Suspect HV Cable fault ( 500m length of Cable ) Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Windy Follow up required (select advisory)? No Additional fault restoration comments: NOC dispatched a field switcher to attend to a Bute Repeater AC mains warning that alarmed on night shift. Upon arrival the field switcher found Fuses 7865 to be blown (Open) Requested permission to re-load and re-liven which was not successful. (Blew back) AP 6183 was taken to disconnect the HV Cable terminations at Transformer T3011. TP 6183-02 was taken to test the HV Cable to identify the root cause of this fault. Field Switcher informed NOC that the test results do not look very good and NOC should organize a back-up Generator for this RPT Site. NOC then logged a job with IS who in turn opened a Ticket with Vital - INC0092748 to arrange a Generator for Bute Rpt Site. Liam from Ventia called to inform NOC that the Generator at Bute Rpt Site was in Service at 15:42 ( Manual Changeover Switch) Liam is unsure how long the Generator will run for, estim | .
2385 |  | JE24036185 | WAITAWHETA | Eastern | WAITAWHETA | 2024-09-29 | 7:59 | 2024-09-29 | 13:18 | 0.038431 | 0.00013243 | 48 | 13930 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV SEC 9454/2 Protection flags (nil where none): A, B, C Ø O/C & E/F CAUSE: Broken HV Line down due to a Bird.(as per Field Switcher) Location: Pole P2212 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Awaiting Field Switchers to commence a Line Patrol. Les Cole & Nic Hyland called in to NOC to confirm the device and to start with the Line Patrol. Terrain is rural and high volume of trees involved. Member of the public called in with a Lines down Hazard. Lines down was repaired under the AP Full Power restored via ABS 248 at 13:17 | .
2386 |  | JE24036193 | MANGOREWA | Eastern | MANGOREWA | 2024-09-29 | 10:03 | 2024-09-30 | 16:02 | 0.62341 | 0.0023258 | 663 | 225960 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV SEC 9689/2 feeding PGA 1 + PGA 6 Protection flags (nil where none): A B Ø O/C CAUSE: HV Lines down across SH 33 ( Hedge fire ) Location: Pole 483 168 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Calm LFI (Y/N + Comments): Yes, at Pole 221755 Follow up Required (select advisory)? Yes Additional fault restoration comments: PGA CB1 & CB6 is currently being back feed via NOP from TPV2 SEC 9689/2 The entire PGA CB1 & CB6 is currently affected with this fault.(No Power) Fire Comms updated both sides of the road Hedge on fire Line down across road near Pole 483 168 Road currently closed - Fire requesting traffic management. Major tree trimming required two spans before ABS IP625, therefore Isolation area had to be increased for this additional work to be carried out, the tree trimming company have been aware of this hedge which is very overgrown and touching HV Lines. (NOC Performance Team to investigate) Isolation was carried out, back feed via PGA3 was put in place by closing ABS SF6-039 at 12:44 Earthing is currently taking place right now. Repairs and tree trimming are being carried out under AP 6193 Lines repaired and tree cleared Power restored 19:55 Se | .
2387 |  | JE24036212 | GILMOUR ST | Eastern | GILMOUR ST | 2024-09-29 | 14:38 | 2024-10-01 | 13:30 | 0.55025 | 0.0023396 | 821 | 199442 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV WHI CB8 Protection flags (nil where none): A Ø O/C & E/F CAUSE: Deterioration/rust (Glass disc insulator shattered) Location: Pole 853414 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Light wind LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: No LFI's operated at Sw/Gear 14585 & Sw/Gear 13868. Opened Sw/Gear 14585/3 and then closed in Sw/Gear 13868/1 via WHI3 to back feed a portion of the network. Les Cole to investigate if LFI;s operated at Sw/Gear 13474 Report from the public - At 34 Silverton Road, broken insulator. NOC informed the Field Switcher of this new information. Les to Isolate at ABS IC2633 & Nic Isolated at ABS 266 Insulator Replaced Power restored 19:33 HV, Contacted LV, fed from Transformer TP4325, multiple smart meters blown up. Isolated at Fuses 14712 Note: Transformer TP4325 to be investigated as per Field Switcher, seems like it has blown a rack. Tech will be on site to carry out some testing. Transformer Livened with LV fuses open, Loop tests poor R0.05 W 1.60, B 1.61 Transformer Isolated again Generator be installed on LV Still a number of properties to be inspected. Inspec | .
2388 |  | JE24033600 | 8 TITOKI PLACE MOUNT MAUNGANUI TAURANGA | Eastern | TE MAUNGA | 2024-09-28 | 10:19 | 2024-09-28 | 16:09 | 0.0064376 | 0.0001076 | 39 | 2333 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Linkbox maintenance | .
2389 |  | JE24036142 | WILSON RD | Eastern | WILSON RD | 2024-09-28 | 11:04 | 2024-09-28 | 16:58 | 0.58504 | 0.0024196 | 877 | 212049 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Voltage & Device ID: 33kV CB 3222 / CB 4 Protection flags (nil where none): A, B, C Ph Fault, O/C / A, B, C Fault, O/C CB 4 A/R Load half of load before tripping Weather (wind/rain): Calm Follow up required (select advisory): LFI Activation: Y/N NA CB 4 Open due to report of Transformer Exploding. waiting for FM on site Bird strike report near 2A Seaforth Rd Tech required to check Relays for T2 and down load flags Blown Jumpers at ABS IP50, (ABS currently DNO'd) Second lot of Blown Jumpers found at Pole Q12378 during isolating for repairs Back feed installed up to ABS 218 via Sectionaliser 13788, Power restored up to ABS IP627 once isolation in place. Tech carried out checks on protection and relays for T2 (CB 3222) Both Transformers protection picked up O/C T2 protect tripped in mil seconds, where T1 still time when CB 4 tripped. Tech has down loaded readings and protection settings for both protection systems to send to o Powerco's protect team. Transformer was returned to service after discussion with tech. | .
2390 |  | JE24036162 | 4153 MOUNTAIN ROAD, NGAERE, STRATFORD, 4393 | Western | CLOTON RD INDUSTRIAL | 2024-09-28 | 16:11 | 2024-09-28 | 17:24 | 0.00019915 | 2.759e-06 | 1 | 72 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 4995 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 17:23 hrs Cause: Suspect Duck hit lines Weather (wind/rain): Calm Follow up required (select advisory)? | .
2391 |  | JE24036164 | SOUTH FEATHERSTON | Western | SOUTH FEATHERSTON | 2024-09-28 | 17:12 | 2024-09-28 | 18:30 | 0.00043495 | 5.5179e-06 | 2 | 158 | Unplanned | WILDLIFE - BIRD | Fuses Location: 11001 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 18:30 Cause: Duck Strike Weather (wind/rain): Follow up required (select advisory)? | .
2392 |  | JE24033393 | 190 TURAKINA BEACH ROAD TURAKINA WANGANUI | Western | TURAKINA | 2024-09-27 | 9:15 | 2024-09-27 | 13:17 | 0.1095 | 0.00045247 | 164 | 39688 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT: Repair conductor sag at poles 802085, 802059 & 356172. Repair sag & replace stay at 360706. | .
2393 |  | JE24033455 | 427 CARDIFF ROAD PEMBROKE STRATFORD | Western | CARDIFF RD | 2024-09-27 | 8:54 | 2024-09-27 | 15:20 | 0.12673 | 0.00032832 | 119 | 45934 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove switch and links 5455/2 & /4. install new recloser 12700/2, links /4. Remove ABS 6691 and install new entec switch 12709/2, links /4,/6 | .
2394 |  | JE24034133 | 210 JELLICOE STREET TE PUKE TE PUKE | Eastern | NO 3 ROAD | 2024-09-27 | 15:30 | 2024-09-27 | 15:44 | 0.013401 | 0.0010319 | 374 | 4857 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - SE5-121/SE5-123/SE5-120 | .
2395 |  | JE24035862 | 48 CAMPBELL ST WAIHOU | Eastern | SPRINGDALE | 2024-09-27 | 9:00 | 2024-09-27 | 10:07 | 0.0020243 | 3.0349e-05 | 11 | 734 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RED DEFECT. LOOSE DDO UNIT. REQUIRES REPLACEMENT AND ALSO REPLACE ROTTON DDO XARM | .
2396 |  | JE24035952 | TE KIRI | Western | TE KIRI | 2024-09-27 | 1:38 | 2024-09-27 | 6:24 | 0.05486 | 0.00056559 | 161 | 19884 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11KV Rec 12273-2 Protection flags (nil where none): B Phase E/F CAUSE: Unknown Location: Unknown Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Light Rain LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Nothing Found Light Rain We are Thinking a Cracked Insulator SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2397 |  | JE24035957 | COONOOR | Western | COONOOR | 2024-09-27 | 2:57 | 2024-09-27 | 4:52 | 0.028896 | 0.00030073 | 109 | 10473 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: T42 Protection flags (nil where none): B & C phase EF CAUSE: Magpie at base of pole Location: Pole P23089 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: cursory Weather (wind/rain): windy, rain LFI (Y/N + Comments): N Follow up Required (select advisory)? Additional fault restoration comments: | .
2398 |  | JE24035958 | PARK RD | Western | PARK RD | 2024-09-27 | 4:05 | 2024-09-27 | 7:15 | 0.080271 | 0.001316 | 217 | 29094 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: REC C422 Protection flags (nil where none): C phase EF CAUSE: trees near the lines at multiple sites Location: Pole 824381 & 824342 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: cursory Weather (wind/rain): windy, rain LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: | .
2399 |  | JE24035962 | PUKETIRO | Western | PUKETIRO | 2024-09-27 | 6:13 | 2024-09-27 | 10:11 | 0.010491 | 4.4143e-05 | 16 | 3802 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses 7856 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 10:10 Cause: Bird Strike - Dam right next to line Weather (wind/rain): Overcast Follow up required (select advisory)? - NIL | .
2400 |  | JE24035965 | STRATHMORE | Western | STRATHMORE | 2024-09-27 | 6:30 | 2024-09-27 | 8:53 | 0.0043396 | 3.0349e-05 | 11 | 1573 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: 5453 No. Fuses: 2 Fuse Amp Size:8A TIME CLOSED: 08:53 Cause: Line calsh Weather (wind/rain):windy Follow up required (select advisory)?N Fuses Location: 4407T No. Fuses: 1 Fuse Amp Size:2A TIME CLOSED: 09:37 Cause: LIgtning suspected from other day Weather (wind/rain): Wind Follow up required (select advisory)?N Line patrolled twice by FM | .
2401 |  | JE24035977 | PARK RD | Western | PARK RD | 2024-09-27 | 7:08 | 2024-09-27 | 11:11 | 0.00066853 | 2.759e-06 | 1 | 242 | Unplanned | WILDLIFE - BIRD | Fuses Location: T1557 No. Fuses: 2 Fuse Amp Size: 2 TIME CLOSED: 11:10 Cause: Bird trike Weather (wind/rain): calm Follow up required (select advisory)?N | .
2402 |  | JE24035990 | ATUAROA 33kV | Eastern | ATUAROA 33kV | 2024-09-27 | 8:25 | 2024-09-27 | 10:27 | 0.079991 | 0.0040446 | 1105 | 28993 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 33kV CB 3162 Protection flags (nil where none): B O/C E/F. CAUSE: Cable tie broken from Jumper that was folded Back after recloser installation Location: Rec 3227 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): Pole 269274 (KMO Side) Follow up Required (select advisory)? Yes Additional fault restoration comments: Surge arrestor will need to be replaced in a planned shutdown. Only 2 of the jumpers could be cut clear Third jumper will need to be cut clear when a planned shut down is organised. No flags from Switch 3520, opened & recloser 3227 closed. A/R on KMO CB 2182. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): ATU Circuit that tripped: 3162 DTF (KM): Lightning Arrestors to be replaced at later date 2R to be left open 9/10/2024 - 9/10/2024 - Waiting to be scheduled. CG 01/11/2024 - NAPA 116677 Scheduled for Surge Arrestors to be replaced 15/11/2024 Have completed job because no further work to be carried out under this fault job | .
2403 |  | JE24036002 | SPRINGDALE | Eastern | SPRINGDALE | 2024-09-27 | 15:46 | 2024-09-27 | 19:06 | 0.004407 | 2.2072e-05 | 8 | 1597 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Reload of fuses for TC2354 Failed Recloser RP04 A/R on closing fuses Transformer TC2354 found to be faulty, Deterioration 3 Phase 30kVA Isolated at Fuses for Transformer TC2354, Replaced 19:05 | .
2404 |  | JE24036010 | MAURICEVILLE | Western | MAURICEVILLE | 2024-09-27 | 9:37 | 2024-09-27 | 12:02 | 0.037975 | 0.00056283 | 204 | 13764 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Stay wire at Pole P29506 has broken and the pole has come over causing lines to be approx 1m from ground. Isolate for safety before back feeding customers due to hazard. Delays caused in back feeding due to tree work on donor feeder under CAC 115005-5 | .
2405 |  | JE24036012 | KAPANGA ROAD | Eastern | KAPANGA ROAD | 2024-09-27 | 9:45 | 2024-09-27 | 12:50 | 0.0020435 | 1.1036e-05 | 4 | 741 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 27/09/2024 Replace Faulty Transformer TC2383 due to High voltages Transformer Replaced under NAPA E00153 | .
2406 |  | JE24036026 | WAITUNA | Western | WAITUNA | 2024-09-27 | 10:31 | 2024-09-27 | 12:33 | 0.0033701 | 2.759e-05 | 10 | 1222 | Unplanned | VEGETATION - OUTSIDE ZONE | 1 x line down at Pole P70484 bought down by tree branch NDR to follow | .
2407 |  | JE24036040 | KOPANE | Western | KOPANE | 2024-09-27 | 11:54 | 2024-09-27 | 14:46 | 0.00047463 | 2.759e-06 | 1 | 172 | Unplanned | HUMAN ERROR - POTENTIAL SWITCHING ERROR | Part of Non outage NAPA 113049 - Unplanned outage, customer not notified | .
2408 |  | JE24036079 | INLAND COAST | Western | INLAND COAST | 2024-09-27 | 16:50 | 2024-09-27 | 18:01 | 0.00077637 | 1.1036e-05 | 4 | 281 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Floating Conductor at pole 757505 Isolated at Fuses 8487 All so Used 2 X10 H/V Fuses | .
2409 |  | JE24036114 | PUKETIRO | Western | PUKETIRO | 2024-09-27 | 22:16 | 2024-09-28 | 0:05 | 0.0048383 | 4.4143e-05 | 16 | 1754 | Unplanned | WILDLIFE - BIRD | Fuses Location: 7856 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 00:05 Cause: Duck Strike Weather (wind/rain): Calm Follow up required (select advisory)? No | .
2410 |  | JE24032544 | 14 MOORE STREET FEATHERSTON FEATHERSTON | Western | REVANS ST | 2024-09-26 | 9:16 | 2024-09-26 | 15:00 | 0.19343 | 0.00056283 | 204 | 70108 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | reconductor 11kv between 814247 & 813924 , change 11kv arms between 813912 & 798615 | .
2411 |  | JE24033091 | 617 MAUNGARANGI ROAD PAENGAROA TE PUKE | Eastern | MANGOREWA | 2024-09-26 | 8:47 | 2024-09-26 | 14:58 | 0.055266 | 0.00014898 | 54 | 20031 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv/400vt poles 230053,230054,230055,230056,230057 & 230058 | .
2412 |  | JE24033149 | 49 JACKEYTOWN ROAD TIAKITAHUNA PALMERSTON NORTH | Western | BAINESSE | 2024-09-26 | 8:31 | 2024-09-26 | 13:15 | 0.026677 | 9.3805e-05 | 34 | 9669 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Change poles and crossarms P44995; 857901; P44997; P43228; P43230 reconductoring between poles. 457792 remove birds nest. LV reconductor from P44995 - P44997 | .
2413 |  | JE24033175 | 847 matau road | Western | HUIROA | 2024-09-26 | 9:49 | 2024-09-26 | 15:11 | 0.03649 | 0.00011312 | 41 | 13226 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | asplundh to remove trees from between poles 709291 to 709292 | .
2414 |  | JE24033228 | 129 TENNANTS ROAD BULLS BULLS | Western | BULLS | 2024-09-26 | 9:04 | 2024-09-26 | 14:47 | 0.025572 | 7.4492e-05 | 27 | 9269 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re-conductor 11KV O/H lines with Ferret between poles 801885 & 378138. | .
2415 |  | JE24033257 | 706 GLOUCESTER ROAD PAPAMOA BEACH TAURANGA | Eastern | GLOUCESTER RD | 2024-09-26 | 10:30 | 2024-09-26 | 13:23 | 0.043405 | 0.00025107 | 91 | 15732 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - IP318-IP326-FP413 | .
2416 |  | JE24033320 | 1412 HALCOMBE ROAD HALCOMBE FEILDING | Western | KAKARIKI | 2024-09-26 | 9:30 | 2024-09-26 | 14:36 | 0.021076 | 6.8974e-05 | 25 | 7639 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove ABS M41 at P19304 replace P19305 with new pole and install new Tavridi recloser 10910/2, bypass ABS /1, Links /4,/6 & VT | .
2417 |  | JE24033346 | 116 OXFORD ROAD OKATO OKATO | Western | INLAND COAST | 2024-09-26 | 9:30 | 2024-09-26 | 10:35 | 0.019195 | 0.00030073 | 109 | 6957 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Urgent shut requested By poco PM to replace ABS U bracket Recloser 12720/1- By pass ABS | .
2418 |  | JE24033386 | 325 NGATIMARU ROAD TIKORANGI WAITARA | Western | TIKORANGI | 2024-09-26 | 9:01 | 2024-09-26 | 16:05 | 0.024166 | 5.7938e-05 | 21 | 8759 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 754728 for a new wooden. Replace pole 760782 and install new 33kV viper recloser 3568, remove old ABS 5051. Install new pole fitted with 33kV ABS 3564. Replace pole 760783 and install new 11kV ABS, old 33kV ABS 144 will be removed. Remove the 11kV OH from pole 760783 to 754728 and install new 11kV UG cable in replace. Install a new LV UG cable from Tx 4322T to the new Viper Recloser on pole 760782 for supply. Commission Recloser 3568. Install temp generation for Tikorangi School. | .
2419 |  | JE24033419 | 540 OROPI ROAD OROPI TAURANGA | Eastern | OHAUITI RD | 2024-09-26 | 9:15 | 2024-09-26 | 16:16 | 0.22788 | 0.00054627 | 198 | 82597 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 210971 to 210989. Relocate ABS SE4-031 from pole 210970 to pole 210975 | .
2420 |  | JE24035802 | LEPPERTON | Western | LEPPERTON | 2024-09-26 | 2:41 | 2024-09-26 | 4:39 | 0.0012976 | 1.1036e-05 | 4 | 470 | Unplanned | WILDLIFE - BIRD | Fuses Location: 8185 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 04:38 Cause: Bird strike Weather (wind/rain): calm Follow up required (select advisory)?n Line patrolled | .
2421 |  | JE24035803 | KAPONGA 33kV | Western | KAPONGA 33kV | 2024-09-26 | 6:30 | 2024-09-26 | 8:11 | 0.35265 | 0.0037577 | 1362 | 127821 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 2862 Protection flags (nil where none): Yellow Phase E/F CAUSE: Bird strike Location: Pole 737336 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Fine LFI (Y/N + Comments): Yes non SCADA'd Follow up Required (select advisory)? No Additional fault restoration comments: Fault Called in As doing Patrol Richard Williams has Photos of Bird. Cardiff ABR not fully commissioned, Needs Mirrored Bits between the units SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Cardiff & Kaponga Circuit that tripped: CB 2862 DTF (KM):No | .
2422 |  | JE24035813 | PIRINOA | Western | PIRINOA | 2024-09-26 | 7:54 | 2024-09-26 | 10:54 | 0.00049596 | 2.759e-06 | 1 | 180 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses 7343 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 10:53 Cause: Bird Strike Weather (wind/rain): windy Follow up required (select advisory)? | .
2423 |  | JE24035817 | HORRELLS RD | Eastern | HORRELLS RD | 2024-09-26 | 8:42 | 2024-09-26 | 14:08 | 0.0044895 | 1.3795e-05 | 5 | 1627 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: TC2490 Protection flags (nil where none): CAUSE: Deterioration Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Deterioration Rotten Broken Crossarm Replaced, HV Fuses Removed for Isolation , Fuses were on Fly Arm 400v Fly Arm on Transformer Structure SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2424 |  | JE24035836 | CROWN | Western | CROWN | 2024-09-26 | 10:04 | 2024-09-26 | 10:08 | 0.00057115 | 0.00013243 | 48 | 207 | Unplanned | THIRD PARTY INTERFERENCE - OTHER | Remove plastic wrap over 2 phases at Pole P32610 using hot sticks with feeder deenergised. No back feed available due to DNO 2408013 | .
2425 |  | JE24035842 | HORRELLS RD | Eastern | HORRELLS RD | 2024-09-26 | 9:34 | 2024-09-26 | 11:58 | 0.0011964 | 8.2769e-06 | 3 | 434 | Unplanned | WILDLIFE - BIRD | Fuses Location: FC2206 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 11:58 Cause: Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? | .
2426 |  | JE24035854 | DAIRY FACTORY | Western | DAIRY FACTORY | 2024-09-26 | 11:54 | 2024-09-26 | 12:01 | 1.8669e-05 | 2.759e-06 | 1 | 7 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Tap Transformer T3179 down to tap 2. Transformer either side is set to tap 2. Suspect that this transformer may have been taped up before Regulators 11235 were installed and now they are in sevice voltage is too high. New voltage 244V / 244V / 243V Enquiry sent to protection to check the set point of Regulators 11235 as they were found with output voltage of 11.24kV but SCADA indicates the set point should be 11.1kV | .
2427 |  | JE24035864 | HUNTERVILLE 22KV | Western | HUNTERVILLE 22KV | 2024-09-26 | 10:46 | 2024-09-26 | 14:41 | 0.0006467 | 2.759e-06 | 1 | 234 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 4053 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 14-40 Cause: Birds ?? Weather (wind/rain): Fine Follow up required (select advisory)? | .
2428 |  | JE24035897 | HAU NUI - TUTURUMURI - CB C642/2 | Western | TUTURUMURI | 2024-09-26 | 14:19 | 2024-09-26 | 19:40 | 0.12889 | 0.00051869 | 188 | 46717 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: CB C642 Protection flags (nil where none): C phase EF CAUSE: broken insulator and floating conductor at pole 811089 Location: Pole 810531 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: cursory Weather (wind/rain): windy LFI (Y/N + Comments): N Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2429 |  | JE24035899 | TINUI SUB - ANNEDALE - CB C936 | Western | ANNEDALE | 2024-09-26 | 14:26 | 2024-09-26 | 15:59 | 0.028814 | 0.00031176 | 113 | 10444 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: CB C936 Protection flags (nil where none): A & C Phase OC CAUSE: Unknwon, suspect line clashing in high winds Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: cursory Weather (wind/rain): windy LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: | .
2430 |  | JE24035945 | recloser_14473:2 | Eastern | WAIMAPU | 2024-09-26 | 18:44 | 2024-09-27 | 2:17 | 0.031966 | 0.00028141 | 102 | 11586 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: Recloser 14473 Protection flags (nil where none): Phase A OC CAUSE: Faulty Transformer TE4-196 Location: 211223 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: To replace Transformer TE4-196 Transformer replaced, Power on 02:17 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): No Circuit that tripped: N/A DTF (KM):N/A | .
2431 |  | JE24032713 | 283 RAILWAY ROAD KELVIN GROVE PALMERSTON NORTH | Western | BUNNYTHORPE | 2024-09-25 | 9:36 | 2024-09-25 | 11:51 | 0.00037375 | 2.759e-06 | 1 | 135 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace leaking TX T6/574 & replace TX arms | .
2432 |  | JE24032724 | 107 FRATERS ROAD MARTINBOROUGH MARTINBOROUGH | Western | DYERVILLE | 2024-09-25 | 8:30 | 2024-09-25 | 15:00 | 0.070988 | 0.00018209 | 66 | 25730 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles 808830 and 808827 Replace 11kv xarms poles 808822 and 808823 and 808816 | .
2433 |  | JE24033051 | 337 NO 1 ROAD TE PUKE TE PUKE | Eastern | TE MATAI RD | 2024-09-25 | 8:46 | 2024-09-25 | 14:40 | 0.010658 | 3.0349e-05 | 11 | 3863 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install a new 11kv/400vt 12.5m pole mid span between poles 230406 & 266896. Install new reclosure # 14923 with source side links. Remove redundant ABS IP441 . Connect new 400vt cable from Transformer TE5-176 to pole 231397 | .
2434 |  | JE24033067 | 155 KUAOTUNU WHAREKAHO ROAD KUAOTUNU WHITIANGA | Eastern | OWERA RD | 2024-09-25 | 9:27 | 2024-09-25 | 16:19 | 0.14758 | 0.00035867 | 130 | 53491 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Sectionaliser 9219 with new Tavrida switch. Replace pole and hardware at site. New radio and comms gear. | .
2435 |  | JE24033081 | 1941 TAIRUA WHITIANGA ROAD COROGLEN WHITIANGA | Eastern | TAIRUA NORTH | 2024-09-25 | 9:30 | 2024-09-25 | 17:25 | 0.1228 | 0.0002621 | 95 | 44508 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Stringing fibre between poles W12702 / W1739 & 248910 | .
2436 |  | JE24033082 | 1169 TAIHAPE-NAPIER ROAD MOAWHANGO TAIHAPE | Western | MOAWHANGO | 2024-09-25 | 9:03 | 2024-09-25 | 13:33 | 0.08084 | 0.00030349 | 110 | 29301 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install poles for new regulator site 16179/2 new ABS 16179 installed fuses /4 links /6 connect on the source side, change X arms on TX pole X2864 install stay on pole | .
2437 |  | JE24033093 | 387 WORTLEY ROAD WAIONGANA INGLEWOOD | Western | LEPPERTON | 2024-09-25 | 9:36 | 2024-09-25 | 15:43 | 0.036519 | 9.9323e-05 | 36 | 13237 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace Tx poles 1291 , Tx 1353 | .
2438 |  | JE24033094 | Rangiwaea Island | Eastern | MATAKANA RD | 2024-09-25 | 9:45 | 2024-09-25 | 12:19 | 0.0091574 | 6.0697e-05 | 22 | 3319 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT Remedial works required - Matakana Rd 300807774 â€“ Poles 202029 to 202030 - Conductor out of sag â€“ Resag required | .
2439 |  | JE24033122 | 67 QUEEN STREET WAITARA WAITARA | Western | BROWNE ST | 2024-09-25 | 9:31 | 2024-09-25 | 15:01 | 0.00091055 | 2.759e-06 | 1 | 330 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace TX 4619T like for like. WWTP Waitara West Queen Str. Email attached to negotiate new date. | .
2440 |  | JE24033223 | 1205 WIREMU ROAD OPUNAKE OPUNAKE | Western | IHAIA RD | 2024-09-25 | 9:16 | 2024-09-25 | 15:21 | 0.0040349 | 1.1036e-05 | 4 | 1462 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace xarm 712772, 712776, 712786, 712775. remove conductor from poles 712789 and 712787 | .
2441 |  | JE24035566 | TIRAUMEA | Western | TIRAUMEA | 2024-09-25 | 10:46 | 2024-09-25 | 11:24 | 0.0030884 | 8.001e-05 | 29 | 1119 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Swapped customer phase over to restore power, will return to complete full repairs 25/09 - Lines were isolated at ABS's V73 & V76 to repair broken jumper at Tfr T9/237. | .
2442 |  | JE24035661 | PARK RD | Western | PARK RD | 2024-09-25 | 9:40 | 2024-09-25 | 15:25 | 0.0047528 | 1.3795e-05 | 5 | 1723 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: Tfr T771 CAUSE: De4fective Temp generation (stage details when used): n PERFORMANCE DETAIL DNO (number or state no): n Circuit patrolled & type: n Weather (wind/rain): calm Follow up required (select advisory)?n Additional fault restoration comments: Job was not at Tfr T1109 but at customers other Tfr site, Tfr T771 was replaced due to been defective | .
2443 |  | JE24035695 | BROWNE ST | Western | BROWNE ST | 2024-09-25 | 10:01 | 2024-09-25 | 12:13 | 0.020366 | 0.0001545 | 56 | 7382 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB F11 Protection flags (nil where none): Nil CAUSE: Broken binders Location: Pole 744695 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F2, not patrolled. Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? no Additional fault restoration comments: Broken binders found during isolation of NAPA 112657. Lines isolated and binders replaced. 3 x binders SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2444 |  | JE24035741 | COROMANDEL SUB - KAPANGA RD - SEC 13198 | Eastern | KAPANGA ROAD | 2024-09-25 | 13:27 | 2024-09-25 | 17:04 | 0.077746 | 0.00035867 | 130 | 28179 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV Sec 13198 Protection flags (nil where none): E/F ,C Phase, CAUSE: Duck Strike Location: Pole 267077 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Calm LFI (Y/N + Comments): Yes Follow up Required (select advisory)? Additional fault restoration comments: Squirrel Conductor Failed when Duck hit the lines. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2445 |  | JE24035753 | DYERVILLE | Western | DYERVILLE | 2024-09-25 | 14:36 | 2024-09-25 | 15:38 | 0.0023985 | 3.8625e-05 | 14 | 869 | Unplanned | WILDLIFE - BIRD | Fuses Location: 7395 No. Fuses: 2 Fuse Amp Size:10A TIME CLOSED: 15:38 Cause: Bird Strike Weather (wind/rain):calm Follow up required (select advisory)?n Spur line patrolled 2R used for replacement barrel | .
2446 |  | JE24035760 | ARATAKI | Eastern | ARATAKI | 2024-09-25 | 13:30 | 2024-09-25 | 13:36 | 0.017422 | 0.0028252 | 1024 | 6315 | Unplanned | HUMAN ERROR - POTENTIAL SWITCHING ERROR | Unplanned outage for Non outage NAPA 113437 due to switching error. Safety manager 1406593 | .
2447 |  | JE24035778 | switch_10105 | Western | AOKAUTERE | 2024-09-25 | 16:58 | 2024-09-25 | 18:36 | 0.004623 | 4.6902e-05 | 17 | 1676 | Unplanned | VEGETATION - INSIDE ZONE | Customer advised Faultman of lines in the trees, line was isolated at ABS 10105 so tree can be removed from lines. | .
2448 |  | JE24030814 | 30 TOWER ROAD MATAMATA MATAMATA | Eastern | TAINUI ST | 2024-09-24 | 15:15 | 2024-09-24 | 15:19 | 0.0014226 | 0.00041936 | 152 | 516 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Secondary testing of relays to commission AUFLS scheme. Access to CB 2 and 7 to perform CB opening times test. | .
2449 |  | JE24032064 | 5 CORBETT DRIVE TE PUNA TAURANGA | Eastern | WAIPUNA | 2024-09-24 | 13:01 | 2024-09-24 | 14:32 | 0.0068061 | 7.4492e-05 | 27 | 2467 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Linkbox maintenance at SD3-059 | .
2450 |  | JE24032427 | 9 TIAKITAHUNA ROAD TIAKITAHUNA PALMERSTON NORTH | Western | BAINESSE | 2024-09-24 | 8:31 | 2024-09-24 | 13:48 | 0.074387 | 0.00023451 | 85 | 26962 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Change poles and crossarms P28327 dble pole; P28328; P45243; P45242 crossarm only reconductoring between poles from P28327 to P45242 | .
2451 |  | JE24032533 | 14 MOORE STREET FEATHERSTON FEATHERSTON | Western | REVANS ST | 2024-09-24 | 9:47 | 2024-09-24 | 15:43 | 0.20025 | 0.00056283 | 204 | 72583 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | change 11kv arms between 814247 & 820016, 813925 & 798616 | .
2452 |  | JE24032567 | 1254 BRUNSWICK ROAD BRUNSWICK WANGANUI | Western | BRUNSWICK | 2024-09-24 | 10:00 | 2024-09-24 | 15:27 | 0.018976 | 5.7938e-05 | 21 | 6878 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 2 X Defected TX Poles Y167- 782422 & Y309 - 782444 | .
2453 |  | JE24032571 | 594 MAUNGARANGI ROAD PAENGAROA TE PUKE | Eastern | MANGOREWA | 2024-09-24 | 8:51 | 2024-09-24 | 13:17 | 0.039617 | 0.00014898 | 54 | 14360 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv/400vt poles 230048,230049,230051 & 230052. Replace 11kv cross arms @ pole 230050. | .
2454 |  | JE24032608 | 298 BAKER ROAD MANAWARU TE AROHA | Eastern | MAUNGAKAWA ROAD | 2024-09-24 | 9:07 | 2024-09-24 | 13:44 | 0.015298 | 5.5179e-05 | 20 | 5545 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 1 x HT pole and HT arms at 7 sites | .
2455 |  | JE24032616 | 3178 MOUNTAIN ROAD MIDHIRST STRATFORD | Western | CLOTON RD NORTH | 2024-09-24 | 11:04 | 2024-09-24 | 14:50 | 0.012471 | 5.5179e-05 | 20 | 4520 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re-install 11kV ABS 5586 on Pole 740727. ABS currently on Pole jump jumpered straight through after Car Vs Pole incident. This will remove DNO 2407003. install stay anchor. | .
2456 |  | JE24032617 | 558 DOUGLAS NORTH ROAD DOUGLAS STRATFORD | Western | HUIROA | 2024-09-24 | 9:01 | 2024-09-24 | 14:15 | 0.0060774 | 1.9313e-05 | 7 | 2203 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | asplundh to remove trees between poles 759548 to 759553 | .
2457 |  | JE24032689 | 699 MASTERTON STRONVAR ROAD WERAITI MASTERTON | Western | WERAITI | 2024-09-24 | 9:16 | 2024-09-24 | 11:41 | 0.00080084 | 5.5179e-06 | 2 | 290 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Isolation for Vegetation cutting pole 827105 - 827106 Work completed but no job created due to EMAP error, Fuses 11485 Opened, SCADA notified | .
2458 |  | JE24032692 | 432 MASTERTON STRONVAR ROAD WERAITI MASTERTON | Western | WERAITI | 2024-09-24 | 12:01 | 2024-09-24 | 14:11 | 0.0007165 | 5.5179e-06 | 2 | 260 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Isolation for Vegetation cutting pole 827159 - 827160 | .
2459 |  | JE24032750 | 1 TIROHANGA ROAD MATAKANA ISLAND TAURANGA | Eastern | MATAKANA RD | 2024-09-24 | 8:52 | 2024-09-24 | 12:54 | 0.13162 | 0.00054352 | 197 | 47705 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT Remedial works required - Matakana Rd â€“ Pole 202071 - Conductors on DOH out of sag â€“ Poles 202011 to 202012 - Conductors out of sag, conductor full of joints - Pole Y0159 - Conductor out of sag â€“ Poles 201763- Out of sag | .
2460 |  | JE24032837 | 1 PORTSIDE DRIVE MOUNT MAUNGANUI TAURANGA | Eastern | HULL RD | 2024-09-24 | 3:04 | 2024-09-27 | 5:04 | 0.036599 | 0.00033659 | 61 | 13265 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Create 11kV cable-break (X)2 at poles 213804 & 213806. Replace 11kv bus-coupling and rust repairs at SD switchgear SC4-819>825. Reinstate cable-breaks. | .
2461 |  | JE24033921 | 84 TANIWHA PLACE BETHLEHEM TAURANGA | Eastern | WAIROA | 2024-09-24 | 9:22 | 2024-09-24 | 11:24 | 0.012955 | 0.00048282 | 104 | 4695 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Linkbox maintenance at TD3-285 | .
2462 |  | JE24034167 | 2970 Old Taupo Road Tokoroa | Eastern | OLD CAMBRIDGE RD | 2024-09-24 | 9:46 | 2024-09-24 | 17:21 | 0.033894 | 7.4492e-05 | 27 | 12285 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace KINMAR036 with new Double 15.5m Pole, Remove LV Circuit between Poles 483696 & KINMAR036, Install a 33kV Crucifix and terminate 3 x 1c 1000mm2 Al XPLE cable and complete cable testing. Leave cable break between 33KV links and crucifix, earth cables at crucifix | .
2463 |  | JE24035289 | 62 TAONUI ROAD AORANGI FEILDING | Western | BUNNYTHORPE | 2024-09-24 | 9:31 | 2024-09-24 | 13:21 | 0.059778 | 0.00025934 | 94 | 21667 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace Hv xarms on taonui and reids line east | .
2464 |  | JE24035353 | STATION RD | Eastern | STATION RD | 2024-09-24 | 8:24 | 2024-09-24 | 11:15 | 0.0014145 | 8.2769e-06 | 3 | 513 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses FC2170 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 11:15 Cause: Bird Strike Weather (wind/rain): Windy Follow up required (select advisory)? | .
2465 |  | JE24035418 | TIKORANGI | Western | TIKORANGI | 2024-09-24 | 10:59 | 2024-09-24 | 15:21 | 0.015912 | 6.0697e-05 | 22 | 5767 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: Fuses 5209 CAUSE: LIGHTNING Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): N/A Circuit patrolled & type: F4. Not patrolled. Weather (wind/rain): Rain/Lightning Follow up required (select advisory)? No Additional fault restoration comments: FAULTY TX, NEEDS TO BE REPLACED Spurr line that comes down to LV TX 4375 63A LV OH Pole fuse Cause Lightening At 4809T transformer replaced 1 x 30kVA 3 Ø 11kV/400V 3 x 3A HV fuses At 5132T transformer replaced 1 x 15kVA 3 Ø 11kV/400V 3 x 2A HV fuses | .
2466 |  | JE24035419 | WAIONE | Western | WAIONE | 2024-09-24 | 11:13 | 2024-09-24 | 16:46 | 0.067467 | 0.00042212 | 114 | 24454 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Voltage & Device ID: 11kV REC V27 Protection flags (nil where none): B & C ph O/C & E/F Weather (wind/rain): very windy Follow up required (select advisory): n LFI Activation: N Lines were patrolled and sectionalized and no fault was found. | .
2467 |  | JE24035432 | EDITH ST | Western | EDITH ST | 2024-09-24 | 11:14 | 2024-09-24 | 18:33 | 0.031007 | 0.00040833 | 74 | 11239 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC C223 Protection flags (nil where none): A ph E/F CAUSE: Multiple floating conductors & broken cross arm Location: poles 359023 & 834395 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: cursory Weather (wind/rain): very windy LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Line isolated at Fuses 8181 and 7745 to make repairs SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2468 |  | JE24035433 | BROOKLANDS | Western | BROOKLANDS | 2024-09-24 | 11:14 | 2024-09-24 | 18:27 | 0.052597 | 0.00012139 | 44 | 19064 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: I23, CB found to be open on arrival Protection flags (nil where none): na CAUSE: Unknown Location: na Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): windy LFI (Y/N + Comments): n Follow up Required (select advisory)? Additional fault restoration comments: Line patrolled, no fault found SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2469 |  | JE24035448 | CLAREVILLE SUB - CB C831 | Western | SOMERSET RD | 2024-09-24 | 11:43 | 2024-09-24 | 18:56 | 0.07593 | 0.00077251 | 278 | 27521 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB C831 Protection flags (nil where none): O/C CAUSE: Twisted LV lines over HV lines Location: 823922 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: cursory Weather (wind/rain): Very windy LFI (Y/N + Comments): Y - pole 823859 Follow up Required (select advisory)? n Additional fault restoration comments: Two faults were repaired under different AP's 1. HV Lines twisted over other HV Lines on the main line. (Repaired first to get the bulk of the ICP's Power back on) 2. Replace original fault of the Broken Pole at 823923 Full Power restored via Fuses 7630 at 18:55 | .
2470 |  | JE24035461 | PARK RD | Western | PARK RD | 2024-09-24 | 12:06 | 2024-09-24 | 19:23 | 0.085588 | 0.00019589 | 71 | 31022 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: 7607 No. Fuses: 2 Fuse Amp Size: 15 Amp TIME CLOSED: 19:23 Cause: Wind Weather (wind/rain): Windy Follow up required (select advisory)? No | .
2471 |  | JE24035466 | TE ARAKURA | Western | TE ARAKURA | 2024-09-24 | 12:19 | 2024-09-24 | 14:11 | 0.064367 | 0.00057386 | 208 | 23330 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC D77/2 Protection flags (nil where none): A & B ph E/F CAUSE: Old dead tree fallen on lines Location: Pole P38139 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: cursory Weather (wind/rain): very windy LFI (Y/N + Comments): N Follow up Required (select advisory)? n Additional fault restoration comments: Faultman removed old dead tree from lines with hot sticks at pole P38139. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2472 |  | JE24035479 | HUKANUI | Western | HUKANUI | 2024-09-24 | 12:48 | 2024-09-24 | 15:51 | 0.028875 | 0.00015726 | 57 | 10466 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: S9 No. Fuses: 2 Fuse Amp Size:25A TIME CLOSED: 15:51 Cause: lineclash Weather (wind/rain): Windy Follow up required (select advisory)?n 2R used for patrol | .
2473 |  | JE24035496 | STRATHMORE | Western | STRATHMORE | 2024-09-24 | 13:03 | 2024-09-24 | 16:01 | 0.0048807 | 3.0349e-05 | 11 | 1769 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 5453 No. Fuses: 2 Fuse Amp Size: 8A TIME CLOSED: 15:40 Cause: LIGHTNING Weather (wind/rain): WINDY Follow up required (select advisory)? Full Power Other TX reload/relivened, no calls TX 33379T 2X2A CLOSED 16:01 TX 2497T 2X2A CLOSED 15:24 | .
2474 |  | JE24035497 | MOUNTAIN RD | Western | MOUNTAIN RD | 2024-09-24 | 15:52 | 2024-09-24 | 17:10 | 0.0047384 | 6.0697e-05 | 22 | 1717 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Raised Job to Replace Insulator at ABS 5637 - Emergency Shutdown Required - Organised for 24/09/24 During isolation for NAPA113656 it was noted that ABS 5637 had a broken insulator. After the NAPA replacement of ABS 5586 was done the ABS 5637 was isolated and repaired. | .
2475 |  | JE24035506 | LINTON | Western | LINTON | 2024-09-24 | 13:23 | 2024-09-24 | 18:10 | 0.0023734 | 8.2769e-06 | 3 | 860 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: H116 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 18:10 Cause: Wind Weather (wind/rain): very windy Follow up required (select advisory)?n | .
2476 |  | JE24035533 | EDITH ST | Western | EDITH ST | 2024-09-24 | 14:39 | 2024-09-24 | 16:30 | 0.00091643 | 8.2769e-06 | 3 | 332 | Unplanned | VEGETATION - OUTSIDE ZONE | Fuses Location: 7714 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 16:29 Cause: Branches on line at pole 836406 Weather (wind/rain): wind Follow up required (select advisory)?n | .
2477 |  | JE24035539 | NGAUMUTAWA RD | Western | NGAUMUTAWA RD | 2024-09-24 | 14:44 | 2024-09-29 | 13:40 | 0.00091827 | 1.1036e-05 | 2 | 333 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Isolation: 11kV Fuses 7050 CAUSE: Cable burnt off the termination at TX T1239 Temp generation (stage details when used): Yes, Generator in service at 17:15 PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Windy Follow up required (select advisory)? Yes Additional fault restoration comments: HV Cable burnt off the termination at Transformer T1239 Isolation carried out at Fuses 7050 (Open, removed & Tagged) Generator connected to Transformer T1239 29/09/2024 HV Cable termination repaired at TX T1239 (Very old cable and the cause was due to deterioration) Generator removed from service at 13:25 at TX T1239 Full Power restored via closing Fuses 7050 at 13:40 This was for the Bread works factory. | .
2478 |  | JE24035545 | KATIKATI | Eastern | KATIKATI | 2024-09-24 | 14:54 | 2024-09-24 | 18:29 | 0.0029699 | 1.3795e-05 | 5 | 1076 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: SB1-074 No. Fuses: 2 Fuse Amp Size: 10 Amp TIME CLOSED: 18:29 Cause: Wind Weather (wind/rain): Windy Follow up required (select advisory)? No | .
2479 |  | JE24035553 | RAWHITIROA | Western | RAWHITIROA | 2024-09-24 | 13:01 | 2024-09-24 | 15:10 | 0.00035627 | 2.759e-06 | 1 | 129 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 2310T No. Fuses: 2 Fuse Amp Size: 2 TIME CLOSED: 15:10 Cause: Lightning Weather (wind/rain):lightning Follow up required (select advisory)?N | .
2480 |  | JE24035558 | MANGOREWA | Eastern | MANGOREWA | 2024-09-24 | 16:50 | 2024-09-24 | 20:34 | 0.0098911 | 4.4143e-05 | 16 | 3585 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV FABS SE6-043 Protection flags (nil where none): Fuses operated. CAUSE: Deterioration Location: Pole 221 763 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Windy LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: HV Lines down at Pole 221 763 (on the ground) Fuses had operated at SE6-043 Isolation & Earthed the work site and repairs carried out under AP Full Power restored at 20:34 | .
2481 |  | JE24035579 | RUAWHATA | Western | RUAWHATA | 2024-09-24 | 16:18 | 2024-09-24 | 20:55 | 0.010713 | 3.8625e-05 | 14 | 3883 | Unplanned | VEGETATION - OUTSIDE ZONE | Fuses Location: Q84 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 20:55 Cause: Tree has come down and clipped HV line, no damage to network, by pole P19887 Weather (wind/rain): windy, rain Follow up required (select advisory)?n | .
2482 |  | JE24035584 | PURANGI | Eastern | PURANGI | 2024-09-24 | 16:33 | 2024-09-24 | 18:37 | 0.0020578 | 1.6554e-05 | 6 | 746 | Unplanned | HUMAN ERROR - LOAD SHEDDING - NETWORK LOAD | Fuses Location: FC4172 No. Fuses: 1 Fuse Amp Size: 3 Amp TIME CLOSED: 18:37 Cause: In rush current Weather (wind/rain): Calm Follow up required (select advisory)? No | .
2483 |  | JE24035639 | BROOKLANDS | Western | BROOKLANDS | 2024-09-24 | 20:09 | 2024-09-25 | 9:30 | 0.09353 | 0.00012139 | 44 | 33900 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | Notes Line to be patrolled in day light hours, most of the line is cross-country unable to patrol at night REGULATORY INFORMATION Voltage & Device ID: 11kV CB I23 Protection flags (nil where none): None CAUSE: Branch on lines Location: Between poles p10250 & P09420 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: cursory Weather (wind/rain): windy LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Line was patrolled and sectionalized and branch on the line was removed. 2R left open for Tree contractor needed to remove the tree. | .
2484 |  | JE24035641 | HAURAKI RD | Eastern | HAURAKI RD | 2024-09-24 | 17:56 | 2024-09-24 | 21:26 | 0.019105 | 9.1046e-05 | 33 | 6925 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: 11kV Sw/Gear 14497/1 Location: TX TC2543 CAUSE: Deterioration Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Rain & wind. Follow up required (select advisory)? No Additional fault restoration comments: DDO's failed at Transformer TC2543 ( All three to be replaced & arm ) Isolation required on the 11kV main line at KPE S/S CB 3 Unable to Isolate at Sw/Gear 14497/1 due to having no access. (secure site) Isolation and earthed the main line and then carried out the repairs at Transformer TC2543 under AP 5612 Three DDO's replaced and the arm. Full Power restored at 22:41 Field Switcher confirmed full power on site at TX TC2543. | .
2485 |  | JE24031340 | 223 LOWER BALL ROAD KAKARAMEA PATEA | Western | MANUTAHI | 2024-09-23 | 13:00 | 2024-09-23 | 15:00 | 0.00033098 | 2.759e-06 | 1 | 120 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace TX 5529E. Critical customer comms attached. | .
2486 |  | JE24032167 | 279 MAKINO ROAD FEILDING FEILDING | Western | MAKINO | 2024-09-23 | 9:16 | 2024-09-23 | 12:41 | 0.022099 | 0.0001076 | 39 | 8010 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles P17654 and P17652. | .
2487 |  | JE24032400 | 153 RICHARDSONS LINE MILSON PALMERSTON NORTH | Western | BUNNYTHORPE | 2024-09-23 | 9:03 | 2024-09-23 | 11:31 | 0.002858 | 1.9313e-05 | 7 | 1036 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace leaking TX T6/521 & replace TX arms | .
2488 |  | JE24032418 | 441 HOT WATER BEACH ROAD WHENUAKITE WHITIANGA | Eastern | COROGLEN | 2024-09-23 | 8:09 | 2024-09-23 | 11:43 | 0.0070922 | 3.3108e-05 | 12 | 2571 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace defected 11kv pole W1380 and hardware. | .
2489 |  | JE24032611 | 22A SHARP ROAD AONGATETE KATIKATI | Eastern | WILLS RD | 2024-09-23 | 8:31 | 2024-09-23 | 17:03 | 0.55735 | 0.001145 | 415 | 202015 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 1: Test HV UG Cable from: 422869/422283 to 201142; 201142 to 201139; Link Box to 201140; 201140 to 14969/2 2: Remove ABS SB1-012 3: Remove ABS SB1-063, install ENTEC LBS 14965 4: Install RMU 14969 5: Remove Fuses SB1-085 6: Term HV UG Cable from 422869/422283 to 14969/4 7: Term HV UG Cable from 201139 to 14969/1 8: Run new HV UG Cable from 201142 to 14969/3 9: Drop UG Cable from 201140, joint to new HV UG Cable, term into 14969/2 Refer additional information for items 10, 11 & 12 | .
2490 |  | JE24034874 | TE KIRI | Western | TE KIRI | 2024-09-23 | 9:35 | 2024-09-24 | 14:22 | 0.005063 | 8.2769e-06 | 3 | 1835 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: Transformer T7029 CAUSE: Lightning Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: Weather (wind/rain): Follow up required (select advisory)? Additional fault restoration comments: Failed Re-Load Re-Liven, Transformer Fuses Isolated 09:35 Ready to be replaced under 2R Note: See Child Job JE24035181 for Fuses TA959 which blew when closing transformer T7029 Fuses 0272740455 Nolen 1 x 15kVA 3 Ø 11kV/400V 3 x 2A HV fuses | .
2491 |  | JE24034968 | OTAKEHO | Western | OTAKEHO | 2024-09-23 | 9:16 | 2024-09-24 | 15:41 | 0.010072 | 5.5179e-06 | 2 | 3651 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: Transformer T5475 Fuses CAUSE: Lightning Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): N/A Circuit patrolled & type: F4. Not patrolled Weather (wind/rain): Rain/lightening Follow up required (select advisory)? No Additional fault restoration comments: Tried to Re-Load/Re-Liven at 09:15 - Fuses blew, Isolated Ready for Replacement under the 2R 1 x 50kVA 3 Ø 11kV/400V 3 x 6A HV fuses | .
2492 |  | JE24034972 | RAETIHI | Western | RAETIHI | 2024-09-23 | 14:04 | 2024-09-23 | 15:30 | 0.00047629 | 5.5179e-06 | 2 | 173 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Blown Transformer X4063 due to Lightning strike - To be replaced under 2R Isolated at TFR X4063 Fuses TFR Replaced, Full power restored | .
2493 |  | JE24034973 | AUROA | Western | AUROA | 2024-09-23 | 11:15 | 2024-09-23 | 20:11 | 0.0014787 | 2.759e-06 | 1 | 536 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: 5497E CAUSE: Lightning Follow up required (select advisory)? Additional fault restoration comments: Replaced blown 50/11/3ph Transformer 5497E | .
2494 |  | JE24035002 | PARAPARA | Western | PARAPARA | 2024-09-23 | 11:15 | 2024-09-23 | 13:00 | 0.0014473 | 1.3795e-05 | 5 | 525 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Faulty Transformer needs replacing Isolated at TFR 1953W Fuses TFR Replaced, full power restored | .
2495 |  | JE24035003 | TE KIRI | Western | TE KIRI | 2024-09-23 | 11:27 | 2024-09-23 | 19:12 | 0.0076972 | 1.6554e-05 | 6 | 2790 | Unplanned | LIGHTNING - LIGHTNING STRIKE | ***Defective TX to be replaced under 2R**** Isolation: T7360 CAUSE: Lightning Temp generation (stage details when used): Weather (wind/rain): Lightning Follow up required (select advisory)? Additional fault restoration comments: Replaced 50/11/3ph Transformer T7360 | .
2496 |  | JE24035041 | MANAIA | Western | MANAIA | 2024-09-23 | 11:06 | 2024-09-23 | 16:46 | 0.00093051 | 5.5179e-06 | 1 | 337 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: Fuses MA550 CAUSE: Lightning Strike Notes: Replaced Set of Broken Fuse Holders & Bases at Fuses M4295 - relates to JE24035147 2R left open as other work is required down Spur line under the 2R PERFORMANCE DETAIL DNO (number or state no): N/A Circuit patrolled & type: F4. Npt patrolled Weather (wind/rain): Rain/lightning Follow up required (select advisory)? Additional fault restoration comments: No 1 x 50kVA 3 Ø 11kV/400V 1 x 6A HV fuse Replace crossarms, repalced 50kva TX 5247E | .
2497 |  | JE24035042 | MANAIA | Western | MANAIA | 2024-09-23 | 9:17 | 2024-09-23 | 11:03 | 0.0052326 | 4.9661e-05 | 18 | 1897 | Unplanned | LIGHTNING - LIGHTNING STRIKE | BROKEN DDO'S TO BE REPLACED UNDER 2R DDOs Replaced, Fuses MA550 Closed 11:02 | .
2498 |  | JE24035084 | Recloser 6286, SH3 Uriti | Western | MAIN RD MOTONUI | 2024-09-23 | 5:20 | 2024-09-23 | 13:18 | 0.17702 | 0.00068698 | 178 | 64163 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 6286 Protection flags (nil where none): NIL - SCADA Coms failure CAUSE: Branch on Lines Location: Pole 762883- 762884 Temp generation (state details when used): NIL PERFORMANCE DETAIL DNO (number or state No): NIL Circuit patrolled and type: 11kv Cursory Weather (wind/rain): Stormy - Fine LFI (Y/N + Comments): Yes SW/Gear 12590/3 Follow up Required (select advisory)? NIL Additional fault restoration comments: Branch on lines between pole 762883 - 762884, tree cut under AP no damage to asset SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2499 |  | JE24035095 | APITI | Western | APITI | 2024-09-23 | 6:53 | 2024-09-23 | 9:31 | 0.0039077 | 2.4831e-05 | 9 | 1416 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Fuses P26 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 09:30 Cause: Lightning Weather (wind/rain): Storm Yesterday Follow up required (select advisory)? Confirmed the other jobs down stream of this have been confirmed to have full power restored | .
2500 |  | JE24035114 | PARAPARA | Western | PARAPARA | 2024-09-23 | 9:58 | 2024-09-23 | 17:25 | 0.0047174 | 5.242e-05 | 19 | 1710 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Broken HV fuse bases at transformer X2865 due to lightning strike. Lines isolated at ABS 821 2 x HV fuse bases replaced | .
2501 |  | JE24035116 | Recloser 525 | Western | MAKIRIKIRI | 2024-09-23 | 7:53 | 2024-09-24 | 13:45 | 0.14772 | 0.00040005 | 145 | 53542 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: Rec 2995/2 & Rec 575 Protection flags (nil where none): O/C A, B & C - E/F, O/C A & C CAUSE: Tree through lines & Fault current Location: Poles 784786 & 784744 lines down due to fault current, Broken pole and lines due to tree past Links 705 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): wind, rain LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Isolated at ABS 1493 & Links 1013 - Lines down fixed at Pole 784786 & 784744 Fixed Isolated at Links 705 - Pole and lines still have to be replaced/fixed - Leave 2R open 24/09 - Pole been replaced & lines repaired | .
2502 |  | JE24035127 | MATAPU | Western | MATAPU | 2024-09-23 | 8:36 | 2024-09-23 | 12:52 | 0.0062576 | 2.4831e-05 | 9 | 2268 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Fuses 6924 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 12:46 Cause: Lightning Weather (wind/rain): Storm Yesterday Follow up required (select advisory)? Also See Child Job JE24035127 for Transformer K4260 Notes. Completed under this 1R | .
2503 |  | JE24035129 | RAETIHI | Western | RAETIHI | 2024-09-23 | 8:38 | 2024-09-23 | 14:26 | 0.00095996 | 2.759e-06 | 1 | 348 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Transformer X1960 No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 14:25 Cause: Lighting Weather (wind/rain): Fine Follow up required (select advisory)? Lee Jackson has attended waiting for him to be assigned and onsite to complete job. | .
2504 |  | JE24035168 | WESTMERE PEAT ST | Western | WESTMERE PEAT ST | 2024-09-23 | 12:46 | 2024-09-23 | 14:16 | 0.0012287 | 1.3795e-05 | 5 | 445 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Broken DDO to TFR X2881 at pole 782019 Isolated at Fuses 1130 DDO to TFR X2881 Replaced, full power restored | .
2505 |  | JE24035172 | TIKORANGI | Western | TIKORANGI | 2024-09-23 | 10:05 | 2024-09-23 | 16:15 | 0.0020415 | 5.5179e-06 | 2 | 740 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Fuses 5177 No. Fuses: 3 Fuse Amp Size: 3A TIME CLOSED: 16:15 Cause: LIGHTNING Weather (wind/rain): CALM Follow up required (select advisory)? Need Neitana onsite before closing | .
2506 |  | JE24035180 | AUROA | Western | AUROA | 2024-09-23 | 10:37 | 2024-09-23 | 15:06 | 0.00074227 | 2.759e-06 | 1 | 269 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Fuses 8647 (NOT Transformer Fuses M1115) No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 15:06 Cause: Lightning Weather (wind/rain): Storm Yesterday Follow up required (select advisory)? Notes: Outage logged to house, not the cow shed. Cow Shed is fed off Transformer 5485E | .
2507 |  | JE24035182 | RAETIHI | Western | RAETIHI | 2024-09-23 | 10:51 | 2024-09-23 | 12:51 | 0.00032994 | 2.759e-06 | 1 | 120 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: X1073 No. Fuses: 3 Fuse Amp Size: 2 TIME CLOSED: 12:50 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n | .
2508 |  | JE24035189 | PUTORINO | Western | PUTORINO | 2024-09-23 | 11:30 | 2024-09-23 | 13:40 | 0.016897 | 0.00050489 | 183 | 6125 | Unplanned | THIRD PARTY INTERFERENCE - OVERHEAD CONTACT | Cause: 3rd Part damage - Tractor hit lines What was replaced? 2x63A fuses, carrier, length of conductor Where was it replaced (pole/TX/pillar box)? Pole Is 2R required? Y 2R Y - What is the timeframe for repairs? Complete Additional Info: Repaired under NDR Lines not live on ground HV isolated for safety - Discovered was LV - LV Fuses Isolate at Transformer X1009 | .
2509 |  | JE24035208 | RUAPEHU | Western | RUAPEHU | 2024-09-23 | 12:20 | 2024-09-23 | 14:58 | 0.00043522 | 2.759e-06 | 1 | 158 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: X3074 No. Fuses: 2 Fuse Amp Size: 8 TIME CLOSED: 14:58 Cause: lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n 2R required | .
2510 |  | JE24035210 | TATUANUI | Eastern | TATUANUI | 2024-09-23 | 12:32 | 2024-09-23 | 13:50 | 0.001074 | 1.3795e-05 | 5 | 389 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Trf TC2464 No. Fuses: 3 Fuse Amp Size: 3A and LV 63 A pole Fuse TIME CLOSED: 13:50 Cause: Lightning Weather (wind/rain): Rain Follow up required (select advisory)? No Still LV issues being investigated | .
2511 |  | JE24035211 | AUROA | Western | AUROA | 2024-09-23 | 15:36 | 2024-09-24 | 13:33 | 0.0036332 | 2.759e-06 | 1 | 1317 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: M1048 Fuses CAUSE: Blown TX, Lightning, being replaced Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): N/A Circuit patrolled & type: F4. not patrolled Weather (wind/rain): Rain/lightning Follow up required (select advisory)? No Additional fault restoration comments: 1 x 15kVA 3 Ø 11kV/400V 3 x 2A HV fuses | .
2512 |  | JE24035216 | LEEDSTOWN 22KV | Western | LEEDSTOWN 22KV | 2024-09-23 | 17:16 | 2024-09-23 | 19:01 | 0.00086535 | 8.2769e-06 | 3 | 314 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Cause: Lightning What was replaced? 15kVA/22/3phase Transformer Where was it replaced (pole/TX/pillar box)? Z164 Is 2R required? N 2R Y - What is the timeframe for repairs? Complete Additional Info: Isolated, transformer has been replaced | .
2513 |  | JE24035219 | DUTHIE RD | Western | DUTHIE RD | 2024-09-23 | 13:24 | 2024-09-23 | 16:57 | 0.031721 | 0.00014898 | 54 | 11498 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 2 Protection flags (nil where none): Nil CAUSE: Vehicle V pole Location: 843497 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4 at the accident scene Weather (wind/rain): Rain LFI (Y/N + Comments): nil Follow up Required (select advisory)? NDR to follow Additional fault restoration comments: 11m pole replaced 1 x double HV pin arm SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2514 |  | JE24035275 | MANAIA | Western | MANAIA | 2024-09-23 | 15:02 | 2024-09-23 | 17:06 | 0.011627 | 9.3805e-05 | 34 | 4214 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 8 Protection flags (nil where none): Nil CAUSE: Broken Fuse base Location: M4240 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4 not patrolled Weather (wind/rain): Rain/lightning LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: 3 x Fuse base replaced SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2515 |  | JE24035286 | RUAPEHU | Western | RUAPEHU | 2024-09-23 | 12:21 | 2024-09-23 | 15:25 | 0.00050857 | 2.759e-06 | 1 | 184 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 4027W No. Fuses: 3 Fuse Amp Size:3 TIME CLOSED: 15:25 Cause: lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n | .
2516 |  | JE24035288 | RUAPEHU | Western | RUAPEHU | 2024-09-23 | 12:20 | 2024-09-23 | 13:35 | 0.00020724 | 2.759e-06 | 1 | 75 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 2863 No. Fuses: 3 Fuse Amp Size:8 TIME CLOSED: 1335 Cause: lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n | .
2517 |  | JE24035305 | MAIN RD MOTONUI | Western | MAIN RD MOTONUI | 2024-09-23 | 17:44 | 2024-09-23 | 18:33 | 0.0097413 | 0.00019865 | 72 | 3531 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 5196 No. Fuses: 2 Fuse Amp Size: 20A TIME CLOSED: 18:32 Cause: Lightning Weather (wind/rain): Follow up required (select advisory)? | .
2518 |  | JE24035326 | COAST ROAD | Western | COAST ROAD | 2024-09-23 | 9:20 | 2024-09-23 | 9:38 | 0.0001935 | 1.1036e-05 | 4 | 70 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faultman tapped Tfr 7255P down 2 taps | .
2519 |  | JE24035360 | MATAPU | Western | MATAPU | 2024-09-23 | 17:51 | 2024-09-24 | 11:07 | 0.015895 | 4.4143e-05 | 16 | 5761 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: ABS KA743 CAUSE: Lightning Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): N/A Circuit patrolled & type: F4. Not patrolled. Weather (wind/rain): Rain/lightning Follow up required (select advisory)? No Additional fault restoration comments: Isolation at ABS KA743 due to not being able to maintain MADs with crane. 1 x 30kVA 3 Ø 11kV/400V transformer 3 x Fuse bases 3 x 3A HV fuses | .
2520 |  | JE24035423 | MAIN RD MOTONUI | Western | MAIN RD MOTONUI | 2024-09-23 | 18:00 | 2024-09-24 | 14:01 | 0.055902 | 0.0002152 | 78 | 20262 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: 4097T Fuses CAUSE: Lightning Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): N/A Circuit patrolled & type: F4. not patrolled Weather (wind/rain): Rain/Lightning Follow up required (select advisory)? No Additional fault restoration comments: Blown transformer requires replacement 1 x 30kVA 3 Ø 11kV/400V | .
2521 |  | JE24035807 | OKOROIRE | Eastern | OKOROIRE | 2024-09-23 | 10:01 | 2024-09-23 | 12:18 | 0.0034175 | 2.4831e-05 | 9 | 1239 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace transformer TC969 - Upgrade from 25KVA to 50KVA due to Loading/Voltage issues | .
2522 |  | JE24030819 | 40 HEWLETTS ROAD MOUNT MAUNGANUI TAURANGA | Eastern | NEWTON ST | 2024-09-22 | 8:46 | 2024-09-22 | 16:09 | 0.12068 | 0.00031452 | 114 | 43740 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV ABS SC4-660 with new ENTEC Sectionaliser 14869/2 and Links 14869/4 and SCADA commission. Remove 11kV cable from pole 214736 and join to new 3C 185mm cable connecting to new Links 14874 installed at pole 249549. ------------------------------------------------------------------------------------------------------------- 22/09/2024 NOC NOTE: When Power was turned OFF at 08:45 the Traffic Lights at a major intersection of Aerodrome Road & Hewletts Road were also not working. Unsure of who was suppose to organize a back up generator to run the Traffic lights for this planned outage. Field Switcher informed NOC and the Downer crew on site made a plan to run the traffic lights off of an inverter in the interim, while we could decide if the outage should go ahead or be cancelled. NOC tried calling the applicant on the NAPA application: Anthony Brill (Voicemail) Recipient: Sam Holloway picked up, not on site and part of the outage. Additional person: Here Hiha : Came up as this number is not valid. During this time NOC escalated this situation to Wayne Hosking who was on-call for 22/09/24 from 7am to 1pm NOC received a call from the Field Switcher stating that TSL had arrived on site with a generator to Power the traffic lights for the duration of the outage until 15:30. Overall it seems as if th | .
2523 |  | JE24034846 | MANGAWEKA | Western | MANGAWEKA | 2024-09-22 | 6:50 | 2024-09-22 | 9:10 | 0.0023262 | 1.6554e-05 | 6 | 843 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: 638 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 09:10 Cause: unknown Weather (wind/rain): windy Follow up required (select advisory)?n Line patrolled | .
2524 |  | JE24034853 | OLD CAMBRIDGE RD | Eastern | OLD CAMBRIDGE RD | 2024-09-22 | 9:42 | 2024-09-22 | 10:29 | 0.00064116 | 1.3795e-05 | 5 | 232 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: TC3106 No. Fuses: 1 Fuse Amp Size: 3 Amp TIME CLOSED: 10:28 Cause: Deterioration Weather (wind/rain): Slight wind. Follow up required (select advisory)? No | .
2525 |  | JE24034857 | STRATHMORE | Western | STRATHMORE | 2024-09-22 | 11:30 | 2024-09-22 | 13:32 | 0.0013417 | 1.1036e-05 | 4 | 486 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 3871T No. Fuses: 2 Fuse Amp Size: 2 TIME CLOSED: 13:31 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n | .
2526 |  | JE24034858 | CASTLEPOINT | Western | CASTLEPOINT | 2024-09-22 | 12:00 | 2024-09-22 | 13:30 | 0.0012347 | 1.3795e-05 | 5 | 448 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: T2835 No. Fuses: 1 Fuse Amp Size: (Fuse was just open and then closed back in) Size unknown TIME CLOSED: 13:29 Cause: Windy Weather (wind/rain): Windy Follow up required (select advisory)? No | .
2527 |  | JE24034860 | WAITOTARA | Western | WAITOTARA | 2024-09-22 | 12:28 | 2024-09-22 | 14:45 | 0.0011335 | 8.2769e-06 | 3 | 411 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: X687 No. Fuses: 2 Fuse Amp Size: 2 TIME CLOSED: 14:45 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n | .
2528 |  | JE24034861 | WAITOTARA | Western | WAITOTARA | 2024-09-22 | 12:35 | 2024-09-22 | 15:40 | 0.0015262 | 8.2769e-06 | 3 | 553 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: X631 No. Fuses: 3 Fuse Amp Size: 2 TIME CLOSED: 15:39 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n | .
2529 |  | JE24034867 | TE KIRI | Western | TE KIRI | 2024-09-22 | 13:05 | 2024-09-22 | 13:25 | 0.00039631 | 1.9313e-05 | 7 | 144 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Transformer T7170 No. Fuses: 3 Fuse Amp Size: 3A TIME CLOSED: 13:25 Cause: Lighting Weather (wind/rain): Rainy Follow up required (select advisory)? NIL | .
2530 |  | JE24034868 | GLOVER RD WEST | Western | GLOVER RD WEST | 2024-09-22 | 13:06 | 2024-09-22 | 14:09 | 0.15726 | 0.0033356 | 1209 | 57000 | Unplanned | LIGHTNING - LIGHTNING STRIKE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 9 Protection flags (nil where none): O/C A, B & C CAUSE: Lightning Location: na Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): Lightning LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Line patrolled after lightning storm SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2531 |  | JE24034870 | OTAKEHO | Western | OTAKEHO | 2024-09-22 | 13:07 | 2024-09-22 | 14:28 | 0.054939 | 0.00096012 | 348 | 19913 | Unplanned | LIGHTNING - LIGHTNING STRIKE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 6 Protection flags (nil where none): E/F, O/C B & C CAUSE: Lightning Location: na Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): Lightning LFI (Y/N + Comments): y flashing at Pole 717475 Follow up Required (select advisory)? n Additional fault restoration comments: Line patrolled after lightning storm, no fault found LFI flashing center phase onsite and outside phase on SCADA SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2532 |  | JE24034871 | PIHAMA | Western | PIHAMA | 2024-09-22 | 13:08 | 2024-09-22 | 15:47 | 0.00087435 | 8.2769e-06 | 3 | 317 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 5095E No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 15:39 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n Fuses Location: 6579 No. Fuses: 1 Fuse Amp Size: 8 TIME CLOSED: 15:47 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n | .
2533 |  | JE24034879 | TE KIRI | Western | TE KIRI | 2024-09-22 | 21:09 | 2024-09-23 | 15:36 | 0.0030546 | 2.759e-06 | 1 | 1107 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: T7113 Fuses CAUSE: Lightning Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): N/A Circuit patrolled & type: F4 Cursory patrolled Weather (wind/rain): Lightning Follow up required (select advisory)? No Additional fault restoration comments: 1 x 30kVA 3 Ø 11kV/400V transformer 3 x 3A HV fuses | .
2534 |  | JE24034880 | TE KIRI | Western | TE KIRI | 2024-09-22 | 22:01 | 2024-09-23 | 20:16 | 0.0036834 | 2.759e-06 | 1 | 1335 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: 5102E CAUSE: Lightning Weather (wind/rain): Heavy Rain / Windy Follow up required (select advisory)? Additional fault restoration comments: Replaced 15/11/3ph Transformer 5102E & 2x 2A HV fuse links | .
2535 |  | JE24034881 | IRIRANGI | Western | IRIRANGI | 2024-09-22 | 13:31 | 2024-09-22 | 16:51 | 0.002759 | 1.3795e-05 | 5 | 1000 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: X674 No. Fuses: 3 Fuse Amp Size: 2 TIME CLOSED: 16:50 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n Replaced 1 x barrel | .
2536 |  | JE24034883 | MATAPU | Western | MATAPU | 2024-09-22 | 13:34 | 2024-09-22 | 16:29 | 0.0033821 | 1.9313e-05 | 7 | 1226 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: K4035 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 16:28 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? | .
2537 |  | JE24034885 | AUROA | Western | AUROA | 2024-09-22 | 13:37 | 2024-09-22 | 16:00 | 0.0031487 | 2.2072e-05 | 8 | 1141 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: M1045 No. Fuses: 3 Fuse Amp Size: 6 TIME CLOSED: 15:59 Cause: lightning Weather (wind/rain): lightning Follow up required (select advisory)?n | .
2538 |  | JE24034893 | WESTMERE PEAT ST | Western | WESTMERE PEAT ST | 2024-09-22 | 13:56 | 2024-09-22 | 22:19 | 0.0013862 | 2.759e-06 | 1 | 502 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: X4298 No. Fuses: 3 Fuse Amp Size: 2Amp TIME CLOSED: 22:18 hrs Cause: Lightning Weather (wind/rain): Follow up required (select advisory)? | .
2539 |  | JE24034894 | INLAND COAST | Western | INLAND COAST | 2024-09-22 | 18:33 | 2024-09-23 | 13:01 | 0.012227 | 1.1036e-05 | 4 | 4432 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: Transformer 1149 Fuses CAUSE: Lightning Temp generation (stage details when used): Failed Re-Load Re-Liven, Replaced Transformer 1149 23/09/24. Used: 1x30kVA Transformer 3Phase 3x 3A HV Fuses 3x 63A 400V HRC Fuses PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: Weather (wind/rain): Follow up required (select advisory)? Additional fault restoration comments: | .
2540 |  | JE24034897 | DOUGLAS 33KV | Western | DOUGLAS 33KV | 2024-09-22 | 13:59 | 2024-09-22 | 15:01 | 0.14285 | 0.0024031 | 871 | 51776 | Unplanned | LIGHTNING - LIGHTNING STRIKE | REGULATORY INFORMATION Voltage & Device ID: CB 2762 Protection flags (nil where none): E/F, O/C CAUSE: Lightning Location: na Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): lightning LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: 33kV Line patrolled, no fault found supply restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Douglas & Strathmore Circuit that tripped: 2762 DTF (KM):na | .
2541 |  | JE24034898 | RANGIKURA | Western | RANGIKURA | 2024-09-22 | 13:59 | 2024-09-22 | 16:50 | 0.00142 | 8.2769e-06 | 3 | 515 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: X1784 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 16:50 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n | .
2542 |  | JE24034899 | 1490 SKEET ROAD, MANAIA | Western | AUROA | 2024-09-22 | 14:41 | 2024-09-23 | 16:38 | 0.012892 | 8.2769e-06 | 3 | 4673 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: Fuses M1120 CAUSE: Lightning Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): N/A Circuit patrolled & type: F4 not patrolled. Weather (wind/rain): Rain/lightning. Follow up required (select advisory)? No Additional fault restoration comments: Blown Transformer - LV Lines Down - Tag A42805 Fuses M1120 O,R,T 1 x 15kVA 3 Ø 11kV/400V 3 x 2A HV fuses | .
2543 |  | JE24034902 | CLOTON RD INDUSTRIAL | Western | CLOTON RD INDUSTRIAL | 2024-09-22 | 14:00 | 2024-09-22 | 14:15 | 8.2807e-05 | 5.5179e-06 | 2 | 30 | Unplanned | LIGHTNING - LIGHTNING STRIKE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 6942 Protection flags (nil where none): E/F, O/C A, B & C CAUSE: Lightning Location: na Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: na Weather (wind/rain): Lightning LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: NOC Liven after Lightning storm SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2544 |  | JE24034905 | IRIRANGI | Western | IRIRANGI | 2024-09-22 | 14:01 | 2024-09-22 | 21:22 | 0.0072977 | 1.6554e-05 | 6 | 2645 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: X710 No. Fuses: 2 Fuse Amp Size: 2 Amp TIME CLOSED: 21:22 Cause: Lightning Weather (wind/rain): Lightning, Rain Follow up required (select advisory)? N Fuses Location: X709 No. Fuses: 1 Fuse Amp Size: 2 Amp TIME CLOSED: 21:22 Cause: Lightning Weather (wind/rain): Lightning, Rain Follow up required (select advisory)? N | .
2545 |  | JE24034906 | WAREA | Western | WAREA | 2024-09-22 | 14:03 | 2024-09-22 | 16:27 | 0.0066269 | 5.7938e-05 | 21 | 2402 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 6293 No. Fuses: 2 Fuse Amp Size: 20 TIME CLOSED: 15:49 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? Fuses Location: P1030 No. Fuses: 1 Fuse Amp Size: 6 TIME CLOSED: 16:07 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? Fuses Location: 5581E No. Fuses: 1 Fuse Amp Size: 3 TIME CLOSED: 16:18 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n Fuses Location: P1035 No. Fuses: 1 Fuse Amp Size: 3 TIME CLOSED: 16:26 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n | .
2546 |  | JE24034912 | OAONUI | Western | OAONUI | 2024-09-22 | 20:49 | 2024-09-23 | 15:49 | 0.0031465 | 2.759e-06 | 1 | 1140 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Need SIS - TX 5585E replaced Isolation: 8901 Fusses CAUSE: Lightning Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: Weather (wind/rain): Follow up required (select advisory)? Additional fault restoration comments: Fuses Location: 8901 No. Fuses: 3 Fuse Amp Size: Failed TIME CLOSED: Cause: Lightning Weather (wind/rain): Follow up required (select advisory)? Transformer 5585E Faulty, to be replaced tomorrow Transformer replaced 1 x 30kVA 3 Ø 11kV/400V 3 x 3A HV fuses | .
2547 |  | JE24034916 | ARAHINA 33KV | Western | ARAHINA 33KV | 2024-09-22 | 14:24 | 2024-09-22 | 15:41 | 0.059908 | 0.0024996 | 906 | 21714 | Unplanned | LIGHTNING - LIGHTNING STRIKE | REGULATORY INFORMATION Voltage & Device ID: 33kV CB 3086 Protection flags (nil where none): E/F, O/C A & B CAUSE: Lightning Location: na Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): lightning LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Line patrolled after lightning strike, no fault found, full power restored Back feeds put in place for Hunterville 22kV CB 4138 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Rata Circuit that tripped: Arahina CB 3086 DTF (KM):na | .
2548 |  | JE24034921 | WESTMERE PEAT ST | Western | WESTMERE PEAT ST | 2024-09-22 | 14:33 | 2024-09-22 | 20:49 | 0.0041423 | 1.1036e-05 | 4 | 1501 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: X921 No. Fuses: 3 Fuse Amp Size: 2A TIME CLOSED: 20:48 Cause: Lightning Weather (wind/rain): Follow up required (select advisory)? | .
2549 |  | JE24034924 | TUTAENUI | Western | TUTAENUI | 2024-09-22 | 14:36 | 2024-09-22 | 16:40 | 0.0017173 | 1.3795e-05 | 5 | 622 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: X1101 No. Fuses: 3 Fuse Amp Size: 2 TIME CLOSED: 16:40 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n Replaced 1 x Barrel | .
2550 |  | JE24034925 | LEPPERTON | Western | LEPPERTON | 2024-09-22 | 14:36 | 2024-09-22 | 21:29 | 0.0068306 | 1.6554e-05 | 6 | 2476 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 1353 No. Fuses: 3 Fuse Amp Size: 3 Amp TIME CLOSED: 21:28 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? N | .
2551 |  | JE24034926 | MATAPU | Western | MATAPU | 2024-09-22 | 18:31 | 2024-09-23 | 10:52 | 0.0081196 | 8.2769e-06 | 3 | 2943 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Need SIS TX 5244E Replaced Fuses Location: 12744 No. Fuses: 1 Fuse Amp Size: 8 TIME CLOSED: Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n Fuses Location: 5244E No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 10:51 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n TFR 5244E Faulty Isolated at TFR 5244E Fuses Replaced 1 50KVA Transformer 11kV - 400V Robert Northcott Completed | .
2552 |  | JE24034936 | TIKORANGI | Western | TIKORANGI | 2024-09-22 | 14:56 | 2024-09-23 | 10:57 | 0.003315 | 2.759e-06 | 1 | 1202 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Transformer 4835T No. Fuses: 3 Fuse Amp Size: 3A TIME CLOSED: 10:57 Cause: Lightning Weather (wind/rain): Storm Yesterday Follow up required (select advisory)? Can be completed when neitana is on site | .
2553 |  | JE24034941 | SEAWARD COAST | Western | SEAWARD COAST | 2024-09-22 | 13:45 | 2024-09-22 | 17:20 | 0.016188 | 8.2769e-05 | 30 | 5867 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 8475 No. Fuses: 1 Fuse Amp Size: 15 TIME CLOSED: 16:56 Cause: Lightning Weather (wind/rain): Follow up required (select advisory)? Fuses Location: 989 No. Fuses: 1 Fuse Amp Size: 3 TIME CLOSED: 17:08 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? Fuses Location: 971 No. Fuses: 2 Fuse Amp Size: 3, Replaced 1 x barrel TIME CLOSED: 17:20 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? | .
2554 |  | JE24034942 | TIKORANGI | Western | TIKORANGI | 2024-09-22 | 15:06 | 2024-09-23 | 14:01 | 0.0075831 | 5.5179e-06 | 2 | 2749 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: TX 4080T No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 14:00 Cause: LIGHTNING Weather (wind/rain): CALM Follow up required (select advisory)? | .
2555 |  | JE24034946 | LEPPERTON | Western | LEPPERTON | 2024-09-22 | 14:59 | 2024-09-22 | 18:59 | 0.0046305 | 1.9313e-05 | 7 | 1678 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 8482 No. Fuses: 2 Fuse Amp Size: 25A TIME CLOSED: 18:58 Cause: Lightning Weather (wind/rain): Follow up required (select advisory)? Also replaced 1x HV fuse carrier | .
2556 |  | JE24034947 | LEPPERTON | Western | LEPPERTON | 2024-09-22 | 14:55 | 2024-09-22 | 20:55 | 0.0029846 | 8.2769e-06 | 3 | 1082 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Fuses 8447 No. Fuses: 3 Fuse Amp Size: 3A TIME CLOSED: 20:55 Cause: Lightning Weather (wind/rain): Rainy Follow up required (select advisory)? NIL | .
2557 |  | JE24034948 | LEPPERTON | Western | LEPPERTON | 2024-09-22 | 14:58 | 2024-09-22 | 20:32 | 0.0027696 | 8.2769e-06 | 3 | 1004 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 1538 No. Fuses: 3 Fuse Amp Size: 3A TIME CLOSED: 20:32 Cause: Lightning Weather (wind/rain): Lightning, Raining Follow up required (select advisory)? N | .
2558 |  | JE24034949 | LEPPERTON | Western | LEPPERTON | 2024-09-22 | 14:39 | 2024-09-22 | 19:46 | 0.00084642 | 2.759e-06 | 1 | 307 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Transformer 2379N No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 19:46 Cause: Lightning Weather (wind/rain): Fine Follow up required (select advisory)? NIL | .
2559 |  | JE24034953 | RATAPIKO | Western | RATAPIKO | 2024-09-22 | 17:46 | 2024-09-22 | 17:50 | 3.6535e-05 | 8.2769e-06 | 3 | 13 | Unplanned | LIGHTNING - LIGHTNING STRIKE | In correct job location Fuses Location: 3589T No. Fuses: 3 Fuse Amp Size: 2 TIME CLOSED: 17:50 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n Chris has attended job | .
2560 |  | JE24034959 | WESTMERE PEAT ST | Western | WESTMERE PEAT ST | 2024-09-22 | 18:16 | 2024-09-22 | 21:37 | 0.00225 | 1.3795e-05 | 5 | 816 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: X927 No. Fuses: 2 Fuse Amp Size: TIME CLOSED: Cause: Lightning Weather (wind/rain): Lightning Additional Info: Repaired broken HV Jumper at Tx X927. On closing Fuses X927 one broke. Isolation at Fuses 1130 to then replace 3x HV fuseholders complete with 2Amp fuses Follow up required (select advisory)? | .
2561 |  | JE24034960 | NGAERE | Western | NGAERE | 2024-09-22 | 15:36 | 2024-09-22 | 18:47 | 0.0021046 | 1.1036e-05 | 4 | 763 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 6268 No. Fuses: 2 Fuse Amp Size: 3Amp TIME CLOSED: 18:46 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? 1x fuse replaced at 3656T & 1 replaced at Fuses 6268 along with HV fuse carrier | .
2562 |  | JE24034963 | RAETIHI | Western | RAETIHI | 2024-09-22 | 15:39 | 2024-09-23 | 11:43 | 0.026574 | 2.2072e-05 | 8 | 9632 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Transformer X4054 No. Fuses: 3 Fuse Amp Size: 6A TIME CLOSED: 11:42 Cause: Lightning Weather (wind/rain): Storm Yesterday Follow up required (select advisory)? Confirmed Full Power Restored to 3038 Main Rd aswell (Linked Job) | .
2563 |  | JE24034966 | RAETIHI | Western | RAETIHI | 2024-09-22 | 15:45 | 2024-09-23 | 0:25 | 0.0071769 | 1.3795e-05 | 5 | 2601 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: X1959 No. Fuses: 3 Fuse Amp Size: 2A TIME CLOSED: 00:25 hrs Cause: Lightning Weather (wind/rain): Follow up required (select advisory)? | .
2564 |  | JE24034969 | TE KIRI | Western | TE KIRI | 2024-09-22 | 18:35 | 2024-09-23 | 11:20 | 0.0083133 | 8.2769e-06 | 3 | 3013 | Unplanned | LIGHTNING - LIGHTNING STRIKE | 2R left open for replacement of faulty Transformer T7175 Isolation: Transformer T7175 11kV Fuses CAUSE: Lightning Strike Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: Weather (wind/rain): Follow up required (select advisory)? Additional fault restoration comments: FM also replaced 3x 3A fuses at T7170, 1x 3A fuse at T7180, 1x 3A fuse & 1x HV fuse carrier at T7185 due to lightning - See related to jobs for T7180 & T7185 11:37 - Completed Replacement of Transformer T7175, Full Power Restored at 11:19 | .
2565 |  | JE24034971 | RAWHITIROA | Western | RAWHITIROA | 2024-09-22 | 15:57 | 2024-09-22 | 21:05 | 0.003402 | 1.1036e-05 | 4 | 1233 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 3761T No. Fuses: 2 Fuse Amp Size: 2 Amp TIME CLOSED: 21:05 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? N Replaced 1 x Carrier | .
2566 |  | JE24034974 | PIHAMA | Western | PIHAMA | 2024-09-22 | 16:14 | 2024-09-23 | 13:39 | 0.010637 | 8.2769e-06 | 3 | 3855 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: Transformer 5096E Fuses CAUSE: Lightning Temp generation (stage details when used): Transformer Replacement completed under the 2R - Full Power Restored PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: Weather (wind/rain): Follow up required (select advisory)? Additional fault restoration comments: | .
2567 |  | JE24034978 | PARAPARA | Western | PARAPARA | 2024-09-22 | 16:03 | 2024-09-22 | 17:46 | 0.0041271 | 4.9661e-05 | 18 | 1496 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 498 No. Fuses: 1 Fuse Amp Size: 8 TIME CLOSED: 17:22 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n Fuses Location: X1955 No. Fuses: 3 Fuse Amp Size: 2 TIME CLOSED: 17:45 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n | .
2568 |  | JE24034983 | PARAPARA | Western | PARAPARA | 2024-09-22 | 16:08 | 2024-09-22 | 22:30 | 0.002108 | 5.5179e-06 | 2 | 764 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 2828 No. Fuses: 2 Fuse Amp Size: 8 Amp TIME CLOSED: 22:30 hrs Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n | .
2569 |  | JE24034985 | NGAERE | Western | NGAERE | 2024-09-22 | 16:10 | 2024-09-22 | 17:55 | 0.00028969 | 2.759e-06 | 1 | 105 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 8680 No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 17:55 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? | .
2570 |  | JE24034995 | MANGAWEKA | Western | MANGAWEKA | 2024-09-22 | 16:36 | 2024-09-22 | 20:50 | 0.01404 | 5.5179e-05 | 20 | 5089 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 2813 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 20:50 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n | .
2571 |  | JE24034996 | RATAPIKO | Western | RATAPIKO | 2024-09-22 | 20:36 | 2024-09-23 | 17:45 | 0.010507 | 8.2769e-06 | 3 | 3808 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: Fuses 6234 CAUSE: Lightning Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): N/A Circuit patrolled & type: F4, Not patrolled Weather (wind/rain): Rain/lightning Follow up required (select advisory)?No Additional fault restoration comments: 1 x 15kVA 3 Ø 11kV/400V transformer 1 x 2A HV fuse 2 x 63A HRC fuses | .
2572 |  | JE24035008 | TIKORANGI | Western | TIKORANGI | 2024-09-22 | 17:11 | 2024-09-23 | 15:25 | 0.0036812 | 2.759e-06 | 1 | 1334 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: FUSES 5883 No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 15:25 Cause: LIGHTING Weather (wind/rain): CALM Follow up required (select advisory)? Need Neitana on site before closing | .
2573 |  | JE24035009 | HUNTERVILLE 22KV | Western | HUNTERVILLE 22KV | 2024-09-22 | 17:12 | 2024-09-22 | 20:51 | 0.012072 | 5.5179e-05 | 20 | 4375 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Z102 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 20:50 Cause: Lightning Weather (wind/rain): Follow up required (select advisory)? | .
2574 |  | JE24035019 | TE KIRI | Western | TE KIRI | 2024-09-22 | 22:45 | 2024-09-23 | 17:49 | 0.0094672 | 8.2769e-06 | 3 | 3431 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: T7100 Fuses CAUSE: Lightning Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): N/A Circuit patrolled & type: F4, not patrolled. Weather (wind/rain): Rain/lightning Follow up required (select advisory)? No Additional fault restoration comments: Transformer T7100 Faulty Needs replacing under 2R later today. 1 x 30kVA 3 Ø 11kV/400V 2 x 3A HV fuses | .
2575 |  | JE24035021 | OTAKEHO | Western | OTAKEHO | 2024-09-22 | 21:00 | 2024-09-22 | 21:45 | 0.0022166 | 4.9661e-05 | 18 | 803 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Repair broken jumper to DDO at tx M4120 Cause: Wind Isolation: MA574 What was replaced? Jumper & 2x Conductor Joints Where was it replaced (pole/TX/pillar box)? M4120 Additional Info: | .
2576 |  | JE24035025 | PARAPARA | Western | PARAPARA | 2024-09-22 | 18:12 | 2024-09-23 | 15:21 | 0.014001 | 1.1036e-05 | 4 | 5075 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: X618 No. Fuses: 2 Fuse Amp Size:2 TIME CLOSED: 15:20 Cause: Lightning Weather (wind/rain): Follow up required (select advisory)?N | .
2577 |  | JE24035027 | AUROA | Western | AUROA | 2024-09-22 | 18:17 | 2024-09-23 | 9:22 | 0.0049931 | 5.5179e-06 | 2 | 1810 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Transformer M1125 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 09:22 Cause: Lightning Weather (wind/rain): Stormy Follow up required (select advisory)? | .
2578 |  | JE24035028 | AUROA | Western | AUROA | 2024-09-22 | 18:21 | 2024-09-22 | 20:31 | 0.00035692 | 2.759e-06 | 1 | 129 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: M1048 No. Fuses: 3 Fuse Amp Size: 2 Amp TIME CLOSED: 20:30 Cause: Lightning Weather (wind/rain): Lightning, Rain Follow up required (select advisory)? N | .
2579 |  | JE24035029 | MAIN RD MOTONUI | Western | MAIN RD MOTONUI | 2024-09-22 | 18:23 | 2024-09-23 | 17:45 | 0.019345 | 1.3795e-05 | 5 | 7012 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: TX 2920T No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 17:45 Cause: LIGHTNING Weather (wind/rain): CALM Follow up required (select advisory)? | .
2580 |  | JE24035035 | RAETIHI | Western | RAETIHI | 2024-09-22 | 18:39 | 2024-09-23 | 12:20 | 0.017551 | 1.6554e-05 | 6 | 6362 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: X371 No. Fuses: 3 Fuse Amp Size: 6 TIME CLOSED: 12:19 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n | .
2581 |  | JE24035048 | INLAND COAST | Western | INLAND COAST | 2024-09-22 | 19:52 | 2024-09-23 | 17:00 | 0.010502 | 8.2769e-06 | 3 | 3807 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: TX 2282N No. Fuses: 3 Fuse Amp Size: 2A TIME CLOSED: 17:00 Cause: LIGHTNING Weather (wind/rain): CALM Follow up required (select advisory)? | .
2582 |  | JE24035050 | TE KIRI | Western | TE KIRI | 2024-09-22 | 19:11 | 2024-09-23 | 16:15 | 0.0034889 | 2.759e-06 | 1 | 1265 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: Fuses 6785 CAUSE: Lightning Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): N/A Circuit patrolled & type: F4 cursory patrolled Weather (wind/rain): Lightning Follow up required (select advisory)? No Additional fault restoration comments: 1 x 30kVA 3 Ø 11kV/400V 2 x 3A HV fuses | .
2583 |  | JE24035051 | TE KIRI | Western | TE KIRI | 2024-09-22 | 19:46 | 2024-09-23 | 13:52 | 0.0029977 | 2.759e-06 | 1 | 1087 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: Fuses 8671 1x 10amp CAUSE: Lightning Temp generation (stage details when used): Replaced blown Transformer 5499E Under 2R - 1x 100kVA 3Phase Transformer Closed 13:52 PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: Weather (wind/rain): Follow up required (select advisory)? Additional fault restoration comments: | .
2584 |  | JE24035053 | INLAND COAST | Western | INLAND COAST | 2024-09-22 | 19:00 | 2024-09-23 | 15:41 | 0.0034231 | 2.759e-06 | 1 | 1241 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: 6489 Fuses CAUSE: Lightning Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): N/A Circuit patrolled & type: F4 cursory patrolled. Weather (wind/rain): Lightning Follow up required (select advisory)? no Additional fault restoration comments: 11 x 30 kVA 3 Ø 11kV/400V transformer 6 x 3A HV fuses | .
2585 |  | JE24035054 | INLAND COAST | Western | INLAND COAST | 2024-09-22 | 19:00 | 2024-09-23 | 13:41 | 0.0030937 | 2.759e-06 | 1 | 1121 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: Fuses 6379 CAUSE: Lightning Temp generation (stage details when used): Transformer 1766N Replaced under the 2R - 1x50kVA Transformer, 3x6A HV Fuses PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: Weather (wind/rain): Follow up required (select advisory)? Additional fault restoration comments: | .
2586 |  | JE24035056 | RAWHITIROA | Western | RAWHITIROA | 2024-09-22 | 14:20 | 2024-09-22 | 19:40 | 0.0026504 | 8.2769e-06 | 3 | 961 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Fuses 6074 No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 19:40 Cause: Lightning Weather (wind/rain): Drizzle Follow up required (select advisory)? NIL 2R Under JE24034913 | .
2587 |  | JE24035062 | BUCKLAND RD | Eastern | BUCKLAND RD | 2024-09-22 | 23:42 | 2024-09-22 | 23:48 | 0.00026831 | 4.1384e-05 | 15 | 97 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: FP26-P No. Fuses: 2 Fuse Amp Size: 10 Amp TIME CLOSED: 23:48 Cause: Lightning Weather (wind/rain): Rain, Lightning Follow up required (select advisory)? Isolated at ABS 1183 for reload Off 23:41 On 23:48 | .
2588 |  | JE24035077 | 100 SUTHERLAND ROAD, MANAIA, HAWERA, 4678 | Western | OTAKEHO | 2024-09-22 | 23:52 | 2024-09-23 | 13:16 | 0.0052127 | 5.242e-05 | 19 | 1889 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: Transformer M4105 CAUSE: Lightning Strike - Arcing & Sparking from top of pole. Was on fire. Transformer M4105 is faulty & requires replacement Temp generation (stage details when used): Used: 1x30kVA 3phase Transformer, & 3x3A HV Fuses Transformer M4105 Replacement Completed 23/09/24, Full Power Restored Fuses MA574 replaced 1x 20amp HV fuse, power restored 23/9 00:55 PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: Weather (wind/rain): Follow up required (select advisory)? Additional fault restoration comments: | .
2589 |  | JE24035143 | PARAPARA | Western | PARAPARA | 2024-09-22 | 15:54 | 2024-09-22 | 22:40 | 0.0056014 | 1.3795e-05 | 5 | 2030 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: X1987 No. Fuses: 3 Fuse Amp Size: 2 Amp TIME CLOSED: 22:39 hrs Cause: Lightning Weather (wind/rain): Heavy Rain Follow up required (select advisory)? | .
2590 |  | JE24035233 | STRATHMORE | Western | STRATHMORE | 2024-09-22 | 16:10 | 2024-09-23 | 13:28 | 0.017635 | 1.3795e-05 | 5 | 6392 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 4103T No. Fuses: 2 Fuse Amp Size:3 TIME CLOSED: 13:28 Cause: Lightning Weather (wind/rain):Lightning Follow up required (select advisory)?n | .
2591 |  | JE24032383 | 152 LINCOLN ROAD MASTERTON MASTERTON | Western | TOTARA ST | 2024-09-21 | 9:33 | 2024-09-21 | 15:53 | 0.0031427 | 8.2769e-06 | 3 | 1139 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Change T1365 daniel sawmill due to end of life project requested by powerco | .
2592 |  | JE24034107 | 30 KATERE ROAD WAIWHAKAIHO NEW PLYMOUTH | Western | KATERE 6 | 2024-09-21 | 9:16 | 2024-09-21 | 10:55 | 0.011302 | 0.00011312 | 41 | 4097 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Urgent replacement of defective HV x-arm on pole 749067 | .
2593 |  | JE24034797 | HAURAKI RD | Eastern | HAURAKI RD | 2024-09-21 | 2:03 | 2024-09-21 | 5:06 | 0.0060605 | 3.3108e-05 | 12 | 2197 | Unplanned | WILDLIFE - BIRD | Fuses Location: FP1996 No. Fuses: 2 Fuse Amp Size: TIME CLOSED: 05:05 Cause: Duck Strike Weather (wind/rain): Follow up required (select advisory)? | .
2594 |  | JE24034802 | INLAND COAST | Western | INLAND COAST | 2024-09-21 | 2:37 | 2024-09-21 | 7:00 | 0.0065244 | 2.4831e-05 | 9 | 2365 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 8455 No. Fuses: 2 Fuse Amp Size: 8 Amp TIME CLOSED: 06:59 hrs Cause: Unk Weather (wind/rain): Calm / Light Rain Follow up required (select advisory)? | .
2595 |  | JE24034813 | HUNTERVILLE 22KV | Western | HUNTERVILLE 22KV | 2024-09-21 | 6:55 | 2024-09-21 | 9:45 | 0.002352 | 1.3795e-05 | 5 | 852 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 2661 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 09:45 Cause: Suspect Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? | .
2596 |  | JE24034817 | CLIMIE RD | Western | CLIMIE RD | 2024-09-21 | 13:26 | 2024-09-21 | 17:19 | 0.002573 | 1.1036e-05 | 4 | 933 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: 2759T CAUSE: Unknown Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: N/A Weather (wind/rain): Calm Follow up required (select advisory)? Additional fault restoration comments: Replaced Transformer 2759T with like for like 30/11/3phase | .
2597 |  | JE24034824 | BURETA RD | Eastern | BURETA RD | 2024-09-21 | 14:09 | 2024-09-21 | 14:45 | 0.0036925 | 0.00010208 | 37 | 1338 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Fuses Location: SC4-442 No. Fuses: 1 Fuse Amp Size: 15 Amp TIME CLOSED: 14:45 Cause: Deterioration Weather (wind/rain): Calm Follow up required (select advisory)? No Recreated for calls sucked into JE24034815 as this appeared to be unrelated to the others | .
2598 |  | JE24034825 | KATERE 11 | Western | KATERE 11 | 2024-09-21 | 14:27 | 2024-09-24 | 19:45 | 0.0054742 | 1.1036e-05 | 3 | 1984 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Advised the details of who hit the Transformer is Richard Watkins - 027 489 8532 Car hit Sw/Gear 12521 & Transformer 2451N. Pads have moved and some damage to equipment, but no power off, and no cables exposed, or anything unsafe. 2R left open pending decision on repairs. Transformer to be changed out. All checked, small spot of oil on the bushing, oil is full, rain might make it look like it is leaking more. Waiting for gear and will do the work over the weekend, under a urgent HV NAPA, as this transformer is supplying a block of businesses. Isolated at Sw/Gear 8809/3 TFR 2451N Replaced, Full power restored | .
2599 |  | JE24034839 | THOMPSON DR | Eastern | THOMPSON DR | 2024-09-21 | 23:12 | 2024-09-22 | 0:49 | 0.017016 | 0.00017657 | 64 | 6167 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | LV cable fault found near Transformer TC1230. HV Isolated for repairs o be carried out. Isolated at Fuse/Sw 9083/2 Off 23:12 On 0048 | .
2600 |  | JE24034843 | PASCAL ST 9 | Western | PASCAL ST 9 | 2024-09-21 | 22:47 | 2024-09-22 | 1:56 | 0.11671 | 0.0037163 | 1347 | 42303 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: REC 10189 Protection flags (nil where none): A Phase EF CAUSE: Unknown Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): windy LFI (Y/N + Comments): LFI's shown in SCADA at Tfr T6/267 are not there Follow up Required (select advisory)? Additional fault restoration comments: No fault found | .
2601 |  | JE24032082 | 368 BLUESKIN ROAD BRUNSWICK WANGANUI | Western | BRUNSWICK | 2024-09-20 | 9:20 | 2024-09-20 | 11:28 | 0.00035333 | 2.759e-06 | 1 | 128 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Red Tagged Pole 782385 | .
2602 |  | JE24032095 | 698B RUATANGATA ROAD WHANGAEHU WANGANUI | Western | FORDELL | 2024-09-20 | 10:27 | 2024-09-20 | 15:26 | 0.01568 | 5.242e-05 | 19 | 5683 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace defect pole 794070 | .
2603 |  | JE24032223 | 7 ARMSTRONG AVENUE WAITARA WAITARA | Western | BLAKE ST | 2024-09-20 | 9:28 | 2024-09-20 | 12:06 | 0.032914 | 0.00021244 | 77 | 11930 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 33kV cable sheath integrity testing and 11kV Cap 5025T maint. | .
2604 |  | JE24032278 | 65 WHITE ROCK ROAD MARTINBOROUGH MARTINBOROUGH | Western | DYERVILLE | 2024-09-20 | 9:24 | 2024-09-20 | 13:36 | 0.15851 | 0.00062904 | 228 | 57452 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replacing 11kv xarms on pole 808854 and 808851 underneath 33kv lines and above LV lines | .
2605 |  | JE24032349 | 703 ROBERTS LINE MILSON PALMERSTON NORTH | Western | BUNNYTHORPE | 2024-09-20 | 9:46 | 2024-09-20 | 12:08 | 0.00039292 | 2.759e-06 | 1 | 142 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace leaking TX T6/525 & replace TX arms. Replaced 100kVA Transformer with a 15kVA | .
2606 |  | JE24032759 | 545 TE KOUMA ROAD TE KOUMA COROMANDEL | Eastern | MANAIA COROMANDEL | 2024-09-20 | 8:30 | 2024-09-20 | 11:37 | 0.068903 | 0.0003697 | 134 | 24974 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT Urgent works. To resag spans V1157-V12981. To resag span 384318-V1180. Cut palm at V12990. | .
2607 |  | JE24033980 | 217 RAHO RURU ROAD PIRINOA FEATHERSTON | Western | PIRINOA | 2024-09-20 | 8:53 | 2024-09-21 | 13:34 | 0.0047468 | 2.759e-06 | 1 | 1721 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove 11kv lines from pole 466917 to T742 | .
2608 |  | JE24034045 | 23 PUNGAREHU ROAD PUNGAREHU OPUNAKE | Western | PUNGAREHU | 2024-09-20 | 10:28 | 2024-09-20 | 14:47 | 0.066467 | 0.00025658 | 93 | 24091 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Disconnect mobile sub. Reconnect 33kV and 11kV feeder cables. Timing considered due to backfeed restrictions for milking time loading. - Disconnect Mobile Sub 33kV cable at Links 3126 & reconnect 33kV cable from CB 3122 - Disconnect Mobile Sub 11kV cable at ABS PU277 & reconnect 11kV cable from CB PU2 - Disconnect Mobile Sub 11kV cable at ABS PU313 & reconnect 11kV cable from CB PU3 (NOT ready for service, see additional info) | .
2609 |  | JE24034065 | 502A THE TERRACE THAMES THAMES | Eastern | RICHMOND ST | 2024-09-20 | 10:05 | 2024-09-20 | 10:45 | 0.013105 | 0.00032832 | 119 | 4750 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Isolate transformer TC 5224 to adjust tap changer Voltages before R-243, W-245, B-243 Voltages After R-235, W-238, B-235 | .
2610 |  | JE24034594 | MANGAWEKA | Western | MANGAWEKA | 2024-09-20 | 1:30 | 2024-09-20 | 12:28 | 0.041712 | 6.3456e-05 | 23 | 15119 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV Fuses 2813 Protection flags (nil when none): nil CAUSE: tree on lines Location: 812195 & 812196 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state no): n Circuit patrolled & type: cursory Weather (wind/rain): rain & wind Follow up required (select advisory)? Additional fault restoration comments: Line isolated at Fuses 2813 tree contractors needed to cut tree away. | .
2611 |  | JE24034603 | HORRELLS RD | Eastern | HORRELLS RD | 2024-09-20 | 4:47 | 2024-09-20 | 8:01 | 0.0056779 | 4.1384e-05 | 15 | 2058 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: FC2444 No. Fuses: 3 Fuse Amp Size: 10 Amp TIME CLOSED: 07:10 Cause: Lightning Weather (wind/rain): Follow up required (select advisory)? Fuses Location: TC5167 No. Fuses: 3 Fuse Amp Size: 6 Amp TIME CLOSED: 07:18 Cause: Lightning Weather (wind/rain): Follow up required (select advisory)? Fuses Location: TC2224 No. Fuses: 2 Fuse Amp Size: 3 Amp TIME CLOSED: 07:34 Cause: Lightning Weather (wind/rain): Follow up required (select advisory)? Fuses Location: TC2761 No. Fuses: 3 Fuse Amp Size: 2 Amp TIME CLOSED: 07:45 Cause: Lightning Weather (wind/rain): Follow up required (select advisory)? | .
2612 |  | JE24034635 | RANGIKURA | Western | RANGIKURA | 2024-09-20 | 8:27 | 2024-09-20 | 10:52 | 0.0020005 | 1.3795e-05 | 5 | 725 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Location: Cause: 2x Broken Insulators Isolation: Fuses 697 Weather (wind/rain): Windy / Heavy Rain Follow up required (select advisory)? Additional Info: Replaced HV Pin Arm | .
2613 |  | JE24034665 | MAIN RD MOTONUI | Western | MAIN RD MOTONUI | 2024-09-20 | 7:08 | 2024-09-20 | 10:11 | 0.0010078 | 5.5179e-06 | 2 | 365 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Transformer 4047T No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 10:10 Cause: Lightning Weather (wind/rain): overcast Follow up required (select advisory)? NIL | .
2614 |  | JE24034667 | MANGATAINOKA | Western | MANGATAINOKA | 2024-09-20 | 10:35 | 2024-09-20 | 11:50 | 0.00083018 | 1.1036e-05 | 4 | 301 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Transformer T7/95 No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 11:50 Cause: Lightning Weather (wind/rain): Overcast Follow up required (select advisory)? NIL | .
2615 |  | JE24034732 | WAITUNA | Western | WAITUNA | 2024-09-20 | 15:09 | 2024-09-20 | 16:50 | 0.00027789 | 2.759e-06 | 1 | 101 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T5/193 No. Fuses: 1 Fuse Amp Size:2 TIME CLOSED: 16:50 Cause: lighting Weather (wind/rain): lighting Follow up required (select advisory)?n Some how all jobs went to main line and merged | .
2616 |  | JE24034753 | RAETIHI | Western | RAETIHI | 2024-09-20 | 16:42 | 2024-09-20 | 20:05 | 0.00056027 | 2.759e-06 | 1 | 203 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 4379W No. Fuses: 2 Fuse Amp Size: 2 TIME CLOSED: 20:05 Cause: lighting Weather (wind/rain):lighting Follow up required (select advisory)?N | .
2617 |  | JE24034755 | WAITUNA | Western | WAITUNA | 2024-09-20 | 15:24 | 2024-09-20 | 17:51 | 0.00040396 | 2.759e-06 | 1 | 146 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T5/194 No. Fuses: 3 Fuse Amp Size:3 TIME CLOSED: 17:50 Cause: lighting Weather (wind/rain): n Follow up required (select advisory)?n | .
2618 |  | JE24034758 | WAITUNA | Western | WAITUNA | 2024-09-20 | 15:10 | 2024-09-20 | 16:45 | 0.00052457 | 5.5179e-06 | 2 | 190 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T5/22 No. Fuses: 2 Fuse Amp Size:6A TIME CLOSED: 16:45 Cause: Lighting Weather (wind/rain)lighting : Follow up required (select advisory)?N | .
2619 |  | JE24034765 | POHANGINA | Western | POHANGINA | 2024-09-20 | 17:24 | 2024-09-20 | 19:01 | 0.0016128 | 1.6554e-05 | 6 | 585 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T4/249 No. Fuses: 3 Fuse Amp Size:3 TIME CLOSED: 19:00 Cause: lightning Weather (wind/rain): Follow up required (select advisory)?na | .
2620 |  | JE24034770 | TATUANUI | Eastern | TATUANUI | 2024-09-20 | 17:34 | 2024-09-20 | 19:03 | 0.00049381 | 5.5179e-06 | 2 | 179 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: FC2185 No. Fuses: 3 Fuse Amp Size: 2 TIME CLOSED: 19:03 Cause: Lightning Weather (wind/rain): Follow up required (select advisory)? | .
2621 |  | JE24034772 | KOPANE | Western | KOPANE | 2024-09-20 | 17:41 | 2024-09-20 | 19:51 | 0.00071603 | 5.5179e-06 | 2 | 260 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T1/183 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 1950 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? | .
2622 |  | JE24034782 | WAITUNA | Western | WAITUNA | 2024-09-20 | 18:10 | 2024-09-20 | 18:41 | 0.0006904 | 2.2072e-05 | 8 | 250 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T5/8 No. Fuses: 2 Fuse Amp Size:6 TIME CLOSED: 18:40 Cause: lightning Weather (wind/rain):lightning Follow up required (select advisory)?n | .
2623 |  | JE24034788 | APITI | Western | APITI | 2024-09-20 | 18:22 | 2024-09-20 | 23:26 | 0.0025149 | 8.2769e-06 | 3 | 912 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: Fuses T5/124 CAUSE: Lightning Temp generation (stage details when used): N PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: Weather (wind/rain): Lightning Follow up required (select advisory)? Replaced tx T5/124 | .
2624 |  | JE24034793 | RAETIHI | Western | RAETIHI | 2024-09-20 | 16:39 | 2024-09-20 | 19:21 | 0.00911 | 6.0697e-05 | 22 | 3302 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 171 No. Fuses: 1 Fuse Amp Size: 6 TIME CLOSED: 19:08 Cause: Lighting Weather (wind/rain):lighting Follow up required (select advisory)?n Fuses Location: X1691 No. Fuses: 1 Fuse Amp Size:2 TIME CLOSED: 19:20 Cause: Lighting Weather (wind/rain):lighting Follow up required (select advisory)?n Line was patrolled and other TXs checked from original calls | .
2625 |  | JE24034795 | COLYTON | Western | COLYTON | 2024-09-20 | 17:34 | 2024-09-20 | 19:36 | 0.00097667 | 8.2769e-06 | 3 | 354 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Fuses E18 No. Fuses: 3 Fuse Amp Size: 6A TIME CLOSED: 1935 Cause: lightning Weather (wind/rain): Lightning Follow up required (select advisory)? | .
2626 |  | JE24040187 | AOKAUTERE | Western | AOKAUTERE | 2024-09-20 | 6:51 | 2024-11-06 | 15:50 | 0.2143 | 0.00013519 | 25 | 77673 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Repair damaged conductor pulled down by trees close line break P26254 Final repairs for JE24034608 | .
2627 |  | JE24031422 | 407 PLYMOUTH ROAD KORU NEW PLYMOUTH | Western | PIONEER RD | 2024-09-19 | 9:01 | 2024-09-19 | 15:26 | 0.052271 | 0.00014347 | 52 | 18946 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv conductors between poles 755187 and 755166. | .
2628 |  | JE24031427 | 983 OROUA VALLEY ROAD APITI KIMBOLTON | Western | APITI | 2024-09-19 | 8:46 | 2024-09-19 | 12:17 | 0.0046652 | 2.2072e-05 | 8 | 1691 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace crossarms between and including Pole P01725 and P05443. Reconductor LV from P05405 to P05443 | .
2629 |  | JE24031505 | 373 BALLANCE ROAD BALLANCE PAHIATUA | Western | MANGATAINOKA | 2024-09-19 | 9:00 | 2024-09-19 | 14:38 | 0.019563 | 5.7938e-05 | 21 | 7091 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace crossarms & hardware between P26683 and P26459. | .
2630 |  | JE24032012 | 50 SHOOTING BUTTS ROAD MARTINBOROUGH MARTINBOROUGH | Western | DYERVILLE | 2024-09-19 | 12:01 | 2024-09-19 | 13:34 | 0.00025806 | 2.759e-06 | 1 | 94 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace lightening arrestors on pole 817289/fuses 7337 | .
2631 |  | JE24032020 | 148 DUBLIN STREET MARTINBOROUGH | Western | DYERVILLE | 2024-09-19 | 8:31 | 2024-09-19 | 10:14 | 0.001419 | 1.3795e-05 | 5 | 514 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re-sag 11kv conductors pole 842242 | .
2632 |  | JE24032063 | 842 WAIHI WHANGAMATA ROAD WAIHI WAIHI | Eastern | WAIHI NORTH | 2024-09-19 | 12:00 | 2024-09-19 | 13:38 | 0.0010795 | 1.1036e-05 | 4 | 391 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Stay wire through HV | .
2633 |  | JE24032068 | 223 REID LINE EAST AORANGI FEILDING | Western | BUNNYTHORPE | 2024-09-19 | 9:30 | 2024-09-19 | 13:50 | 0.067334 | 0.00025934 | 94 | 24406 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace xarms and hv resag on various locations beyond abs E5 | .
2634 |  | JE24032073 | 1213 IHAIA ROAD OPUNAKE OPUNAKE | Western | IHAIA RD | 2024-09-19 | 9:46 | 2024-09-19 | 15:35 | 0.011578 | 3.3108e-05 | 12 | 4197 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | to replace various X- arms in between poles 715117 - 715157 | .
2635 |  | JE24032078 | 521 MAUNGARANGI ROAD PAENGAROA TE PUKE | Eastern | MANGOREWA | 2024-09-19 | 8:46 | 2024-09-19 | 14:33 | 0.051645 | 0.00014898 | 54 | 18719 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv/400vt poles,266807,221899,221896 & 221894. Replace 11kv/400vt cross arms @ pole 221895. Retrofit LA and earth @ pole 221898 (422130). Replace LV conductors with PVC ferret between poles 221896 & 221899. | .
2636 |  | JE24032113 | 256 OLD TAURANGA ROAD WAIHI WAIHI | Eastern | OLD TAURANGA RD | 2024-09-19 | 9:31 | 2024-09-19 | 10:46 | 0.0027115 | 3.5867e-05 | 13 | 983 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Insulators and D/E at Poles P13467 And P0282 | .
2637 |  | JE24032520 | 4 TE MATA DRIVE TE MATA THAMES | Eastern | MANAIA COROMANDEL | 2024-09-19 | 9:06 | 2024-09-19 | 13:02 | 0.066512 | 0.00028141 | 102 | 24108 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT - Urgent works. To re-sag spans T1534-263329 and T13049-488285 | .
2638 |  | JE24034433 | PUHUNGA ISLAND RD | Eastern | PUHUNGA ISLAND RD | 2024-09-19 | 3:24 | 2024-09-19 | 5:13 | 0.06569 | 0.0016278 | 590 | 23810 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: CB 7 Protection flags (nil where none): Phase B, C Fault, OCINVT CAUSE: Dead Duck at the ground at Pole O247 Location: Pole O247 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Patrolled restored, found dead duck on ground SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2639 |  | JE24034440 | HAURAKI RD | Eastern | HAURAKI RD | 2024-09-19 | 7:14 | 2024-09-19 | 9:14 | 0.0026402 | 2.2072e-05 | 8 | 957 | Unplanned | WILDLIFE - BIRD | Fuses Location: FP1076 No. Fuses: 2 Fuse Amp Size: 8A TIME CLOSED: 09:13 Cause: Birds Weather (wind/rain): Overcast Drizzle Follow up required (select advisory)? NIL Stu going to attend 205 Ngataipua Rd to confirm power has been restore will call back Checked the above, power restored 1r 24023409 used | .
2640 |  | JE24034446 | RANGIKURA | Western | RANGIKURA | 2024-09-19 | 8:03 | 2024-09-19 | 11:52 | 0.0031534 | 1.3795e-05 | 5 | 1143 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 697 No. Fuses: 2 Fuse Amp Size: 8A TIME CLOSED: 11:51 Cause: Unknown Weather (wind/rain): Windy Follow up required (select advisory)? NIL | .
2641 |  | JE24034450 | WAIHI-WHANGAMATA 33KV | Eastern | WAIHI-WHANGAMATA 33KV | 2024-09-19 | 8:15 | 2024-09-19 | 8:54 | 0.18669 | 0.017953 | 6507 | 67665 | Unplanned | HUMAN ERROR - PROTECTION SETTINGS - INCORRECT/ERROR | REGULATORY INFORMATION Voltage & Device ID: 33kV CB PC92 Protection flags (nil where none): RES O/V CAUSE: VT fuse removal?? Location: WGM Sub Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Nil Weather (wind/rain): Fine LFI (Y/N + Comments): Nil Follow up Required (select advisory)? Yes Additional fault restoration comments: During planned switching for NAPA 109348 the 33kV BUS VT secondary fuses were opened, removed & tagged. At this point 33kV CB92 & 11kV 17 tripped on RES O/V. The fuses were restored & the power restored. BESS also tripped offline at the same time & didn't take any load. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): WGM Sub Circuit that tripped: PC92 DTF (KM): Nil | .
2642 |  | JE24034511 | DAIRY FACTORY | Western | DAIRY FACTORY | 2024-09-19 | 12:02 | 2024-09-19 | 14:19 | 0.0018894 | 1.3795e-05 | 5 | 685 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: Fuses 7226 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 14:19 Cause: Wind Weather (wind/rain): Windy Follow up required (select advisory)? NIL | .
2643 |  | JE24034518 | STRATHMORE | Western | STRATHMORE | 2024-09-19 | 12:54 | 2024-09-19 | 15:16 | 0.0042913 | 3.0349e-05 | 11 | 1555 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 5453 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 15-15 Cause: Unknown Weather (wind/rain): Rain Follow up required (select advisory)? | .
2644 |  | JE24034532 | 11TH AVE | Eastern | 11TH AVE | 2024-09-19 | 16:00 | 2024-09-19 | 17:13 | 0.010791 | 0.00014898 | 54 | 3911 | Unplanned | HUMAN ERROR - POTENTIAL SWITCHING ERROR | Fuses found blown in Fuse/Sw SK5-125 Isolated at Sw/Gear SK5-119 & 14406/2 Fuse not blown Fuse/Sw SK5-125 open, Sw/Gear SK5-124 closed. Switch error during NAPA 113213 Power restored 17:12 Do not close job, on request of D. Spellman 109A Twelfth Avenue have advised that he has a Tropical fish Tank and would like to know when he could expect Power back on.0272750755 | .
2645 |  | JE24034549 | RANGIKURA | Western | RANGIKURA | 2024-09-19 | 13:13 | 2024-09-19 | 16:58 | 0.0031055 | 1.3795e-05 | 5 | 1126 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: 697 No. Fuses: 2 Fuse Amp Size:8 TIME CLOSED: 16:58 Cause: Line clash / Weather Weather (wind/rain): Storm Follow up required (select advisory)?n | .
2646 |  | JE24034579 | RANGIKURA | Western | RANGIKURA | 2024-09-19 | 18:56 | 2024-09-19 | 21:42 | 0.0022838 | 1.3795e-05 | 5 | 828 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 697 No. Fuses: 2 Fuse Amp Size: 8 TIME CLOSED: 21:41 Cause: Suspect Line Clash Weather (wind/rain): wind & rain Follow up required (select advisory)?n | .
2647 |  | JE24034582 | BARRETT RD | Eastern | BARRETT RD | 2024-09-19 | 19:50 | 2024-09-20 | 1:01 | 0.20755 | 0.010084 | 1748 | 75226 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV OMO CB 5 Protection flags (nil where none): B Phase O/C E/F CAUSE: Duck Strike Location: Pole 209224 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Calm LFI (Y/N + Comments): Nil Follow up Required (select advisory)? Additional fault restoration comments: Recloser 9674 Tripped on loading Showing 95A & Tripped says tripping level 120A SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2648 |  | JE24031398 | 19 HIKUNUI ROAD KAHUTARA FEATHERSTON | Western | DAIRY FACTORY | 2024-09-18 | 8:46 | 2024-09-18 | 14:22 | 0.081349 | 0.00024279 | 88 | 29485 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Repair uneven sags and replace hardware past 11169/2 | .
2649 |  | JE24031412 | 488 MAUNGARANGI ROAD PAENGAROA TE PUKE | Eastern | MANGOREWA | 2024-09-18 | 9:31 | 2024-09-18 | 14:35 | 0.045284 | 0.00014898 | 54 | 16413 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv/400vt poles 221889,221891,221892,221893. Replace LV conductors with PVC ferret between poles 221893,230125 & 221887. | .
2650 |  | JE24031414 | 1161 STATE HIGHWAY 4 PARIKINO WANGANUI | Western | MAKIRIKIRI | 2024-09-18 | 9:23 | 2024-09-18 | 14:23 | 0.076232 | 0.00025658 | 93 | 27631 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Swing conductor over onto new regulator site 16168 and remove old regulator R5 | .
2651 |  | JE24031425 | 5137 STATE HIGHWAY 4 WAIMARINO WANGANUI | Western | PARAPARA | 2024-09-18 | 5:45 | 2024-09-18 | 13:40 | 0.024528 | 0.00023727 | 57 | 8890 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Vegetation - Asplundh contractor to clear vegetation between pole 783702 and 783703 | .
2652 |  | JE24031506 | 125 SOLOMON STREET BROOKFIELD TAURANGA | Eastern | CENTRAL OTUMOETAI | 2024-09-18 | 8:34 | 2024-09-18 | 17:29 | 0.16971 | 0.00031728 | 115 | 61514 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace RMU 9117 with new automated CFCC Safelink 14987. Job Over run caused lack of resources. | .
2653 |  | JE24032067 | 96 TIKI ROAD COROMANDEL COROMANDEL | Eastern | KAPANGA ROAD | 2024-09-18 | 23:02 | 2024-09-19 | 1:10 | 0.066908 | 0.00055179 | 200 | 24251 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remake HV cable jumpers at pole 499575/499576 to supply 14967/1. Disconnect temporary supply cable from pole V12605 (Fuses TEMP90) to Transformer TC3773. Connect HV cable removed from old Fuse/Sw FP452 to new Fuse/Sw 14967/2 (Supply to TC3773). Liven Switchgear 14967/1. Liven and test TC3773. | .
2654 |  | JE24032354 | 235 TAPU COROGLEN ROAD TAPU THAMES | Eastern | MANAIA COROMANDEL | 2024-09-18 | 10:10 | 2024-09-18 | 14:21 | 0.049843 | 0.00019865 | 72 | 18066 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT - Urgent works. To re-sag 11kV lines between poles T1440 & T1442. Replace crossarms at T1440 & T1441. Re-sag LV span between T1440 & T1439. | .
2655 |  | JE24033442 | 25 MAHANA ROAD NGATEA NGATEA | Eastern | PUHUNGA ISLAND RD | 2024-09-18 | 9:02 | 2024-09-18 | 10:29 | 0.0075956 | 8.8287e-05 | 32 | 2753 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | reconnect repaired 11kv between RMU 13536/1 and at the cable break @ TC 2259 | .
2656 |  | JE24034282 | TE ROTI | Western | TE ROTI | 2024-09-18 | 3:08 | 2024-09-18 | 4:18 | 0.0015543 | 2.2072e-05 | 8 | 563 | Unplanned | WILDLIFE - BIRD | Fuses Location: 6088 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 04:18 Cause: bird strike Weather (wind/rain): calm Follow up required (select advisory)?n Line patrolled, line is next to water treatment pond's | .
2657 |  | JE24034286 | PUHUNGA ISLAND RD | Eastern | PUHUNGA ISLAND RD | 2024-09-18 | 7:17 | 2024-09-18 | 9:35 | 0.006453 | 4.6902e-05 | 17 | 2339 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV Fuses FP768 Protection flags (nil where none): na CAUSE: Broken Line, Duck Strike Location: Pole 858352 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Calm LFI (Y/N + Comments): NA Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2658 |  | JE24034344 | MANUTAHI | Western | MANUTAHI | 2024-09-18 | 15:29 | 2024-09-18 | 15:57 | 0.002307 | 8.001e-05 | 29 | 836 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolated at Fuses 6849 Replaced the Deadends | .
2659 |  | JE24034373 | 60 ORCHARD WEST ROAD, NGATEA, 3503 | Eastern | PUHUNGA ISLAND RD | 2024-09-18 | 17:20 | 2024-09-18 | 17:53 | 0.0021509 | 6.6215e-05 | 24 | 780 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: Failed 400V Lucy in DTX TC4739. HV Isolated & Earthed for Safety A/P Protection flags (nil where none): nil CAUSE: 400V Lucy / Cutout Failed Location: DTX TC4739 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2660 |  | JE24034396 | PATETONGA | Eastern | PATETONGA | 2024-09-18 | 15:48 | 2024-09-18 | 17:55 | 0.0007036 | 5.5179e-06 | 2 | 255 | Unplanned | WILDLIFE - BIRD | Fuses Location: FC4221 No. Fuses: 2 Fuse Amp Size: 20A TIME CLOSED: 17:55 Cause: Duck Strike Weather (wind/rain): Calm Follow up required (select advisory)? | .
2661 |  | JE24034413 | PIONEER RD | Western | PIONEER RD | 2024-09-18 | 17:24 | 2024-09-18 | 18:07 | 0.00011948 | 2.759e-06 | 1 | 43 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 8403 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 18-07 Cause: Unknown Weather (wind/rain): Fine and Cold Follow up required (select advisory)? | .
2662 |  | JE24034423 | RANGITANUKU RD | Eastern | RANGITANUKU RD | 2024-09-18 | 20:51 | 2024-09-18 | 22:22 | 0.00050425 | 5.5179e-06 | 2 | 183 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Wrong Transformer Number, should be TC5074 blown main line Fuses Fuses Location: Fuses FC1431 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 22:22 Cause: Wind Weather (wind/rain): Windy Follow up required (select advisory)?No | .
2663 |  | JE24030551 | 495 TAIRUA WHITIANGA ROAD COROGLEN WHITIANGA | Eastern | TAIRUA NORTH | 2024-09-17 | 10:16 | 2024-09-17 | 15:02 | 0.033201 | 0.00011588 | 42 | 12034 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV Poles W1915, W13417, New pole 6 (south of pole W13641), W1936& W1941, Tairua/Whitianga Rd | .
2664 |  | JE24030856 | 212 HANGAWERA ROAD MORRINSVILLE MORRINSVILLE | Eastern | HORRELLS RD | 2024-09-17 | 9:36 | 2024-09-17 | 12:16 | 0.0017683 | 1.1036e-05 | 4 | 641 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Arms and Hardware on Poles I0490, I13881 and I13882 | .
2665 |  | JE24030935 | 86 BALLANCE ROAD BALLANCE PAHIATUA | Western | MANGATAINOKA | 2024-09-17 | 9:15 | 2024-09-17 | 15:01 | 0.020045 | 5.7938e-05 | 21 | 7265 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace crossarms & hardware between poles P26697 and P26677. | .
2666 |  | JE24030941 | 3A KEREONE ROAD MORRINSVILLE MORRINSVILLE | Eastern | MOTUMAOHO | 2024-09-17 | 9:16 | 2024-09-17 | 12:41 | 0.0011336 | 5.5179e-06 | 2 | 411 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace HT & LT arm beyond fuses FP1521 | .
2667 |  | JE24030951 | 243 TAONUI ROAD AORANGI FEILDING | Western | BUNNYTHORPE | 2024-09-17 | 9:31 | 2024-09-17 | 12:23 | 0.044546 | 0.00025934 | 94 | 16146 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace HV xarms from P38698 to P38359 | .
2668 |  | JE24030957 | 287 PLYMOUTH ROAD KORU NEW PLYMOUTH | Western | PIONEER RD | 2024-09-17 | 9:00 | 2024-09-17 | 15:26 | 0.052933 | 0.00014347 | 52 | 19186 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV conductor between Poles 755207 and 755187. | .
2669 |  | JE24030995 | 283 HASTINGS ROAD, MATAPU | Western | MATAPU | 2024-09-17 | 9:14 | 2024-09-17 | 13:25 | 0.033273 | 0.00013243 | 48 | 12060 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace DNO ABS KA749 pole, replace HV pin xarms at poles 719961, 719962, 719963. | .
2670 |  | JE24031066 | 983 OROUA VALLEY ROAD APITI KIMBOLTON | Western | APITI | 2024-09-17 | 8:46 | 2024-09-17 | 14:03 | 0.0069897 | 2.2072e-05 | 8 | 2533 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Pole 861355 and crossarms between and including Pole P01727 and P01721 | .
2671 |  | JE24031279 | 916 MOUNTAIN ROAD WAIONGANA INGLEWOOD | Western | LEPPERTON | 2024-09-17 | 9:30 | 2024-09-17 | 14:46 | 0.020884 | 6.6215e-05 | 24 | 7570 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To Replace TX pole 869 install new 30kva TX | .
2672 |  | JE24032169 | 2820 TAIRUA ROAD PUKEPOTO HIKUAI | Eastern | HIKUAI | 2024-09-17 | 10:54 | 2024-09-17 | 13:04 | 0.053641 | 0.00041384 | 150 | 19443 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT - Urgent works. To re-sag 11kV lines between poles 320491/320074 & U12538/U0418 | .
2673 |  | JE24034099 | TE ROTI | Western | TE ROTI | 2024-09-17 | 6:13 | 2024-09-17 | 11:10 | 0.083086 | 0.00092977 | 337 | 30115 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB R61 Protection flags (nil where none): E/F, O/C C CAUSE: Insulator failure Location: Pole 733880 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4, cursory patrolled. Weather (wind/rain): Rain LFI (Y/N + Comments): Installed but did not operate Follow up Required (select advisory)? Yes due to LFI non operation Additional fault restoration comments: Fault found past Fuses 4955 on pole 733880, Insulator failure and cross arm burnt. 1 x HV double pin cross arm complete assembly 1 x stay anchor insulator and stay wire replaced SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2674 |  | JE24034100 | MANGAWEKA | Western | MANGAWEKA | 2024-09-17 | 6:29 | 2024-09-17 | 9:59 | 0.013324 | 6.3456e-05 | 23 | 4829 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: Fuses 2813 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 09:58 Cause: Line Clash Weather (wind/rain): Wind Follow up required (select advisory)? No | .
2675 |  | JE24034170 | THAMES 66kV | Eastern | THAMES 66kV | 2024-09-17 | 11:44 | 2024-09-17 | 13:18 | 3.7053 | 0.062292 | 22578 | 1343020 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 66kV CB 1072 Protection flags (nil where none): A,B O/C CAUSE: High winds Hail, Suspect wind blown branch Location: Pole 873491 section Temp generation (state details when used): Nil PERFORMANCE DETAIL DNO (number or state No): Nil Circuit patrolled and type: Cursory/ Operational, Curse Weather (wind/rain): Strong Winds, Hail LFI (Y/N + Comments): Yes Pole KPUTHS028 & 873491 Follow up Required (select advisory)? No Additional fault restoration comments: Half bus shut for Transpower occurring at the same time as fault. ABR scheme didn't operate correctly, Both Sw/Gear 14100/3 & GMCB 14100/1 opened on power fail Rec 9882 closed, This leaves no power to the Thames hospital (the whole point of the ABR scheme) Need Protection review on the settings at THS 66kV CB QC72, when feeding in the reverse direction settings alter to 120amps trip. If this CB had high settings when a Transpower half bus occurs we could feed the overhead to whitianga from that CB, if a fault was to occur on that Overhead it would keep Thames sub station on. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): WHT, COR, THS, TAI Circuit that tripped: CB 1072 DTF (KM): Nil | .
2676 |  | JE24034188 | TE ROTI | Western | TE ROTI | 2024-09-17 | 12:45 | 2024-09-17 | 18:34 | 0.14307 | 0.0018595 | 337 | 51857 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB R61 Protection flags (nil where none): E/F CAUSE: Broken eyebolt // Gum bark on the lines // Broken Insulator Location: Pole 733813 // 734951 // 733776 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4, cursory patrolled. Weather (wind/rain): High wind and heavy rain LFI (Y/N + Comments): Yes installed but the faultman saw the at pole 733919 the LFIs were installed incorrectly. Follow up Required (select advisory)? Yes LFIs to be corrected Additional fault restoration comments: Bark from a gum tree on the lines at pole 734951 removed with hot stick. Eye bolt was broken due to corrosion 3rd fault - Broken Insulator at at Pole 733776, Isolated at Fused ABs 5998 replaced insulator, full power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2677 |  | JE24034194 | recloser_13109:2 | Eastern | WAOTU | 2024-09-17 | 13:16 | 2024-09-17 | 14:16 | 0.0099764 | 0.00016554 | 60 | 3616 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 13109/2 Protection flags (nil where none): O/C A - B - C Ø CAUSE: Branch across lines Location: Pole M1545 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4, cursory patrolled. Weather (wind/rain): Heavy rain. LFI (Y/N + Comments): yes but no comms Follow up Required (select advisory)? Yes trees need to be cut. Additional fault restoration comments: Branch found with burn marks across lines removed with Hot Sticks. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2678 |  | JE24034219 | MANGATEPARU | Eastern | MANGATEPARU | 2024-09-17 | 11:19 | 2024-09-19 | 15:00 | 0.13974 | 0.00031176 | 97 | 50648 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Replaced AMPAC Joints still more to replace on main line, Bi Metal AMPAC's Failed 19/09/2024 Work completed under Urgent switching 24043212 | .
2679 |  | JE24034239 | OKAIAWA | Western | OKAIAWA | 2024-09-17 | 16:03 | 2024-09-17 | 21:51 | 0.028855 | 8.2769e-05 | 30 | 10459 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Car V pole 453856 Isolated at ABS MA411 & Links 12436/6 Replaced Hit Pole , Replaced HV & LV cross arms & hardware at Pole 721367 & straightened Repaired/pulled up LV road crossing at Pole 721369 Full power restored | .
2680 |  | JE24034253 | OKAIAWA | Western | OKAIAWA | 2024-09-17 | 20:20 | 2024-09-17 | 21:27 | 0.0075808 | 0.00011312 | 41 | 2748 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Broken Jumper found at Pole 718969 from main line to top of Fuses MA407 Isolated at ABS MA456, MA465 & MA481 Jumper repaired, Full power restored | .
2681 |  | JE24034277 | IRIRANGI | Western | IRIRANGI | 2024-09-17 | 21:26 | 2024-09-18 | 1:09 | 0.01722 | 7.7251e-05 | 28 | 6241 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: 2601 No. Fuses: 2 Fuse Amp Size: 8 TIME CLOSED: 01:09 Cause: unknown Weather (wind/rain): rain Follow up required (select advisory)?n Line patrolled from road, a lot of cross country lines could not be patrolled | .
2682 |  | JE24034278 | TAINUI | Eastern | TAINUI | 2024-09-17 | 21:33 | 2024-09-17 | 22:22 | 0.00067509 | 1.3795e-05 | 5 | 245 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses SE7-004 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 22:22 Cause: Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? No | .
2683 |  | JE24030793 | 24 LUND ROAD AONGATETE KATIKATI | Eastern | WILLS RD | 2024-09-16 | 1:36 | 2024-09-16 | 4:04 | 0.00082171 | 5.5179e-06 | 2 | 298 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Linkbox maintenance at TB1-136 | .
2684 |  | JE24030812 | 3774 WAITOTARA VALLEY ROAD NGAMATAPOURI WANGANUI | Western | WAITOTARA | 2024-09-16 | 10:05 | 2024-09-16 | 11:51 | 0.00029194 | 2.759e-06 | 1 | 106 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Pole 780476 & move back from river Operatiuonal control handed to Paul Clutterbuck at 08:47 due to no comms in Area | .
2685 |  | JE24030832 | 61 MABEY STREET ELTHAM ELTHAM | Western | ELTHAM TOWN NORTH | 2024-09-16 | 9:31 | 2024-09-16 | 13:41 | 0.0069176 | 2.759e-05 | 10 | 2507 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | relocate tx 3859T structure to pole 732526. remove span of HV & LV conductor back to pole 732526. replace pole 732526 and install new tx. | .
2686 |  | JE24030926 | 43 KERR ROAD TE POI MATAMATA | Eastern | BUCKLAND RD | 2024-09-16 | 9:18 | 2024-09-16 | 11:20 | 0.0033636 | 2.759e-05 | 10 | 1219 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole E0635 | .
2687 |  | JE24030934 | 873 ROBERTS LINE BUNNYTHORPE PALMERSTON NORTH | Western | BUNNYTHORPE | 2024-09-16 | 9:03 | 2024-09-16 | 12:26 | 0.0027902 | 1.3795e-05 | 5 | 1011 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace leaking TX T2/187 & TX arms | .
2688 |  | JE24030945 | 907 MCLAREN FALLS ROAD OMANAWA TAURANGA | Eastern | KAIMAI DRIVE | 2024-09-16 | 9:00 | 2024-09-16 | 13:47 | 0.036428 | 0.00012691 | 46 | 13204 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | trim shelterbet between poles 212283 & 393500 | .
2689 |  | JE24030963 | 2464 TAIRUA WHITIANGA ROAD KAIMARAMA WHITIANGA | Eastern | COROGLEN | 2024-09-16 | 9:00 | 2024-09-16 | 15:14 | 0.052535 | 0.00014071 | 51 | 19042 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Helicopter stringing fibre between poles W12662 & W12702 / W1739. Request HLT 66kV lines next to works Tairua CB60 & Whitianga CB50 . | .
2690 |  | JE24030998 | 2559 STATE HIGHWAY 4 WAIMARINO WANGANUI | Western | IRIRANGI | 2024-09-16 | 9:56 | 2024-09-16 | 14:06 | 0.018169 | 0.00015726 | 57 | 6586 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Vegetation - Asplundh contractor to clear vegetation between pole 783740 and 783739 | .
2691 |  | JE24031263 | Turakina Valley Road, Turakina, Whanganui | Western | TURAKINA | 2024-09-16 | 9:46 | 2024-09-16 | 15:56 | 0.023468 | 6.3456e-05 | 23 | 8506 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | HV reconductoring from and including pole 851027 and 794726 | .
2692 |  | JE24032373 | 10 KIMBERLEY GROVE WESTBROOK PALMERSTON NORTH | Western | TREMAINE AVE | 2024-09-16 | 9:30 | 2024-09-16 | 16:51 | 0.066815 | 0.00015174 | 55 | 24217 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE BADLY RUSTED TRANSFORMER T6/196. JOINT 11KV/400V CABLES.WHOLE SITE TO BE REDONE. ADDITIONAL NOTE: HAVE SPOKEN WITH ASHMEET WHO IS HAPPY TO OPERATE, ISOLATE & EARTH AT SWITCHGEAR 200. | .
2693 |  | JE24033954 | KOHETE RD | Western | KOHETE RD | 2024-09-16 | 9:39 | 2024-09-16 | 12:00 | 0.00077724 | 5.5179e-06 | 2 | 282 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: Fuses 5321 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 12:00 Cause: Line Clash Weather (wind/rain): Windy Follow up required (select advisory)? No | .
2694 |  | JE24034025 | TURAKINA | Western | TURAKINA | 2024-09-16 | 12:06 | 2024-09-16 | 15:53 | 0.00062523 | 2.759e-06 | 1 | 227 | Unplanned | WILDLIFE - BIRD | Fuses Location: 4500 No. Fuses: 2 Fuse Amp Size:10A TIME CLOSED: 15:52 Cause: Bird Strike Weather (wind/rain): Raining Follow up required (select advisory)NA | .
2695 |  | JE24034084 | TIRAUMEA | Western | TIRAUMEA | 2024-09-16 | 19:10 | 2024-09-16 | 21:06 | 0.0054283 | 4.6902e-05 | 17 | 1968 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: V83 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 21:06 Cause: possible bird strike (ducks flying around) Weather (wind/rain): calm Follow up required (select advisory)?n | .
2696 |  | JE24030786 | 29 MAIN ROAD KATIKATI KATIKATI | Eastern | MURAL TOWN | 2024-09-15 | 22:39 | 2024-09-16 | 0:26 | 0.010656 | 9.9323e-05 | 36 | 3862 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Linkbox maintenance at TB2-029 | .
2697 |  | JE24033450 | 500 State Highway 3, Bulls | Western | BULLS | 2024-09-15 | 8:34 | 2024-09-15 | 15:02 | 0.092002 | 0.00023727 | 86 | 33347 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Reconductor from Pole 801536 to 801519. Replace insulators at poles 801532/801533, 801526, 801525. Remove Temp ABS TEMP116 | .
2698 |  | JE24033458 | 204 BRIDGE STREET BULLS BULLS | Western | SANSONW40-OHAKEA3132 33KV | 2024-09-15 | 23:44 | 2024-09-15 | 23:49 | 0.019048 | 0.0036336 | 1317 | 6904 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Restore Bulls to normal configuration - Break Make required to bring Bulls back to Matron GXP. | .
2699 |  | JE24033898 | 1228 HUIA ROAD, PONGAROA | Western | TIRAUMEA | 2024-09-15 | 14:25 | 2024-09-15 | 15:08 | 0.00035798 | 8.2769e-06 | 3 | 130 | Unplanned | VEGETATION - INSIDE ZONE | Tree / branches in / on lines past pole P27302 De-energised at fuses V79 Tree / branches removed from lines with a saw on a hot stick Full power restored | .
2700 |  | JE24033915 | RIVERLEA | Western | RIVERLEA | 2024-09-15 | 23:14 | 2024-09-16 | 0:31 | 0.0035928 | 4.6902e-05 | 17 | 1302 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 5976 No. Fuses: 2 Fuse Amp Size: 15 Amp TIME CLOSED: 00:30 hrs Cause: Unk Weather (wind/rain): Calm Follow up required (select advisory)? | .
2701 |  | JE24030984 | 100 ARMSTRONG STREET ROSLYN PALMERSTON NORTH | Western | ARMSTRONG ST | 2024-09-14 | 8:30 | 2024-09-15 | 15:57 | 0.045154 | 7.4492e-05 | 27 | 16366 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | AP-01 ISOLATE TX T6/576, REMOVE THE HV CABLE FROM THE TRANSFORMER, MELT THE PITCH IN THE TX HV BUSHING ENCLOSURE READY FOR NEW CABLE TERMINATION, REPAIR LV BUSHING LEAK AP-02 REPLACE POLE P40704 WITH A NEW 12.5MTR BUSK POLE WITH A FUSED ABS (10891) WHICH WILL REPLACE SWITCH GEAR 312 (SWITCH 312 WILL BE REMOVED FROM THE NETWORK) INSTALL 11KV UNDERGROUND CABLE FROM THE FUSED ABS TO TRANSFORMER T6/576. | .
2702 |  | JE24033819 | SEAWARD COAST | Western | SEAWARD COAST | 2024-09-14 | 2:57 | 2024-09-14 | 5:39 | 0.013602 | 8.5528e-05 | 31 | 4930 | Unplanned | WILDLIFE - BIRD | Fuses Location: 8475 No. Fuses: 2 Fuse Amp Size: 20 Amp TIME CLOSED: 05:39 Cause: Bird strike Weather (wind/rain): Calm Follow up required (select advisory)? N | .
2703 |  | JE24033842 | MAHOE | Western | MAHOE | 2024-09-14 | 9:11 | 2024-09-14 | 12:31 | 0.0016497 | 8.2769e-06 | 3 | 598 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: 5768 No. Fuses: 3 & Replaced 1 x barrel Fuse Amp Size: 2 TIME CLOSED: 12:30 Cause: old age Weather (wind/rain): rain Follow up required (select advisory)?n Loop test improved after old barrel and fuses replaced | .
2704 |  | JE24033860 | KATIKATI | Eastern | KATIKATI | 2024-09-14 | 14:31 | 2024-09-14 | 15:13 | 0.0064015 | 0.0001545 | 56 | 2320 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV Fuses SC2-006 Protection flags (nil when none): Fuses operated. CAUSE: Tree branch came down on the HV Lines Location: Pole 423 156 & 423 387 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Rain LFI's operated : Yes, at Pole 327844. Follow up required (select advisory)? No Additional fault restoration comments: Tree branch fell across HV lines Fuses SC2-006 then operated as per design. ( 2 x 30 Amp replaced) Full Power restored at 15:12 | .
2705 |  | JE24030525 | 37 DENBIGH ROAD MIDHIRST STRATFORD | Western | MOUNTAIN RD | 2024-09-13 | 9:31 | 2024-09-13 | 13:35 | 0.039783 | 0.00035315 | 128 | 14420 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace U bolts that secure ABS to the steel work. Worksite 12731 Napa 114723 & 114695 were combined | .
2706 |  | JE24030603 | MATAKANA RD | Eastern | MATAKANA RD | 2024-09-13 | 11:01 | 2024-09-13 | 13:36 | 0.009798 | 6.3456e-05 | 23 | 3551 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Linkbox maintenance at SC3-099 | .
2707 |  | JE24030618 | 98 MANAWAPOU ROAD HAWERA HAWERA | Western | KETEMARAE RD | 2024-09-13 | 8:30 | 2024-09-13 | 17:09 | 0.074735 | 0.00027866 | 88 | 27088 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove ABS structure WH824 and replace with the new ENTEC sectionaliser 12751. Generate transformers 5567E & 5568E during the outage. Please reference switching NAPA 110114 to confirm possible clash depending on how switching has been written . | .
2708 |  | JE24030739 | 620 KIRI ROAD TE KIRI HAWERA | Western | IHAIA RD | 2024-09-13 | 9:00 | 2024-09-13 | 15:21 | 0.0020999 | 5.5179e-06 | 2 | 761 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace tx pole 715659. install new pillar box at boundary. | .
2709 |  | JE24030767 | 2464 TAIRUA WHITIANGA ROAD KAIMARAMA WHITIANGA | Eastern | COROGLEN | 2024-09-13 | 9:03 | 2024-09-13 | 15:00 | 0.04631 | 0.00012967 | 47 | 16785 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Drone installing draw rope between poles 248515 & 248513/248514. Clearing trees around pole W1734/W12683 | .
2710 |  | JE24033443 | 420 STATE HIGHWAY 3, BULLS | Western | BULLS | 2024-09-13 | 8:49 | 2024-09-13 | 16:01 | 0.041701 | 9.6564e-05 | 35 | 15115 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Reconductor from 801595 to 801536 "Break make added to move open point" | .
2711 |  | JE24033667 | HAURAKI RD | Eastern | HAURAKI RD | 2024-09-13 | 5:53 | 2024-09-13 | 7:07 | 0.0024791 | 3.3108e-05 | 12 | 899 | Unplanned | WILDLIFE - BIRD | Fuses Location: FP1996 No. Fuses: 3 Fuse Amp Size: 10 Amp TIME CLOSED: 07:07 Cause: Dead bird found on the ground. Weather (wind/rain): Calm Follow up required (select advisory)? Yes Field Switcher found the dead duck under the O/H Line. | .
2712 |  | JE24033683 | GLOVER RD WEST | Western | GLOVER RD WEST | 2024-09-13 | 8:17 | 2024-09-13 | 8:22 | 0.0075876 | 0.0015864 | 575 | 2750 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Unplanned outage while NAPA 113574 taking place. Customers not advertised. Recloser 8820 Open/tripped 08:17, Recloser 8820 closed 08:22 | .
2713 |  | JE24033732 | 128 CARTERS LINE, CARTERTON | Western | PARK RD | 2024-09-13 | 13:48 | 2024-09-13 | 15:09 | 0.0042277 | 5.242e-05 | 19 | 1532 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Location: 1/. 824168 Split HV Cross arm 2/. 842175 Twisted Cross arm Cause: Aged Isolation: ABS S316 Additional Info: Replaced 2x HV Cross arms and hardware | .
2714 |  | JE24033736 | 541 HENRY WATSON ROAD, MATAMATA | Eastern | PIAKOITI RD | 2024-09-13 | 13:01 | 2024-09-13 | 13:30 | 0.00016186 | 5.5179e-06 | 2 | 59 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: TX TC4381 Fuses CAUSE: Broken stay-wire at TX Pole TC4381 Location: Pole H3673 (TX TC4381) Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Calm Follow up required (select advisory)? No Additional fault restoration comments: Broken stay-wire at Pole H3673. HV Isolation carried out as a safety measure. Repairs carried out and Power restored at 13:30 | .
2715 |  | JE24033806 | PIHAMA | Western | PIHAMA | 2024-09-13 | 18:42 | 2024-09-13 | 19:41 | 0.00032267 | 5.5179e-06 | 2 | 117 | Unplanned | WILDLIFE - BIRD | Fuses Location: TA839 No. Fuses: 2 Fuse Amp Size: 3 Amp TIME CLOSED: 19:40 Cause: Bird strike Weather (wind/rain): Calm Follow up required (select advisory)? | .
2716 |  | JE24033809 | sub_PAR | Western | MAURICEVILLE | 2024-09-13 | 19:14 | 2024-09-14 | 16:36 | 0.33372 | 0.0014374 | 241 | 120960 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11 kV CB3 Protection flags (nil where none): E/F CAUSE: Broken Insulator Location: 356232 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: op Weather (wind/rain): rain LFI (Y/N + Comments): N/A Follow up Required (select advisory)? n Additional fault restoration comments: Only one FM attended Fault between ABS's U22 & U31 Unable to find a safe location to make line break FM to return in morning with polymers to be able to make break. Will also try to get help from Palmy depot Line patrolled, could not find a fault, line break put in place, livened line Rec U39 tripped, isolated line again, opened the TFR Fuses in faulted area, re-livened again Rec U39 tripped, another patrol carried out and a broken insulator was found at pole 356232, fault fixed, line break closed, full power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2717 |  | JE24033814 | TAWAHA | Western | TAWAHA | 2024-09-13 | 18:46 | 2024-09-13 | 20:03 | 0.00084652 | 1.1036e-05 | 4 | 307 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 8044 No. Fuses: 2 Fuse Amp Size: 8A TIME CLOSED: 2002 Cause: suspect birds Weather (wind/rain): fine Follow up required (select advisory)? | .
2718 |  | JE24033816 | TE ROTI | Western | TE ROTI | 2024-09-13 | 22:06 | 2024-09-14 | 0:33 | 0.078301 | 0.00092977 | 337 | 28381 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV CB R61 Protection flags (nil where none): C Ph E/F CAUSE: Unknown, Not Fault Found Location: Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Y Pole 733919 Follow up Required (select advisory)? N Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2719 |  | JE24033818 | DYERVILLE | Western | DYERVILLE | 2024-09-13 | 22:46 | 2024-09-14 | 1:15 | 0.00082133 | 5.5179e-06 | 2 | 298 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 7150 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 0115 Cause: Unknown Weather (wind/rain): light rain Follow up required (select advisory)? | .
2720 |  | JE24029669 | 52 CARLTON STREET BELLEVUE TAURANGA | Eastern | BELLEVUE RD | 2024-09-12 | 9:20 | 2024-09-12 | 15:15 | 0.075131 | 0.00060421 | 219 | 27232 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Linkbox maintenance at TC4-066 & TD4-578. | .
2721 |  | JE24030021 | 23 PATAPU STREET WHANGANUI EAST WANGANUI | Western | EASTOWN RD | 2024-09-12 | 9:16 | 2024-09-12 | 13:45 | 0.041625 | 0.0001545 | 56 | 15087 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install line break at pole 768585, replace X arms on pole 768600, remove line break at pole 768585 | .
2722 |  | JE24030118 | 125 STATE HIGHWAY 3 WESTMERE WANGANUI | Western | WESTMERE PEAT ST | 2024-09-12 | 9:53 | 2024-09-12 | 14:35 | 0.0038852 | 1.3795e-05 | 5 | 1408 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Upgrade TX 4523W to 50KVA | .
2723 |  | JE24030426 | Turakina Valley Road, Turakina, Whanganui | Western | TURAKINA | 2024-09-12 | 9:35 | 2024-09-12 | 15:21 | 0.021918 | 6.3456e-05 | 23 | 7944 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles and crossarms from and including pole 851027 and 794726 | .
2724 |  | JE24030447 | 2919 CAPE PALLISER ROAD CAPE PALLISER FEATHERSTON | Western | BURNSIDE | 2024-09-12 | 8:45 | 2024-09-12 | 14:43 | 0.16677 | 0.00046626 | 169 | 60446 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re sag 11kv conductors past ABS S561 | .
2725 |  | JE24030455 | 96 TIKI ROAD COROMANDEL COROMANDEL | Eastern | KAPANGA ROAD | 2024-09-12 | 23:00 | 2024-09-13 | 1:58 | 0.093517 | 0.00055179 | 200 | 33896 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Disconnect HV cable jumpers at pole 499575/499576 (Isolates cable to IP379). Connect temporary cable to supply transformer TC3773 from Fuses TEMP90 at pole V12605. | .
2726 |  | JE24030471 | 147 PERRY STREET MASTERTON MASTERTON | Western | CORADINE ST | 2024-09-12 | 9:00 | 2024-09-12 | 15:02 | 0.00099856 | 2.759e-06 | 1 | 362 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Change T672 at rail way station due to end of life requested project by powerco | .
2727 |  | JE24030519 | 325 KIRIHAU ROAD KORU NEW PLYMOUTH | Western | PIONEER RD | 2024-09-12 | 9:01 | 2024-09-12 | 14:12 | 0.014622 | 4.6902e-05 | 17 | 5300 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace conductors between poles 755303 and 755316 | .
2728 |  | JE24030552 | 1541 WAITUNA TAPUAE ROAD WAITUNA WEST FEILDING | Western | WAITUNA | 2024-09-12 | 8:30 | 2024-09-12 | 13:13 | 0.010905 | 3.8625e-05 | 14 | 3952 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Vegetation work contractor - Asplundh to complete vegetation work between P11911 - P11912 | .
2729 |  | JE24030584 | 9 WEKA STREET MATUA TAURANGA | Eastern | MATUA POINT | 2024-09-12 | 9:03 | 2024-09-12 | 14:36 | 0.056012 | 0.0001683 | 61 | 20302 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace leaking GMT TC3-067 with a new 300kVA GMT | .
2730 |  | JE24030586 | 162 APITI ROAD KIMBOLTON FEILDING | Western | APITI | 2024-09-12 | 9:31 | 2024-09-12 | 12:36 | 0.016342 | 8.8287e-05 | 32 | 5923 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace ABS P42 and upgrade earthing | .
2731 |  | JE24030606 | 910 MAATA ROAD RAWHITIROA ELTHAM | Western | RAWHITIROA | 2024-09-12 | 8:34 | 2024-09-12 | 15:46 | 0.050796 | 0.00072561 | 134 | 18411 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Cut line break at pole 736120 and replace 11kv pin at pole 736163 Replace tx pole 736127 and replace HV cross arms at 736125, 736126, 736132, 736134 ,736133 & fuses at pole 736133 . DNO 2404008 on fuses 4942 reinstate line break at end of day | .
2732 |  | JE24030613 | 436 MAUNGARANGI ROAD PAENGAROA TE PUKE | Eastern | MANGOREWA | 2024-09-12 | 8:56 | 2024-09-12 | 15:10 | 0.055735 | 0.00014898 | 54 | 20201 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv/400vt poles 221887, 221886, 221888 & 221860. Replace 11kv cross arms @ pole 221859. | .
2733 |  | JE24033506 | MOUNTAIN | Eastern | MOUNTAIN | 2024-09-12 | 4:55 | 2024-09-12 | 8:32 | 0.0025309 | 1.9313e-05 | 7 | 917 | Unplanned | WILDLIFE - POSSUM | REGULATORY INFORMATION Voltage & Device ID: REC RC31 Protection flags (nil where none): EF CAUSE: Possum on the lines, removed with hot sticks Location: Pole C3455 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): fine LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: | .
2734 |  | JE24033509 | PIAKOITI RD | Eastern | PIAKOITI RD | 2024-09-12 | 5:49 | 2024-09-12 | 9:04 | 0.066027 | 0.00033935 | 123 | 23932 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV Sec 13065/2 Protection flags (nil where none): O/C E/F B - C Ø CAUSE: Pukeko in the lines lines down Location: Pole H3630 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: cursory Weather (wind/rain): fine LFI (Y/N + Comments): LFI's have all comms failed Follow up Required (select advisory)? Additional fault restoration comments: | .
2735 |  | JE24033510 | SOUTH RD NGARIKI | Western | SOUTH RD NGARIKI | 2024-09-12 | 6:37 | 2024-09-12 | 7:47 | 0.00078084 | 1.1036e-05 | 4 | 283 | Unplanned | WILDLIFE - BIRD | Fuses Location: ng380 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 07:47 Cause: duck Weather (wind/rain): calm Follow up required (select advisory)? | .
2736 |  | JE24033512 | TIROHIA-KARANGAHAKE | Eastern | TIROHIA-KARANGAHAKE | 2024-09-12 | 6:39 | 2024-09-12 | 9:47 | 0.0025881 | 1.3795e-05 | 5 | 938 | Unplanned | WILDLIFE - BIRD | Fuses Location: FP935 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 08:35 Cause: BIRDS Weather (wind/rain): FINE Follow up required (select advisory)? Stu checking 181D and 181 related, will call back to sign off - Full power restored to both properties | .
2737 |  | JE24033515 | ARAHINA 33KV | Western | ARAHINA 33KV | 2024-09-12 | 7:34 | 2024-09-12 | 9:08 | 0.6262 | 0.012862 | 4181 | 226970 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 33kV TP Marton CB 1132 Protection flags (nil where none): A,B, Phases O/C E/F CAUSE: Wood Pidgon Cnr Pukepapa & Makariki Rd Caused 33kV Flashover Location: Cnr Pukepapa & Makariki Rd Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Curse & Oper Weather (wind/rain): Fine LFI (Y/N + Comments): NIL Follow up Required (select advisory)? Additional fault restoration comments: Wood Pidgon Cnr Pukepapa & Makariki Rd Caused 33kV Flashover Location: Cnr Pukepapa & Makariki Rd, Reported as Wire down & grass fire. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Arahina & Rata Subs Circuit that tripped: 33kV TP Marton CB 1132 DTF (KM):NA | .
2738 |  | JE24033516 | MANGATARATA | Eastern | MANGATARATA | 2024-09-12 | 15:41 | 2024-09-12 | 16:46 | 0.0010685 | 1.6554e-05 | 6 | 387 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Replace Transformer TC1640 Isolation: TC1640 Fuses CAUSE: defective Temp generation (stage details when used): N | .
2739 |  | JE24033595 | MANGATOKI | Western | MANGATOKI | 2024-09-12 | 14:26 | 2024-09-12 | 19:05 | 0.0023134 | 8.2769e-06 | 3 | 839 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: Fuses for Transformer 2074T CAUSE: Rusted out Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: N/A Weather (wind/rain): Calm Follow up required (select advisory)? N Additional fault restoration comments: Transformer 2074T Replaced | .
2740 |  | JE24033611 | KAPONGA 33kV | Western | KAPONGA 33kV | 2024-09-12 | 14:32 | 2024-09-12 | 15:57 | 0.15203 | 0.0018154 | 658 | 55105 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 33kV Recloser 3173 Protection flags (nil where none): E/F A Phase CAUSE: Unknown suspect Bird Strike Location: After ABS 445 site Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Curse Weather (wind/rain): Light Breeze LFI (Y/N + Comments): Yes ABS 445 Follow up Required (select advisory)? Additional fault restoration comments: MABS 3194 wouldn''t operate for backup supply, 2R to fix asap Comms at Gas/Sw 3194 is ok 100% comms at site SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Kaponga Sub Circuit that tripped: Rec 3173 33kV Circuit DTF (KM): N/A Loose serial cable found at Recloser 3194, Checked & tested under 2R by Nick Patten | .
2741 |  | JE24033655 | TARATA | Western | TARATA | 2024-09-12 | 19:11 | 2024-09-12 | 21:04 | 0.0052855 | 4.6902e-05 | 17 | 1916 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 5335 No. Fuses: 2 Fuse Amp Size: 10 Amp TIME CLOSED: 21:04 Cause: Calm Weather (wind/rain): Calm Follow up required (select advisory)? N | .
2742 |  | JE24033662 | sub_ELT | Western | ELTHAM TOWN NORTH | 2024-09-12 | 22:23 | 2024-09-12 | 23:32 | 0.077366 | 0.001145 | 415 | 28042 | Unplanned | WILDLIFE - POSSUM | REGULATORY INFORMATION Voltage & Device ID: 11kV CB R21 Protection flags (nil where none): B Ph E/F CAUSE: Possum Location: Pole 734886 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Calm LFI (Y/N + Comments): N/A Follow up Required (select advisory)? N Additional fault restoration comments: Possum on lines, clear with hot sticks SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2743 |  | JE24030068 | 1611 STATE HIGHWAY 27 PATETONGA MORRINSVILLE | Eastern | PATETONGA | 2024-09-11 | 8:46 | 2024-09-11 | 15:19 | 0.014102 | 3.5867e-05 | 13 | 5111 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace HV arms on poles K13223, K13224,K13228, K13229, K13230, K13231, K13236,K13237, K13238 | .
2744 |  | JE24030114 | 269 KIRIHAU ROAD KORU NEW PLYMOUTH | Western | PIONEER RD | 2024-09-11 | 9:04 | 2024-09-11 | 14:19 | 0.014755 | 4.6902e-05 | 17 | 5348 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace conductor between poles 755319 and 755303. | .
2745 |  | JE24030190 | 15 MILSON LINE ROSLYN PALMERSTON NORTH | Western | RUAHINE | 2024-09-11 | 23:01 | 2024-09-12 | 3:10 | 0.12114 | 0.00048558 | 176 | 43907 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU Oil maintenance at 152/153 & 156/157 & 142/143 | .
2746 |  | JE24030214 | 346 STATE HIGHWAY 3 KAITOKE WANGANUI | Western | MARANGAI | 2024-09-11 | 9:30 | 2024-09-11 | 11:38 | 0.038378 | 0.00030073 | 109 | 13910 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace X arms on pole 793209 | .
2747 |  | JE24030280 | 84 SOLOMON STREET BROOKFIELD TAURANGA | Eastern | CENTRAL OTUMOETAI | 2024-09-11 | 8:30 | 2024-09-11 | 14:55 | 0.098755 | 0.00025658 | 93 | 35794 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install new RMU CFC (14958) between 9117/3 and 13284/3 and transfer 11kv cable from 9117/2 to new rmu 14958/2 | .
2748 |  | JE24030300 | 265 RICHARDSONS LINE MILSON PALMERSTON NORTH | Western | BUNNYTHORPE | 2024-09-11 | 9:03 | 2024-09-11 | 14:27 | 0.02689 | 8.2769e-05 | 30 | 9746 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace multiple 11KV crossarms Richardsons Line, Setters Line, between poles P39680 & P39370. | .
2749 |  | JE24030375 | 66 TALBOT STREET WHANGANUI EAST WANGANUI | Western | KIWI ST | 2024-09-11 | 9:16 | 2024-09-11 | 11:00 | 0.066206 | 0.00064008 | 232 | 23997 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace X arms on pole 768194 | .
2750 |  | JE24030452 | 6 WINDSOR ROAD BELLEVUE TAURANGA | Eastern | SHERWOOD ST | 2024-09-11 | 9:01 | 2024-09-11 | 10:47 | 0.027117 | 0.00025382 | 92 | 9829 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Linkbox maintenance at TD4-087 | .
2751 |  | JE24030456 | 162 BELLEVUE ROAD BELLEVUE TAURANGA | Eastern | BROOKFIELD TCE | 2024-09-11 | 13:00 | 2024-09-11 | 14:48 | 0.035354 | 0.00032832 | 119 | 12814 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Linkbox maintenance at TD4-089 | .
2752 |  | JE24030461 | 58 MANGAROA ROAD EKETAHUNA EKETAHUNA | Western | HUKANUI | 2024-09-11 | 10:00 | 2024-09-11 | 16:31 | 0.10981 | 0.00028141 | 102 | 39800 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To remove pole P08262,install recloser 10908/2, bypass ABS/1, Links /4,/6 and remove ABS S6 and jumper through . | .
2753 |  | JE24033375 | TAVERNER ST | Western | TAVERNER ST | 2024-09-11 | 6:39 | 2024-09-11 | 8:30 | 0.0012255 | 1.1036e-05 | 4 | 444 | Unplanned | VEGETATION - OUTSIDE ZONE | Found sticks on Line at Pole 820720 removed with Hot sticks Also Found Transformer T3383 3 Blown Fuses Used 5 X 10 Fuse at fuses 7536 1 X Barrel and 3 x 3amp Fuses at Transformer All Good | .
2754 |  | JE24033378 | LANGDALE | Western | LANGDALE | 2024-09-11 | 7:51 | 2024-09-11 | 8:56 | 0.0025016 | 3.8625e-05 | 14 | 907 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Floating conductor at Pole 838332 Isolated at Fuses 7889 | .
2755 |  | JE24033383 | MATAKANA RD | Eastern | MATAKANA RD | 2024-09-11 | 7:27 | 2024-09-11 | 11:35 | 0.010945 | 4.4143e-05 | 16 | 3967 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: TC3-117 No. Fuses:2 Fuse Amp Size: 3 TIME CLOSED: 11:35 Cause: Unknown Weather (wind/rain): calm Follow up required (select advisory)?N | .
2756 |  | JE24033413 | OPOUTERE | Eastern | OPOUTERE | 2024-09-11 | 9:31 | 2024-09-11 | 11:00 | 0.0076063 | 8.5528e-05 | 31 | 2757 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Remove Generation from Transformer TC5177 close 11kv Cable break - E00151 Emergency outage Relates JE24032372 | .
2757 |  | JE24029896 | 12 FINNERTY ROAD NGAERE STRATFORD | Western | MAHOE | 2024-09-10 | 9:11 | 2024-09-10 | 14:49 | 0.02987 | 8.8287e-05 | 32 | 10827 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove ABS 6126, remove inline links 6349. replace pole 735346 with new entec pole structure 12765/2 | .
2758 |  | JE24029997 | 68 COLE STREET MASTERTON MASTERTON | Western | CORADINE ST | 2024-09-10 | 8:30 | 2024-09-10 | 14:17 | 0.11986 | 0.00034763 | 126 | 43445 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace defected poles 830704 830732 830716 830719 | .
2759 |  | JE24030001 | 400 MAUNGARANGI ROAD PAENGAROA TE PUKE | Eastern | MANGOREWA | 2024-09-10 | 8:55 | 2024-09-10 | 14:56 | 0.053753 | 0.00014898 | 54 | 19483 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv cross arms @ poles 221858,221857,317528. Replace 11kv overhead conductors between poles 317528 & 486243. | .
2760 |  | JE24030017 | 308 MANGAPIPI EAST ROAD WAITUNA WEST FEILDING | Western | WAITUNA | 2024-09-10 | 9:16 | 2024-09-10 | 13:04 | 0.0044011 | 1.9313e-05 | 7 | 1595 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Vegetation work contractor - Asplundh to complete vegetation work between P11929 - 475228 | .
2761 |  | JE24030019 | 220 BLUFF RANGITUMAU ROAD RANGITUMAU MASTERTON | Western | MIRO ST | 2024-09-10 | 9:49 | 2024-09-10 | 13:46 | 0.0032767 | 1.3795e-05 | 5 | 1188 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | AP to replace poles between 441810 and 834840 including Tx T1988 NO OMS JOB Created | .
2762 |  | JE24030028 | 660B ROBERTS LINE KELVIN GROVE PALMERSTON NORTH | Western | STONEY CREEK | 2024-09-10 | 9:30 | 2024-09-10 | 13:05 | 0.0017791 | 8.2769e-06 | 3 | 645 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Leaking TX T6/569 replace TX arms | .
2763 |  | JE24030046 | 49 WALLSCOURT PLACE NORMANBY HAWERA | Western | TAWHITI RD | 2024-09-10 | 9:15 | 2024-09-10 | 14:25 | 0.090582 | 0.00029245 | 106 | 32832 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace spalling poles 722482, 722534, 722542. Replace HV/LV xarms pole 722537 | .
2764 |  | JE24030120 | 210 DOUGLAS ROAD DOUGLAS STRATFORD | Western | HUIROA | 2024-09-10 | 9:30 | 2024-09-11 | 15:11 | 0.012362 | 3.8625e-05 | 7 | 4481 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | asplundh to remove trees between poles 759572 to 759575 | .
2765 |  | JE24030206 | 16 ADMIRAL PLACE TAKARO PALMERSTON NORTH | Western | RANGITIKEI | 2024-09-10 | 23:00 | 2024-09-11 | 4:48 | 0.10242 | 0.00057662 | 209 | 37124 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Perform oil maintenance at FS145/282/283 & FS140/357/358 On opening Sw/Gear 10094/3 indicators remained lit. Investigation found a LV back feed point left in place on Transformer T6/422. Back feed removed but not enough time to complete maintenance work. Crew will reapply for a shutdown to complete. Can we follow up to see if the back feed point can be used to complete works without having to have an outage. | .
2766 |  | JE24030207 | 64 PAUL ROAD WHENUAKITE WHITIANGA | Eastern | COROGLEN | 2024-09-10 | 9:45 | 2024-09-10 | 16:05 | 0.096449 | 0.00025382 | 92 | 34958 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Helicopter stringing fibre between poles 383445 / 383446 & W13550 / W13549. Request HLT 66kV lines next to works WHTCB50 & TAICB60 | .
2767 |  | JE24030917 | 500 State Highway 3, Bulls | Western | BULLS | 2024-09-10 | 8:36 | 2024-09-10 | 18:32 | 0.083878 | 0.00014071 | 51 | 30402 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Poles & Cross arms between and including Poles 801530 and 803562. Reconductor 33kV from Poles 803562-801530 & 803562 - 803563 | .
2768 |  | JE24033207 | TOWNSHIP & LS | Eastern | TOWNSHIP & LS | 2024-09-10 | 10:54 | 2024-09-10 | 14:45 | 0.0038203 | 1.6554e-05 | 6 | 1385 | Unplanned | THIRD PARTY INTERFERENCE - OVERHEAD CONTACT | REGULATORY INFORMATION Voltage & Device ID: PAO 3142 / 3252 A/R Protection flags (nil where none): B & C Ø O/C E/F CAUSE: irrigator under the lines has caused a flash over to the pole. Location: WHUPKO0134 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: Cursory patrolled Weather (wind/rain): Calm LFI (Y/N + Comments): Follow up Required (select advisory)? Yes NDR to follow Additional fault restoration comments: Break before make switching to move FRM sub to WHU GXP due to unknown issue on the line and risk of trip at WHU. Line now deenergized for safety until inspection can be done during daylight. The farmer has a towed irrigator that he has placed under the lines. Possibly needs a follow up to explain the dangers of this. The Pole is arcing and making a rattling noise. Arcing stops when PAO 3142 circuit is deenergized. FRM advised to submit a urgent NAPA to investigate the pole and see if it needs replacement. Both circuits were isolated and earthed. Pole replaced 12m and associated cross arms. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): FRM / TTU Circuit that tripped: 3142 / 3252 DTF (KM): | .
2769 |  | JE24033219 | KEENAN RD | Eastern | KEENAN RD | 2024-09-10 | 5:50 | 2024-09-10 | 8:01 | 0.092029 | 0.0021272 | 771 | 33356 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 8 Protection flags (nil where none): A - B - C Ø INVT CAUSE: Unknown, lines patrolled. Location: Unknown. Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4, Cursory patrolled Weather (wind/rain): Calm LFI (Y/N + Comments): Yes Follow up Required (select advisory)? SEC 13017 has a note on it saying an OMS job has been completed and the Sectionaliser defected. Can we follow up to see a time frame on this and to see if it should be a DNO due to it affecting the operational use of the SZR Additional fault restoration comments: Lines patrolled and sectionalized, no fault cause could be found. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2770 |  | JE24033287 | MANGATEPARU | Eastern | MANGATEPARU | 2024-09-10 | 10:04 | 2024-09-10 | 11:58 | 0.0031426 | 2.759e-05 | 10 | 1139 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: FC2147 No. Fuses: 2 Fuse Amp Size: 15A TIME CLOSED: 11:58 Cause: Unknown, lines patrolled. Weather (wind/rain): Calm Follow up required (select advisory)? No | .
2771 |  | JE24033299 | PARK RD | Western | PARK RD | 2024-09-10 | 11:48 | 2024-09-10 | 12:09 | 5.849e-05 | 2.759e-06 | 1 | 21 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Nut coming off at Crossarm Dropped Fuse at Pole 819753 ( Not on scada or E Map )and re nuted it with 2 Nuts | .
2772 |  | JE24033303 | COROGLEN | Eastern | COROGLEN | 2024-09-10 | 14:14 | 2024-09-10 | 17:41 | 0.0034218 | 1.6554e-05 | 6 | 1240 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: TC3467 Fuses CAUSE: Lightning Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): N/A Circuit patrolled & type: No Weather (wind/rain): Calm Follow up required (select advisory)? No Additional fault restoration comments: 1 x 30kVA 3 Ø 11kV / 400V transformer 3 x 3A HV fuses 1 x Fuse holder | .
2773 |  | JE24033314 | STRATHMORE | Western | STRATHMORE | 2024-09-10 | 16:00 | 2024-09-11 | 12:07 | 0.0066598 | 5.5179e-06 | 2 | 2414 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Transformer 4142T found to be faulty, Isolated at Transformer fuses Customer has Generator on site Transformer to be replaced on 11/09/2024 11/09/2024 Transformer Replaced | .
2774 |  | JE24033321 | PURIRI | Eastern | PURIRI | 2024-09-10 | 10:18 | 2024-09-10 | 12:32 | 0.00073576 | 5.5179e-06 | 2 | 267 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: FC2107 No. Fuses: 2 Fuse Amp Size:8 TIME CLOSED: 12:31 Cause: Wind Weather (wind/rain):windy Follow up required (select advisory)?N | .
2775 |  | JE24033323 | HOLDSWORTH | Western | HOLDSWORTH | 2024-09-10 | 15:12 | 2024-09-10 | 15:34 | 0.007506 | 0.00033659 | 122 | 2721 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Blown Jumper at Transformer T667 Due to old age Isolated at ABS S114 & ABS S321 No Back Feed | .
2776 |  | JE24033352 | HAURAKI RD | Eastern | HAURAKI RD | 2024-09-10 | 15:35 | 2024-09-10 | 17:31 | 0.0012767 | 1.1036e-05 | 4 | 463 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Transformer TC4515 No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 17:30 Cause: Unknown Weather (wind/rain): Wind Follow up required (select advisory)? No | .
2777 |  | JE24028888 | 14 MEADOWLAND STREET MATUA TAURANGA | Eastern | WARATAH ST | 2024-09-09 | 9:45 | 2024-09-09 | 12:23 | 0.047188 | 0.00029797 | 108 | 17104 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Linkbox maintenance at TC4-058 & TC4-079 | .
2778 |  | JE24029465 | 541 KAPOWAI ROAD COROGLEN WHITIANGA | Eastern | COROGLEN | 2024-09-09 | 9:31 | 2024-09-09 | 15:09 | 0.0065287 | 1.9313e-05 | 7 | 2366 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 66kV H pole CGNTAI038 - CGNTAI040. | .
2779 |  | JE24029493 | 42 TALBOT STREET WHANGANUI EAST WANGANUI | Western | EASTOWN RD | 2024-09-09 | 9:18 | 2024-09-09 | 12:23 | 0.017879 | 9.6564e-05 | 35 | 6480 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install line break at pole 768318, replace X arms pole 768207 & 768203, remove line break pole 768318 | .
2780 |  | JE24029837 | 860 MOUNTAIN ROAD WAIONGANA INGLEWOOD | Western | WAITARA RD | 2024-09-09 | 9:46 | 2024-09-13 | 13:52 | 0.030571 | 0.00016554 | 30 | 11081 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Hv outage to install line breaks + new Regulator structure 12760 Then reinstate break on poles 745296 - 745292 | .
2781 |  | JE24029844 | 121 MAUKORO LANDING ROAD PATETONGA MORRINSVILLE | Eastern | KAIHERE | 2024-09-09 | 9:06 | 2024-09-09 | 14:02 | 0.049712 | 0.0001683 | 61 | 18018 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV Pole 877806. Replace LV termination & stay insulator at 11kV Pole 877805. Replace 11kV Crossarm at Pole K1406. Straighten 11kV Pole K1429. Replace 11kV Pole 877838. | .
2782 |  | JE24029864 | 204 KIRIHAU ROAD KORU NEW PLYMOUTH | Western | PIONEER RD | 2024-09-09 | 9:01 | 2024-09-09 | 13:54 | 0.013781 | 4.6902e-05 | 17 | 4995 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv conductor from poles 755334 to 755319. | .
2783 |  | JE24029867 | 138 KAUPOKONUI HEADS ROAD KAUPOKONUI HAWERA | Western | OTAKEHO | 2024-09-09 | 9:30 | 2024-09-09 | 13:39 | 0.0013722 | 5.5179e-06 | 2 | 497 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace 11kv 2m pin arm to a 3m double term arm at pole 482021 (old pole 717814) | .
2784 |  | JE24031381 | 2 GLENN TERRACE OTUMOETAI TAURANGA | Eastern | CHERRYWOOD DRIVE | 2024-09-09 | 9:31 | 2024-09-09 | 15:24 | 0.13018 | 0.00093529 | 339 | 47183 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Linkbox maintenance at SC4-405 & SC4-402 | .
2785 |  | JE24032051 | 103 APOLLO PARADE MILSON PALMERSTON NORTH | Western | RANGITIKEI | 2024-09-09 | 8:46 | 2024-09-09 | 10:20 | 0.028602 | 0.00036694 | 133 | 10367 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Commission Switchgear 10796 Controls. Back feed except Way 3. Scada to operate and confirm then make live for NOC then NOC to operate will have switcher on site to confirm actuals. | .
2786 |  | JE24033038 | DAIRY FACTORY | Western | DAIRY FACTORY | 2024-09-09 | 5:35 | 2024-09-09 | 7:17 | 0.0025381 | 2.4831e-05 | 9 | 920 | Unplanned | WILDLIFE - BIRD | Fuses Location: 7236 No. Fuses: 2 Fuse Amp Size: 8 TIME CLOSED: 07:17 Cause: Magpies Weather (wind/rain): fine Follow up required (select advisory)? | .
2787 |  | JE24033039 | IHAIA RD | Western | IHAIA RD | 2024-09-09 | 6:05 | 2024-09-09 | 7:50 | 0.0046457 | 4.4143e-05 | 16 | 1684 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: TA191 No. Fuses: 2 Fuse Amp Size: 20A TIME CLOSED: 07:50 Cause: UNKNOWN Weather (wind/rain): FINE Follow up required (select advisory)? N | .
2788 |  | JE24033043 | EKETAHUNA | Western | EKETAHUNA | 2024-09-09 | 8:09 | 2024-09-09 | 9:10 | 0.005475 | 0.00016278 | 59 | 1984 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV U13 Protection flags (nil where none): CAUSE: Brocken Jumper Location: Pole 16897 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: Operational Weather (wind/rain): Wind from weather event in weekend LFI (Y/N + Comments): N Follow up Required (select advisory)? N Additional fault restoration comments: Jumper brocken on Pole 16897. Jumper Repaired SUBTRANSMISSION DETAILN LOS to sub (no, or sub name): N Circuit that tripped: N DTF (KM):N | .
2789 |  | JE24033058 | OHAKEA | Western | OHAKEA | 2024-09-09 | 8:18 | 2024-09-09 | 9:55 | 0.00026799 | 2.759e-06 | 1 | 97 | Unplanned | WILDLIFE - BIRD | Fuses Location: 10373 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 09:55 Cause: BIRD Weather (wind/rain): CALM Follow up required (select advisory)?N | .
2790 |  | JE24033123 | OHAUITI RD | Eastern | OHAUITI RD | 2024-09-09 | 12:23 | 2024-09-09 | 14:57 | 0.023811 | 0.0001545 | 56 | 8631 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV transformer T4535 Protection flags (nil where none): Nil CAUSE: Vehicle drove into transformer Location: T4535 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: N/A Weather (wind/rain): calm LFI (Y/N + Comments): No Follow up Required (select advisory)? NDR to follow Additional fault restoration comments: Transformer found to have a broken LV frame after being hit by a vehicle, LV frame was replaced SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2791 |  | JE24033151 | ANNEDALE | Western | ANNEDALE | 2024-09-09 | 14:13 | 2024-09-09 | 17:40 | 0.02676 | 0.0001545 | 56 | 9699 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec C1050 Protection flags (nil where none): unknown CAUSE: unknown suspect bird Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: curse Weather (wind/rain): windy LFI (Y/N + Comments): nil Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2792 |  | JE24033161 | LINDERMANN RD | Eastern | LINDERMANN RD | 2024-09-09 | 14:53 | 2024-09-09 | 16:31 | 0.0040771 | 4.1384e-05 | 15 | 1478 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses SB2-119 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 16:31 Cause: Unknown Weather (wind/rain): Wind Follow up required (select advisory)? No | .
2793 |  | JE24033181 | MANAIA | Western | MANAIA | 2024-09-09 | 15:51 | 2024-09-09 | 16:51 | 0.0001648 | 2.759e-06 | 1 | 60 | Unplanned | WILDLIFE - BIRD | Transformer M4365 Effected Fuses Location: 12640 No. Fuses: 2 Fuse Amp Size: 15A TIME CLOSED: 16:50 Cause: Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? N | .
2794 |  | JE24033203 | REVANS ST | Western | REVANS ST | 2024-09-09 | 20:00 | 2024-09-09 | 22:56 | 0.058476 | 0.00033659 | 122 | 21195 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: REC C634 Protection flags (nil where none): C phase EF CAUSE: floating conductor Location: Pole 372526 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: cursory Weather (wind/rain): windy, raining LFI (Y/N + Comments): LFI's indicated incorrectly. They Indicated the fault past ABS S505 but lines were patrolled and fault was found before that point Follow up Required (select advisory)? Follow up to check LFI's installation to prevent false indication in the future Additional fault restoration comments: | .
2795 |  | JE24033322 | PARK RD | Western | PARK RD | 2024-09-09 | 8:48 | 2024-09-09 | 14:16 | 0.048955 | 0.0005987 | 217 | 17744 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install Fuses 11486 on pole 819935, Replace pole 819944 & upgrade transformer T2011 | .
2796 |  | JE24030144 | 37 MALEME STREET GREERTON TAURANGA | Eastern | MALEME EXPRESS | 2024-09-08 | 8:34 | 2024-09-08 | 14:49 | 0.044496 | 0.00011864 | 43 | 16128 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To relocate and replace leaking 300kVA GMT TD4-094 | .
2797 |  | JE24032929 | MANGAMAIRE | Western | MANGAMAIRE | 2024-09-08 | 0:13 | 2024-09-09 | 15:56 | 0.23496 | 0.00089666 | 309 | 85164 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV, CB 5 Protection flags (nil where none): E/F, O/C B-C phase CAUSE: Lines down & broken pole Location: P43196 Red Tagged Larch Pole Failed & dropped Conductors Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: cursory Weather (wind/rain): Wind & rain LFI (Y/N + Comments): n Follow up Required (select advisory)? Additional fault restoration comments: Patrolled from Fuses R54 to near end of line by T7/191 but fallen tree blocked road. Faultman found a broken pole and lines down across riven, Heli & digger needed to make repairs, TLB at pole 460314 was made. Crews will return on Monday to carry out repairs. Repaired 9/9/24 @15:56 JE24032896 Child job outage step removed and outage step added to this job OSE24022953 as power was isolated 08/09 00:13-14:18 (feeder fault) Fuses S18 1x 8amp fuse relivened at 08/09 14:18 JE24032879 Child job outage step removed and outage step added to this job OSE24022955 as power was isolated 08/09 00:13-01:19 (feeder fault) Fuses 10381 1x 10amp fuse relivened at 08/09 15:29 | .
2798 |  | JE24032931 | CASTLEPOINT | Western | CASTLEPOINT | 2024-09-08 | 0:56 | 2024-09-08 | 9:40 | 0.091992 | 0.00041109 | 115 | 33343 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC C224/2 Protection flags (nil where none): A Ø E/F CAUSE: Lines down Location: Pole 845448 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): windy rain LFI (Y/N + Comments): None operated. The only LFI available was at Pole 483157 & the communications were offline. Upon further investigation, not shown on our SCADA diagram, field switcher stated that the LFI's near/at REC C224/2 are flashing. Upon arriving on site at LFI's at Pole 483157, field switcher confirmed LFI's are flashing red. Follow up Required (select advisory)? Yes, for the offline LFI & it is approx. the third time this week this Recloser has tripped and the root cause was unknown. Additional fault restoration comments: Recloser tripped & field crew dispatched. Two Field Switchers will be attending this fault. NOC have advised them of the protection that operated and the LFI's that are offline. Line Patrol carried out up to ABS S86 and no fault was found. Line Patrol carried out from ABS S86 towards ABS S169 and no fault was found. Line Patrol carried out from ABS S169 to Fuses 7364 (Field Switcher stated nothing abnormal was found.) Upon closing in ABS S169 , closing in on the fault, REC C2 | .
2799 |  | JE24032940 | RATAPIKO | Western | RATAPIKO | 2024-09-08 | 6:35 | 2024-09-08 | 8:51 | 0.021291 | 0.00015726 | 57 | 7717 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faultman found twisted cross arm at pole 758723 after a line patrol, line was isolated at Fused ABS 5400 to straighten cross arm and replace king bolt. | .
2800 |  | JE24032947 | STRATHMORE | Western | STRATHMORE | 2024-09-08 | 6:51 | 2024-09-08 | 10:23 | 0.0064189 | 3.0349e-05 | 11 | 2327 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: 5453 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 10:22 Cause: Line Clashing Weather (wind/rain): Very Windy Follow up required (select advisory)?n | .
2801 |  | JE24032971 | CLOTON RD NORTH | Western | CLOTON RD NORTH | 2024-09-08 | 9:12 | 2024-09-08 | 11:57 | 0.12129 | 0.0025603 | 928 | 43963 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11KV CB 5 Protection flags (nil where none): B & C ph E/F CAUSE: Broken jumpers Location: Pole 734546 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): Y - 2409009 Circuit patrolled and type: cursory Weather (wind/rain): LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Received call from customer of big bang at 28 Juliet St, Faultman found blown jumper at ABS 5558. Line was isolated at Sw/Gear 5822/1, ABS's 5713 & 5720 to make repairs. | .
2802 |  | JE24032986 | WESTMERE PEAT ST | Western | WESTMERE PEAT ST | 2024-09-08 | 8:21 | 2024-09-08 | 10:54 | 0.0012661 | 8.2769e-06 | 3 | 459 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | Fuses Location: 16077 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 10:30 Cause: Branch hit line Weather (wind/rain): wind Follow up required (select advisory)?N | .
2803 |  | JE24032987 | LINTON | Western | LINTON | 2024-09-08 | 10:42 | 2024-09-08 | 12:02 | 0.013702 | 0.00017106 | 62 | 4966 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Faultman found broken jumper on pole P02776, line was isolated at ABS H110 to repair jumper. | .
2804 |  | JE24032998 | STATION RD | Eastern | STATION RD | 2024-09-08 | 12:43 | 2024-09-08 | 15:12 | 0.0081776 | 5.5179e-05 | 20 | 2964 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses FP1342 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 1511 Cause: unknown Weather (wind/rain): fine Follow up required (select advisory)? | .
2805 |  | JE24033001 | COAST ROAD | Western | COAST ROAD | 2024-09-08 | 18:43 | 2024-09-08 | 21:32 | 0.002333 | 1.3795e-05 | 5 | 846 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Broken jumper to TFR T9/228 Isolated at Fuses 10452 Jumper repaired, also fix star point / neutral fault & Reloaded 3 x 10A Fuses at Fuses 10452 Full power restored | .
2806 |  | JE24032832 | REVANS ST | Western | REVANS ST | 2024-09-07 | 9:30 | 2024-09-07 | 10:57 | 0.00096192 | 1.1036e-05 | 4 | 349 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: Fuses 7254 No. Fuses: 2 Fuse Amp Size: 8A TIME CLOSED: 1056 Cause: suspect line clash Weather (wind/rain): windy Follow up required (select advisory)? | .
2807 |  | JE24032834 | RATAPIKO | Western | RATAPIKO | 2024-09-07 | 10:10 | 2024-09-07 | 11:46 | 0.00026403 | 2.759e-06 | 1 | 96 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Incorrect job location, correct location is TFR 2594T Fuses Location: 2594T No. Fuses: 2 Fuse Amp Size: 2 TIME CLOSED: 11:45 Cause: unknown Weather (wind/rain): rain Follow up required (select advisory)?n | .
2808 |  | JE24032843 | MAURICEVILLE | Western | MAURICEVILLE | 2024-09-07 | 11:34 | 2024-09-07 | 13:11 | 0.0002695 | 2.759e-06 | 1 | 98 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: T8/92 No. Fuses: 2 Fuse Amp Size:2 TIME CLOSED: 13:11 Cause: Unknown Weather (wind/rain): windy Follow up required (select advisory)?n | .
2809 |  | JE24032848 | WESTMERE GLADSTONE | Western | WESTMERE GLADSTONE | 2024-09-07 | 12:29 | 2024-09-07 | 18:03 | 0.047882 | 0.00032004 | 94 | 17355 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: REC 7417 Protection flags (nil where none): B phase EF CAUSE: Line down Location: Pole 359909 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): windy LFI (Y/N + Comments): LFI's at ABS S323 were not flashing but fault was past them. May need to be replaced. Follow up Required (select advisory)? Additional fault restoration comments: | .
2810 |  | JE24032866 | CASTLEPOINT | Western | CASTLEPOINT | 2024-09-07 | 16:05 | 2024-09-07 | 18:03 | 0.021533 | 0.00018209 | 66 | 7805 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: 7366 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 1803 Cause: line clash Weather (wind/rain): windy Follow up required (select advisory)? | .
2811 |  | JE24032869 | HOROEKA | Western | HOROEKA | 2024-09-07 | 16:18 | 2024-09-07 | 19:47 | 0.039188 | 0.00018761 | 68 | 14204 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec V5 Protection flags (nil where none): O/C A & B CAUSE: Broken Insulator Location: P31350 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Yes / Cursory Weather (wind/rain): Light Rain / Windy LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Replaced 2x HV Insulators & 3x Binders SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2812 |  | JE24032873 | STRATHMORE | Western | STRATHMORE | 2024-09-07 | 16:57 | 2024-09-07 | 19:41 | 0.0049551 | 3.0349e-05 | 11 | 1796 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 5453 No. Fuses: 2 Fuse Amp Size: 6 Amp TIME CLOSED: 19:40 hrs Cause: Unknown Weather (wind/rain): Windy Follow up required (select advisory)? | .
2813 |  | JE24032876 | 1530 RANGIWAHIA ROAD, KIMBOLTON, 4774 | Western | RANGIWAHIA | 2024-09-07 | 19:13 | 2024-09-07 | 20:07 | 0.00074814 | 1.3795e-05 | 5 | 271 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Cause: Twisted HV Cross Arm due to King Bolt coming free What was replaced? King Bolt Nuts replaced Where was it replaced (pole/TX/pillar box)? P03768 Additional Info: | .
2814 |  | JE24032877 | CHURCH ST | Western | CHURCH ST | 2024-09-07 | 17:45 | 2024-09-07 | 18:36 | 0.00042212 | 8.2769e-06 | 3 | 153 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: Fuses 7645 No. Fuses: 2 Fuse Amp Size: 6 Amp TIME CLOSED: 18:36 Cause: line clash Weather (wind/rain): Rain, windy Follow up required (select advisory)? No | .
2815 |  | JE24032897 | COONOOR | Western | COONOOR | 2024-09-07 | 19:34 | 2024-09-08 | 17:40 | 0.055326 | 0.00038074 | 109 | 20053 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11KV REC T42 CAUSE: trees through lines Location: P46670 & P46671 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: cursory Weather (wind/rain): wind LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Line was patrolled and sectionalized and tree through lines were found between pole's P46670 & P46671, line was isolated at Fuses T33. Crew returned on Sunday to repair the lines. | .
2816 |  | JE24032907 | EKETAHUNA | Western | EKETAHUNA | 2024-09-07 | 20:53 | 2024-09-09 | 14:06 | 0.011263 | 7.7251e-05 | 14 | 4082 | Unplanned | VEGETATION - OUTSIDE ZONE | Location: P27567 Isolation: Fuses U10 Cause: Fallen Tree from outside notice zone Weather (wind/rain): Light Rain / Windy Additional Information: Cleared Tree enough to make safe from lines. Had to refit crossarm as Kingbolt pulled out of Rotten pole Follow up required (select advisory)? Rotten Pole will be defected for replacement | .
2817 |  | JE24032915 | CLOTON RD NORTH | Western | CLOTON RD NORTH | 2024-09-07 | 21:25 | 2024-09-07 | 23:09 | 0.039765 | 0.0008001 | 145 | 14413 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Location: 734546 Isolation: 5822/1 & 5720 Back feeds: Via ABS 5699 Cause: Aged Contacts on ABS 5558 What was replaced? Temporarily Jumpered through ABS 5558 on one phase. Additional Info: ABS 5558 DNO'd for replacement DNO # 2409009 | .
2818 |  | JE24032930 | OTAUTU | Western | OTAUTU | 2024-09-07 | 23:55 | 2024-09-08 | 9:58 | 0.0066543 | 1.1036e-05 | 4 | 2412 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FM to return in morning to Patrol under 2R Faultman found line down in gully from pole 727123, line was isolated at Fuses LI155 to repair the lines down. | .
2819 |  | JE24033005 | HUKANUI | Western | HUKANUI | 2024-09-07 | 14:24 | 2024-09-08 | 15:37 | 0.17537 | 0.00011588 | 42 | 63562 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Faultman found blown jumper on Fuses S15, line was isolated at ABS S14 & Links 10858/6 to replace DDO at Fuses S15 and reconnect jumper. | .
2820 |  | JE24028592 | 68 WATT LIVINGSTONE ROAD WESTMERE WANGANUI | Western | WESTMERE PEAT ST | 2024-09-06 | 9:05 | 2024-09-06 | 14:20 | 0.029572 | 9.3805e-05 | 34 | 10719 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11KV X-Arms on pole 782688 | .
2821 |  | JE24028681 | 138 MOUNT VIEW ROAD BASTIA HILL WANGANUI | Western | BASTIA HILL | 2024-09-06 | 9:01 | 2024-09-06 | 9:57 | 0.033796 | 0.00060421 | 219 | 12249 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Cut away jumpers to fused ABS 2059, Replace fused ABS 2509, reconnect ABS live line Fused ABS 2059 not replaced, 2 x Insulators replaced, unable to replace Fused ABS 2059 under live line due to the copper conductor on the source side | .
2822 |  | JE24029429 | 52 TODDS ROAD MARTINBOROUGH MARTINBOROUGH | Western | DYERVILLE | 2024-09-06 | 10:00 | 2024-09-06 | 11:32 | 0.013714 | 0.00014898 | 54 | 4971 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Repair Fused ABS S528 | .
2823 |  | JE24029645 | 103 GLENCAIRN ROAD TURAKINA MARTON | Western | TURAKINA | 2024-09-06 | 9:01 | 2024-09-06 | 13:35 | 0.0090869 | 3.3108e-05 | 12 | 3294 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT sites and vegetation outage. Re-sag conductors between 802437- P59256, 802445 - 802447, 802464 - 802465 and replace pole 802475. Clear vegetation at 802448. | .
2824 |  | JE24029672 | 1091 NO 2 LINE FORDELL WANGANUI | Western | FORDELL | 2024-09-06 | 9:05 | 2024-09-06 | 12:57 | 0.026272 | 0.00011312 | 41 | 9522 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace X arms on pole number 792300 | .
2825 |  | JE24029768 | 47 NANRIC LANE PUKEHINA TE PUKE | Eastern | OTAMARAKAU | 2024-09-06 | 8:50 | 2024-09-06 | 12:46 | 0.008431 | 3.5867e-05 | 13 | 3056 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Linkbox SE8-011 rust repairs , 11kv cable terms cleaning | .
2826 |  | JE24029955 | 81 RODERICK LANE TE PUKE TE PUKE | Eastern | TE MATAI RD | 2024-09-06 | 9:31 | 2024-09-06 | 12:15 | 0.0013622 | 8.2769e-06 | 3 | 494 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Link box maintenance at SE5-160 & SE5-156 | .
2827 |  | JE24029972 | 36 NILE STREET WHANGANUI EAST WANGANUI | Western | IKITARA RD | 2024-09-06 | 9:30 | 2024-09-06 | 13:36 | 0.065151 | 0.00026486 | 96 | 23614 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace high voltage X arms on pole 767116 | .
2828 |  | JE24029998 | 94 RANGIURU ROAD RANGIURU TE PUKE | Eastern | MANGOREWA | 2024-09-06 | 14:00 | 2024-09-06 | 14:44 | 0.0051943 | 0.00011864 | 43 | 1883 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace broken 11kv pole 221038 Outage at 14:00 | .
2829 |  | JE24030581 | 420 STATE HIGHWAY 3, BULLS | Western | STATE HIGHWAY 3 | 2024-09-06 | 8:46 | 2024-09-06 | 14:21 | 0.032415 | 9.6564e-05 | 35 | 11749 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Poles & Xarms between & including 801536 & 801547 "CB6 non Parallel point, break make switching required" Fuses 165 Dressed open to create Job as ABS TEMP116 not on Emap LV Off TX X134, coming into outage area, isolated | .
2830 |  | JE24032735 | STRATHMORE | Western | STRATHMORE | 2024-09-06 | 11:54 | 2024-09-06 | 13:54 | 0.027046 | 0.00022623 | 82 | 9803 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolated at ABS 6494 Fuses 5272 replaced | .
2831 |  | JE24032753 | LV NAPA 114681 | Eastern | TE MATAI RD | 2024-09-06 | 12:31 | 2024-09-06 | 15:12 | 0.0022258 | 1.3795e-05 | 5 | 807 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: TX TE6-177 Fuses CAUSE: Safety measures for LV NAPA 114 681 Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: No Weather (wind/rain): Calm Follow up required (select advisory)? No Additional fault restoration comments: LV NAPA 114 681 was booked and ICP's were advertised. Due to LV being hardwired onto the Transformer (Concrete bunker type) Safety measures were required on site. All work completed and Power restored at 15:12 | .
2832 |  | JE24032768 | GRAVATT RD | Eastern | GRAVATT RD | 2024-09-06 | 14:52 | 2024-09-06 | 16:02 | 0.025753 | 0.00036694 | 133 | 9334 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV ABS IP656 Protection flags (nil where none): Nil CAUSE: Car vs Pole Location: Pole 499 821 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: ETA 20-25min, fire service advised Car vs Pole - Pole was taken out and the HV Lines remained up in the air. No risk to the public at the time. Traffic management and material was arranged by the Field Switcher. HV Pin Pole 499 821 was replaced under AP 2768 Full Power restored at 16:02 SAFETY MANAGER | .
2833 |  | JE24028876 | 556 BOAT HARBOUR ROAD WHENUAKITE WHITIANGA | Eastern | TAIRUA NORTH | 2024-09-05 | 10:45 | 2024-09-05 | 13:41 | 0.014526 | 8.2769e-05 | 30 | 5265 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Transformer TC5417. Upgrade DDOs and hardware. | .
2834 |  | JE24029393 | 3387 CAPE PALLISER ROAD CAPE PALLISER FEATHERSTON | Western | BURNSIDE | 2024-09-05 | 8:45 | 2024-09-05 | 14:31 | 0.041966 | 0.00012139 | 44 | 15211 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re sag 11kv conductors past ABS S562 | .
2835 |  | JE24029438 | 864 PUNIWHAKAU ROAD PUNIWHAKAU STRATFORD | Western | STRATHMORE | 2024-09-05 | 8:51 | 2024-09-05 | 12:39 | 0.024533 | 0.0001076 | 39 | 8892 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | asplundh to drop tree between poles 739336-739337. downer to replace xarms & fuses at pole 739293. downer to drop lines at poles 739336 to 739337 so asplundh can safely drop tree | .
2836 |  | JE24029454 | 292 PLYMOUTH ROAD KORU NEW PLYMOUTH | Western | PIONEER RD | 2024-09-05 | 9:00 | 2024-09-05 | 15:59 | 0.057256 | 0.00014347 | 52 | 20753 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 755185,755194,755195,755197,755198,755199,755200, cross arms on pole 848061. | .
2837 |  | JE24029491 | 136 STUART ROAD RANGITUMAU MASTERTON | Western | OXFORD ST | 2024-09-05 | 9:52 | 2024-09-05 | 13:27 | 0.0023777 | 1.1036e-05 | 4 | 862 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 834973 and Tx T1917 under AP | .
2838 |  | JE24029496 | 19 ROLFE WAY PUTARURU PUTARURU | Eastern | KENNEDY DRIVE | 2024-09-05 | 23:30 | 2024-09-06 | 2:06 | 0.046798 | 0.00030073 | 109 | 16962 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - IC1406-FC715-IC1418 | .
2839 |  | JE24029616 | 759 NO 1 ROAD TE PUKE TE PUKE | Eastern | ROADS | 2024-09-05 | 13:11 | 2024-09-05 | 14:50 | 0.0066039 | 6.6215e-05 | 24 | 2394 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Link box maintenance at SF5-040 & TF5-056 | .
2840 |  | JE24029617 | 847 JUNCTION ROAD MATAU STRATFORD | Western | HUIROA | 2024-09-05 | 8:30 | 2024-09-05 | 14:32 | 0.04088 | 0.00011312 | 41 | 14817 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | asplundh to remove trees from poles 709367 to 709369 | .
2841 |  | JE24029639 | 5258 STATE HIGHWAY 4 WAIMARINO WANGANUI | Western | PARAPARA | 2024-09-05 | 9:00 | 2024-09-05 | 15:40 | 0.030768 | 0.00015726 | 57 | 11152 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Vegetation - Asplundh contractor to clear vegetation between pole 783720 and 783723 | .
2842 |  | JE24029659 | 386 MAUNGARANGI ROAD PAENGAROA TE PUKE | Eastern | MAUNGARANGI RD | 2024-09-05 | 8:50 | 2024-09-05 | 14:49 | 0.0535 | 0.00014898 | 54 | 19391 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv/400vt poles 221855,221854,221882,221853 & 221852. Replace LV conductors between poles 221854, 221853 & 221852. | .
2843 |  | JE24029668 | 209 MILL ROAD PAEROA PAEROA | Eastern | TIROHIA-KARANGAHAKE | 2024-09-05 | 9:45 | 2024-09-05 | 14:04 | 0.0047994 | 1.9313e-05 | 7 | 1740 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RE-CONDUCTOR 11KV O/H LINES BETWEEN POLE'S #858341 & N13250 | .
2844 |  | JE24029693 | 2709B TAIRUA WHITIANGA ROAD KAIMARAMA WHITIANGA | Eastern | COROGLEN | 2024-09-05 | 9:30 | 2024-09-05 | 15:56 | 0.072361 | 0.00018761 | 68 | 26228 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Stinging fibre between poles 263116 & W1708. Stringing fibre outside of outage area between poles W1708 & 483881 using MADs | .
2845 |  | JE24030112 | 578 OROUA VALLEY ROAD APITI FEILDING | Western | APITI | 2024-09-05 | 10:00 | 2024-09-05 | 11:17 | 0.00021005 | 2.759e-06 | 1 | 76 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Straighten Pole P09017 and resag road crossing | .
2846 |  | JE24032045 | 83 RIDGE ROAD NORTH MANGATAINOKA PAHIATUA | Western | RUAWHATA | 2024-09-05 | 9:01 | 2024-09-05 | 12:36 | 0.0041519 | 1.9313e-05 | 7 | 1505 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove split tree hanging over 11KV line @ pole P27538 | .
2847 |  | JE24032497 | ORIGIN 2 | Western | ORIGIN 2 | 2024-09-05 | 5:54 | 2024-09-05 | 11:25 | 0.0012875 | 8.2769e-06 | 2 | 467 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 3 Protection flags (nil where none): No Flags CAUSE: Line down caused by bird strike Location: Between poles 738198 & 738199 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Calm LFI (Y/N + Comments): N Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2848 |  | JE24032502 | OVERDALE RD | Eastern | OVERDALE RD | 2024-09-05 | 6:55 | 2024-09-05 | 8:57 | 0.0033456 | 2.759e-05 | 10 | 1213 | Unplanned | WILDLIFE - BIRD | Fuses Location: FP1405 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 08:56 Cause: Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? N | .
2849 |  | JE24032512 | OHAKEA | Western | OHAKEA | 2024-09-05 | 8:27 | 2024-09-05 | 13:12 | 0.24119 | 0.00091873 | 333 | 87420 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV, Rec L77 Protection flags (nil where none): O/C A-B phase CAUSE: Fallen Tree Location: Pole P31224 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: No Weather (wind/rain): Calm LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Tree fell from outside notice zone. Asplundh cleared tree. No damage to lines. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2850 |  | JE24032531 | RATAPIKO | Western | RATAPIKO | 2024-09-05 | 9:07 | 2024-09-05 | 12:05 | 0.00049184 | 2.759e-06 | 1 | 178 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 4728T No. Fuses: 3 Fuse Amp Size: 2 Amp TIME CLOSED: 12:05 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? N | .
2851 |  | JE24032578 | 231 PAKU DRIVE, TAIRUA, 3508 | Eastern | TAIRUA NORTH | 2024-09-05 | 14:36 | 2024-09-05 | 14:48 | 0.0039368 | 0.00031452 | 114 | 1427 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: Customer experiencing High-Voltage at meterboard. Loop tests completed: No Test results: Nil Before: Voltage at TX: At TX TC4482: R 246V W 247V B 248V (Taui tested at the Transformer) Voltage at house: 245V average across all 3 Ø After: Voltage at TX: At TX TC4482: R 238V W 239V B 238V Have all connections been checked? Yes PQI Ref #: No Additional Info: At TX TC4483 : R 241V W 242V B 242V Transformer TC4482 was tapped down from position 3 to 2. Job complete | .
2852 |  | JE24032598 | GATE PA | Eastern | GATE PA | 2024-09-05 | 16:40 | 2024-09-05 | 20:44 | 0.043632 | 0.00017933 | 65 | 15815 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV Sw/Gear 9732/1 & ABS SD4-034 & Sw/Gear 9998/1 Protection flags (nil where none): Nil CAUSE: Car vs Pole 11M Busck Pole installed Location: 203418 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Police ref - P059870284, ETA needed ETA 20mins - Police Comms have been informed Car vs Pole at 203418 - Pole is still upright and Lines are in the air. Note: ABB Safelink Series 1 at Sw/Gear 9732/1 (This was explained to the Field Switcher) Repairs are being carried out under AP 2598-01 SAFETY MANAGER on closure | .
2853 |  | JE24032619 | CASTLEPOINT | Western | CASTLEPOINT | 2024-09-05 | 15:15 | 2024-09-05 | 18:52 | 0.071153 | 0.0011864 | 430 | 25790 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV, Rec C224 Protection flags (nil where none): E/F A phase CAUSE: Unknown sectionalised nothing found Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Calm LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Faultsman Opened the wrong ABS he thought the other Recloser C225 had opened he opened ABS S167. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2854 |  | JE24032653 | WAITARA RD | Western | WAITARA RD | 2024-09-05 | 20:42 | 2024-09-06 | 0:29 | 0.0024987 | 1.1036e-05 | 4 | 906 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: 8453 No. Fuses: 3 Fuse Amp Size: 6 TIME CLOSED: 00:28 Cause: Due to Weather / Lightning Weather (wind/rain): Calm Follow up required (select advisory)?Replaced Transformer 1608 but still getting low readings on one phase going to leave off over night as Pole to check is in swamp and need Day light to see whats going on Tag numbers for house and pump shed are A41935 06/09/2024 - FM have returned this morning and replaced a 63 amp fuse at the pole. Full power restored to the house. Meter board on the pole has a burned out main switch. Tagged - A41934, only a pump shed for 61 Manganui Road. Customer was advised to call a electrician. Have added this into the safety tag reg and emailed the retailer. | .
2855 |  | JE24029001 | 490 BLUFF RANGITUMAU ROAD RANGITUMAU MASTERTON | Western | OXFORD ST | 2024-09-04 | 9:45 | 2024-09-04 | 13:40 | 0.0019433 | 8.2769e-06 | 3 | 704 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 834981 and transformer T987 | .
2856 |  | JE24029004 | 8 KAKA AMU ROAD RANGITUMAU MASTERTON | Western | OXFORD ST | 2024-09-04 | 10:15 | 2024-09-04 | 11:17 | 0.00050913 | 8.2769e-06 | 3 | 185 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Tx T717 | .
2857 |  | JE24029309 | 265 NO 3 ROAD TE PUKE TE PUKE | Eastern | NO 3 ROAD | 2024-09-04 | 9:46 | 2024-09-04 | 11:38 | 0.0012386 | 1.1036e-05 | 4 | 449 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | link box maintenance at SE5-008 | .
2858 |  | JE24029313 | 19 BAYLY ROAD TE PUKE TE PUKE | Eastern | MANOEKA RD | 2024-09-04 | 13:05 | 2024-09-04 | 14:24 | 0.0017367 | 2.2072e-05 | 8 | 629 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | link box maintenance on SE5-145 | .
2859 |  | JE24029316 | 1 JACKSONS CLAIM PAUANUI HIKUAI | Eastern | PAUANUI | 2024-09-04 | 9:37 | 2024-09-04 | 13:23 | 0.11986 | 0.00055179 | 200 | 43445 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace motor drive and Compass B LFI on 9782/1. Parts never fitted , Still not operating | .
2860 |  | JE24029320 | 183 JUNCTION ROAD NORTH KIMBOLTON FEILDING | Western | RANGIWAHIA | 2024-09-04 | 10:00 | 2024-09-04 | 11:53 | 0.0012496 | 1.1036e-05 | 4 | 453 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace crossarms at P05541 and P05544 | .
2861 |  | JE24029327 | 42 WARATAH STREET MATUA TAURANGA | Eastern | WARATAH ST | 2024-09-04 | 9:11 | 2024-09-04 | 14:53 | 0.025468 | 0.00020416 | 74 | 9231 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Linkbox maintenance | .
2862 |  | JE24029364 | 500 State Highway 3, Bulls | Western | BULLS | 2024-09-04 | 8:36 | 2024-09-04 | 15:51 | 0.10312 | 0.00023727 | 86 | 37377 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Poles and Xarms between and including 801535 & 801595. Replace ABS 959. Install Temp ABS TEMP116 at pole 801535. Install New 30kVA PM TX 6598W at pole 801594. Remove LV from pole 801554 (onsite # 801553) to 801552 | .
2863 |  | JE24029373 | 191 MILL ROAD PAEROA PAEROA | Eastern | RAILWAY ST | 2024-09-04 | 9:09 | 2024-09-04 | 15:45 | 0.02281 | 5.7938e-05 | 21 | 8267 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RE-CONDUCTOR 11KV O/H LINES BETWEEN POLES N1266 & 858341 | .
2864 |  | JE24029395 | 22 NEAL STREET PUTARURU PUTARURU | Eastern | KENNEDY DRIVE | 2024-09-04 | 23:31 | 2024-09-05 | 1:43 | 0.041632 | 0.00031452 | 114 | 15090 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance 9442-1/2/3 | .
2865 |  | JE24029482 | 470 NGARUA ROAD WAITOA WAITOA | Eastern | TOWNSHIP & LS | 2024-09-04 | 9:16 | 2024-09-04 | 15:09 | 0.034122 | 9.6564e-05 | 35 | 12368 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE 11KV XARMS AND HARDWARE ON VARIOUS POLES. POLES C1632, C14430, C1633 AND C1644 | .
2866 |  | JE24029488 | 790 TAUMATA ROAD OMANAWA TAURANGA | Eastern | PYES PA | 2024-09-04 | 10:05 | 2024-09-04 | 12:55 | 0.0023362 | 1.3795e-05 | 5 | 847 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace low voltage conductors with PVC Ferret conductor between poles 392374 & 384144 | .
2867 |  | JE24032317 | CLOTON RD INDUSTRIAL | Western | CLOTON RD INDUSTRIAL | 2024-09-04 | 9:25 | 2024-09-04 | 11:10 | 0.00029001 | 2.759e-06 | 1 | 105 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: Tfr 4391T CAUSE: Lightning Temp generation (stage details when used): n PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: Weather (wind/rain): Lightning Follow up required (select advisory)? Additional fault restoration comments: Customer left on part power for the night, Tfr 4391T will need to be replaced in morning. 04/09/02024 Fuses for Transformer opened 09:25 Transformer replaced Livened 11:10 | .
2868 |  | JE24032339 | BUFFALO BEACH | Eastern | BUFFALO BEACH | 2024-09-04 | 4:31 | 2024-09-04 | 6:52 | 0.001946 | 1.3795e-05 | 5 | 705 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: dtx TC2929 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 06:52 Cause: Deterioration Barrel Failed Weather (wind/rain): Wind Rain Follow up required (select advisory)? | .
2869 |  | JE24032344 | CLOTON RD INDUSTRIAL | Western | CLOTON RD INDUSTRIAL | 2024-09-04 | 6:58 | 2024-09-04 | 9:34 | 0.00042885 | 2.759e-06 | 1 | 155 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: 4995 No. Fuses: 2 Fuse Amp Size:3 TIME CLOSED: 09:33 Cause: LIne Clash Weather (wind/rain): wind Follow up required (select advisory)?n | .
2870 |  | JE24032372 | OPOUTERE | Eastern | OPOUTERE | 2024-09-04 | 9:31 | 2024-09-11 | 11:00 | 0.095748 | 0.0018568 | 353 | 34704 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV WGM CB3 Protection flags (nil where none): Unknown CAUSE: Cable fault Location: Between Transformer TC2194 towards Transformer TC5177 Temp generation (state details when used): Yes, Generator connected to Transformer TC5177 PERFORMANCE DETAIL DNO (number or state No): 240 9008 Circuit patrolled and type: Yes Weather (wind/rain): Calm LFI (Y/N + Comments): Yes, at Sw/Gear 9637 Follow up Required (select advisory)? Yes Additional fault restoration comments: HV Cable fault identified between TX TC2194 & TX TC5177 Generator connected to TX TC5177 DNO 240 9008 created by NOC (Finn Parker's request) | .
2871 |  | JE24032378 | KOHETE RD | Western | KOHETE RD | 2024-09-04 | 9:55 | 2024-09-04 | 12:25 | 0.00041385 | 2.759e-06 | 1 | 150 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 3593T No. Fuses: 3 Fuse Amp Size: 2 TIME CLOSED: 12:25 Cause: Lightning Weather (wind/rain):Lightning Follow up required (select advisory)?n Smart Meter is damaged but . There is Full Power to the smart meter. No issue on powerco side . Customer advised to contact retailer by FM | .
2872 |  | JE24032382 | WAITARA RD | Western | WAITARA RD | 2024-09-04 | 10:07 | 2024-09-04 | 10:13 | 0.005654 | 0.0010539 | 382 | 2049 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Recloser 12237/2 Protection flags (nil where none): A, C Ph Fault CAUSE: Livening of Regulator 12728/2 Location: Waitara Rd Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Fault with New Regulator 12728/2 refer NAPA 111765 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2873 |  | JE24032463 | TIROHIA-KARANGAHAKE | Eastern | TIROHIA-KARANGAHAKE | 2024-09-04 | 18:11 | 2024-09-04 | 21:06 | 0.0033884 | 1.9313e-05 | 7 | 1228 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: TC501 Fuses CAUSE: Lightning strike Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): N/A Circuit patrolled & type: No Weather (wind/rain): recent lightning storm Follow up required (select advisory)? No Additional fault restoration comments: 1 x 30kVA 3 Ø 11kV - 400V transformer replaced | .
2874 |  | JE24032493 | SPRINGDALE | Eastern | SPRINGDALE | 2024-09-04 | 23:13 | 2024-09-05 | 1:16 | 0.00067552 | 5.5179e-06 | 2 | 245 | Unplanned | WILDLIFE - BIRD | Fuses Location: FC4233 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 01:15 Cause: Bird strike Weather (wind/rain): Calm Follow up required (select advisory)? No | .
2875 |  | JE24027882 | 330 MAUNGARANGI ROAD PAENGAROA TE PUKE | Eastern | MAUNGARANGI RD | 2024-09-03 | 8:49 | 2024-09-03 | 13:45 | 0.089085 | 0.00030073 | 109 | 32289 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV Poles 221847, 221849 & 221850. Remove redundant overhead conductors between 11kV Poles 221847 & 221849. Commission 3c 185mm 11kV cable between 11kV Poles 221847 & 221849. Remove redundant 11kV Pole 221848. Transpower 110kV Owhata-Te Matai-Tarukenga circuit outage under NAPA 112747. | .
2876 |  | JE24027913 | 50 MATAVAI STREET MOUNT MAUNGANUI TAURANGA | Eastern | MOUNT | 2024-09-03 | 10:30 | 2024-09-03 | 16:00 | 0.029992 | 9.1046e-05 | 33 | 10871 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Access and disconnect all cables at switch 9768. Test cable between SD5 221 & 9768/1 and SC5 022 & 9768/3. Remove 9768 & install new CFCC 14935 . Terminate existing cable from SD5 221 at 14935/1 & from SC5 022 at 14935/3. Terminate new 3c185mm cable from 14930/1 at 14935/4 . Remove old 3c 25mm cable at TD5 094 and abandon cable. Terminate new 3c 35mm cable at 14935/2 & connect TD5-094 Pre-commission cables and liven Check phasing at 14935/1 | .
2877 |  | JE24028581 | 107 LONDONS FORD ROAD KIMBOLTON FEILDING | Western | APITI | 2024-09-03 | 10:00 | 2024-09-03 | 11:28 | 0.00483 | 5.5179e-05 | 20 | 1751 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace HV crossarms on poles P06098 and P06101. Replace TX T4/290 | .
2878 |  | JE24028663 | 26 HART ROAD TAHUNA MORRINSVILLE | Eastern | PATETONGA | 2024-09-03 | 9:15 | 2024-09-03 | 13:20 | 0.004051 | 1.6554e-05 | 6 | 1468 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Poles 878011 and K1267 | .
2879 |  | JE24028769 | 350 PLYMOUTH ROAD KORU NEW PLYMOUTH | Western | PIONEER RD | 2024-09-03 | 9:00 | 2024-09-03 | 15:00 | 0.049983 | 0.00014347 | 52 | 18117 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 755187,755188,755193,755192, replace LV conductor from 755193 to 755188. | .
2880 |  | JE24028854 | SLOSS ROAD/CROAD PLACE, TOKOROA, TOKOROA | Eastern | CAMPBELL ST | 2024-09-03 | 23:30 | 2024-09-04 | 3:43 | 0.045377 | 0.00017933 | 65 | 16447 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9084/1/2/3/4 & 9086/1/2/3 | .
2881 |  | JE24028871 | 715 KAKARIKI ROAD EKETAHUNA EKETAHUNA | Western | HUKANUI | 2024-09-03 | 9:31 | 2024-09-03 | 13:37 | 0.028519 | 0.00011588 | 42 | 10337 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Change 11kv poles & arms P10592,P11401,P11414,P31310 Trim trees between s14 & P10680 | .
2882 |  | JE24028932 | 144 FOREST ROAD PAREWANUI BULLS | Western | PAREWANUI | 2024-09-03 | 9:16 | 2024-09-03 | 13:49 | 0.0045288 | 1.6554e-05 | 6 | 1642 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles and crossarms, poles working on 809614, 809615, 809616, 809617, 809618, 809619, 809620, 809623, 809624 | .
2883 |  | JE24028973 | 51 GRAYS ROAD WAREA NEW PLYMOUTH | Western | WAREA | 2024-09-03 | 10:25 | 2024-09-05 | 14:31 | 0.012002 | 0.0001545 | 28 | 4350 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To Replace poles and lines in between poles 383357 - pole 704419 | .
2884 |  | JE24031791 | OTAKEHO | Western | OTAKEHO | 2024-09-03 | 10:40 | 2024-09-06 | 17:38 | 0.026145 | 5.5179e-06 | 2 | 9476 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Blown Transformer - Needs to be replaced. 02/09/24 - FM advised 1R - not required as investigation for blown transformer M2050 actioned under CAE24039926 yesterday 01/09/2024. 2R CAE24040161 - will be used to replace the transformer today. 06/09/24 - Found out Calls have been automatically merging into this job - lots of calls advising problems with new Transformer - Rung SMC to get them to attend under the 2R HV fuse for Transformer M2050 found blown Replaced 1 x 3 Amp fuse Power restored 17: 38 Cause: Unknown | .
2885 |  | JE24032148 | KATERE 5 | Western | KATERE 5 | 2024-09-03 | 3:27 | 2024-09-03 | 7:05 | 0.0023991 | 1.1036e-05 | 4 | 870 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 8193 No. Fuses: 2 Fuse Amp Size: 2Amp TIME CLOSED: 07:04 Cause: Unk Weather (wind/rain): Calm / Light Rain Follow up required (select advisory)? | .
2886 |  | JE24032149 | HUNTERVILLE 22KV | Western | HUNTERVILLE 22KV | 2024-09-03 | 9:02 | 2024-09-03 | 12:46 | 0.0024685 | 1.1036e-05 | 4 | 895 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: Z105 CAUSE: Lightning Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: Cursory Weather (wind/rain): Heavy Rain/Lightning Follow up required (select advisory)? No Additional fault restoration comments: Replaced 15/22/3ph | .
2887 |  | JE24032164 | PIONEER RD | Western | PIONEER RD | 2024-09-03 | 9:24 | 2024-09-03 | 17:00 | 0.0025162 | 5.5179e-06 | 2 | 912 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Is actually Transformer 833. A pole mounted TX fitted into custom built concrete enclose. Looks to be a 50kVA and it is blown, but can not replace because of enclosure. Customers have own generators on keeping things going at the moment. To be managed by a Planned NAPA refer NAPA 115308 - Replace Transformer 833 with Pole mounted transfomer Fuses 8404 isolated 0924 - Generator connected at customers switchboard at 1700 | .
2888 |  | JE24032174 | MANGATOKI | Western | MANGATOKI | 2024-09-03 | 11:16 | 2024-09-03 | 15:13 | 0.0019558 | 8.2769e-06 | 3 | 709 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Location: 733392 & 733396 Cause: Adverse Weather Wind / Aged What was replaced? 733392 Replace Crossarm & 733396 Replace 3x HV fuse holders Weather: Windy / Heavy Rain Additional Info: Isolated at Fuses 5859 to allow repairs | .
2889 |  | JE24032175 | STRATHMORE | Western | STRATHMORE | 2024-09-03 | 8:31 | 2024-09-03 | 11:15 | 0.00045249 | 2.759e-06 | 1 | 164 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 2497T No. Fuses: 2 Fuse Amp Size:2 TIME CLOSED: 11:15 Cause: lightning Weather (wind/rain):N Follow up required (select advisory)?N Barrels Replaced | .
2890 |  | JE24032185 | NGARIKI RD | Western | NGARIKI RD | 2024-09-03 | 10:56 | 2024-09-03 | 13:14 | 0.0049126 | 6.8974e-05 | 25 | 1781 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: Corossion Isolation: NG404 What was replaced? HV Jumper Where was it replaced (pole/TX/pillar box)? N1205 Is 2R required? Y Additional Info: Replaced corroded HV jumper at N1205 | .
2891 |  | JE24032207 | MAURICEVILLE | Western | MAURICEVILLE | 2024-09-03 | 9:51 | 2024-09-03 | 10:48 | 0.0075088 | 0.00013243 | 48 | 2722 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Found Floating Insulator at Pole P12922 Isolated at Fuses U24 Replaced with 3 X Clamp Top Insulators | .
2892 |  | JE24032229 | COASTAL NO 2 33KV | Western | COASTAL NO 2 33KV | 2024-09-03 | 10:54 | 2024-09-05 | 12:00 | 0.68738 | 0.0034487 | 906 | 249143 | Unplanned | DEFECTIVE EQUIPMENT - ZONE SUBSTATION | REGULATORY INFORMATION Voltage & Device ID: 33kV OPK CB 3242 Protection flags (nil where none): A,B,C O/C CAUSE: 11kV CB switchboard failure Location: PUN Sub Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): 2409004 Circuit patrolled and type: Cursory Weather (wind/rain): Fine LFI (Y/N + Comments): Nil Follow up Required (select advisory)? Yes Additional fault restoration comments: 04/09/2024 33kV lines to PUN Sub Patrolled & Safe to Liven SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Pungerehu Sub Circuit that tripped: OPK CB 3242 / NGA CB 3242 DTF (KM): Hazard at 138 Wataroa Rd that rolled into this feeder Fault dispatched separately under JE24032329 Completed under DNO 2409004 | .
2893 |  | JE24032231 | HUIROA | Western | HUIROA | 2024-09-03 | 11:00 | 2024-09-03 | 18:06 | 0.0035243 | 8.2769e-06 | 3 | 1277 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Transformer 3256T No. Fuses: 3 Fuse Amp Size: 3A TIME CLOSED: 18:05 Cause: Lightning Weather (wind/rain): Stormy Follow up required (select advisory)? 2R to replace 2x DDO Barrels | .
2894 |  | JE24032234 | LAKE ALICE | Western | LAKE ALICE | 2024-09-03 | 11:04 | 2024-09-03 | 13:10 | 0.00034703 | 2.759e-06 | 1 | 126 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 2500W No. Fuses: 2 Fuse Amp Size: 2 TIME CLOSED: 13:10 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?N Logged to wrong TX | .
2895 |  | JE24032243 | CHESTER RD | Western | CHESTER RD | 2024-09-03 | 12:10 | 2024-09-03 | 12:35 | 0.00034418 | 1.3795e-05 | 5 | 125 | Unplanned | THIRD PARTY INTERFERENCE - OVERHEAD CONTACT | LV lines down Suspect a digger or high load has bought the lines down. Isoalte at Tfr T2057 11kV Fuses due to no LV fusing to complete repairs | .
2896 |  | JE24032244 | INLAND COAST | Western | INLAND COAST | 2024-09-03 | 11:40 | 2024-09-03 | 17:08 | 0.0054363 | 1.6554e-05 | 6 | 1970 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Transformer 469 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 17:08 Cause: Lightning Weather (wind/rain): Stormy Follow up required (select advisory)? | .
2897 |  | JE24032252 | RAHOTU | Western | RAHOTU | 2024-09-03 | 16:03 | 2024-09-03 | 19:55 | 0.00063967 | 2.759e-06 | 1 | 232 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: Tfr 5469E Fuses CAUSE: Lightning Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: Yes / Cursory Weather (wind/rain): Lightning Follow up required (select advisory)? Additional fault restoration comments: Replaced Tfr 5469E | .
2898 |  | JE24032262 | KATERE 5 | Western | KATERE 5 | 2024-09-03 | 8:40 | 2024-09-03 | 11:41 | 0.00099623 | 5.5179e-06 | 2 | 361 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 635 No. Fuses: 2 Fuse Amp Size:3 TIME CLOSED: 11:40 Cause: LIghtning Weather (wind/rain):lightning Follow up required (select advisory)? FM checked this TX on the 1/9/24 but Fuses have dropped out since . Bartech/Rimu electrical have been there and replaced a 3Ph Cable but no COC has been left so FM has not Reconnected. | .
2899 |  | JE24032276 | BROOKLANDS 7 | Western | BROOKLANDS 7 | 2024-09-03 | 13:35 | 2024-09-03 | 16:48 | 0.1831 | 0.0024417 | 885 | 66367 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV, CB 7 Protection flags (nil where none): E/F A Phase CAUSE: Broken HV Insulator Location: 701372 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Yes / Cursory Weather (wind/rain): Windy / Heavy Rain LFI (Y/N + Comments): Yes Follow up Required (select advisory)? Pole 701371 activated correctly Additional fault restoration comments: Replaced HV crossarm & all hardware. Repaired damaged line SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2900 |  | JE24032280 | TE KIRI | Western | TE KIRI | 2024-09-03 | 11:23 | 2024-09-03 | 13:43 | 0.0011531 | 8.2769e-06 | 3 | 418 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T7205 No. Fuses: 2 Fuse Amp Size2: TIME CLOSED: 13:42 Cause: lightning Today Weather (wind/rain): Today lighting Follow up required (select advisory)?n | .
2901 |  | JE24032281 | RANGIKURA | Western | RANGIKURA | 2024-09-03 | 13:52 | 2024-09-03 | 16:37 | 0.01002 | 6.0697e-05 | 22 | 3632 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Fuses 806 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 16:36 Cause: Lightning Weather (wind/rain): Stormy Follow up required (select advisory)? Note: Re-loaded 1x Fuse at Fuses 806 at 15:48, then found bad voltages at nearby Transformer, then found a second Fuse blown at same Fuses and Replaced at 16:36. James also confirmed JE24032284 has full power at completion | .
2902 |  | JE24032285 | TE KIRI | Western | TE KIRI | 2024-09-03 | 14:16 | 2024-09-03 | 14:56 | 0.00033023 | 8.2769e-06 | 3 | 120 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T7225 No. Fuses: 2 Fuse Amp Size:6 TIME CLOSED: 14:55 Cause: lightening Weather (wind/rain):Lightening Follow up required (select advisory)?N 2 X barrels replaced | .
2903 |  | JE24032291 | AUROA | Western | AUROA | 2024-09-03 | 14:44 | 2024-09-03 | 15:50 | 0.00018156 | 2.759e-06 | 1 | 66 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 5497E No. Fuses: 2 Fuse Amp Size2: TIME CLOSED: 15:50 Cause: Lighteing Weather (wind/rain):lightning Follow up required (select advisory)?N | .
2904 |  | JE24032296 | TE KIRI | Western | TE KIRI | 2024-09-03 | 11:58 | 2024-09-03 | 15:08 | 0.0026203 | 1.3795e-05 | 5 | 950 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T7325 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 15:07 Cause: lighting Weather (wind/rain):lightning Follow up required (select advisory)?n | .
2905 |  | JE24032298 | RAHOTU | Western | RAHOTU | 2024-09-03 | 15:35 | 2024-09-03 | 17:49 | 0.0014757 | 1.1036e-05 | 4 | 535 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Transformer P2370 No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 17:49 Cause: Lightning Weather (wind/rain): Stormy Follow up required (select advisory)? | .
2906 |  | JE24032310 | WESTMERE PEAT ST | Western | WESTMERE PEAT ST | 2024-09-03 | 16:39 | 2024-09-03 | 17:54 | 0.00082466 | 1.1036e-05 | 4 | 299 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: Fuses 2606 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 17:53 Cause: Suspect Lightning Damage from Saturday Weather (wind/rain): Stormy Follow up required (select advisory)? | .
2907 |  | JE24032313 | RAHOTU | Western | RAHOTU | 2024-09-03 | 17:08 | 2024-09-03 | 20:57 | 0.0037997 | 1.6554e-05 | 6 | 1377 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: P1050 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 20:57 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? P1050 & P1060 same customer job was at P1050 for water shed. | .
2908 |  | JE24028252 | 16 SUSSEX STREET MASTERTON MASTERTON | Western | WORKSOP RD | 2024-09-02 | 9:30 | 2024-09-02 | 10:08 | 0.0056241 | 0.00014898 | 54 | 2039 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Carry out Tap Change at T1408 to lower voltage output | .
2909 |  | JE24028308 | 5 GLENPARK AVENUE WESTOWN NEW PLYMOUTH | Western | BROOKLANDS 14 | 2024-09-02 | 8:45 | 2024-09-02 | 13:16 | 0.11049 | 0.00040833 | 148 | 40049 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 753461 with new B11 and Remove ABS 318 | .
2910 |  | JE24028378 | 219 TE WHITI ROAD HOMEBUSH MASTERTON | Western | CHURCH ST | 2024-09-02 | 8:47 | 2024-09-02 | 11:40 | 0.00095754 | 5.5179e-06 | 2 | 347 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Create line break live line then replace pole 829590, re instate line break | .
2911 |  | JE24028563 | 13 CAMBRIDGE STREET PUTARURU PUTARURU | Eastern | BENT ST | 2024-09-02 | 9:47 | 2024-09-02 | 10:36 | 0.0028042 | 5.7938e-05 | 21 | 1016 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Purpose of switching is to change the tap selector switch position and confirm voltage correct at site. | .
2912 |  | JE24028601 | 404 WAIHEKAU ROAD TE AROHA WEST TE AROHA | Eastern | NGARUA | 2024-09-02 | 8:58 | 2024-09-02 | 15:04 | 0.01213 | 3.3108e-05 | 12 | 4396 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replacing Xarms and uypgrading TX structures. Worksite Poles C13028, C070, C074, C13026 | .
2913 |  | JE24028657 | 2454 STATE HIGHWAY 4 WAIMARINO WANGANUI | Western | MAKIRIKIRI | 2024-09-02 | 9:00 | 2024-09-02 | 15:07 | 0.02762 | 0.00015174 | 55 | 10011 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Vegetation - Asplundh contractor to clear vegetation between pole 783782 and 783786 | .
2914 |  | JE24028730 | 56 RACECOURSE ROAD WHITIANGA WHITIANGA | Eastern | KUAOTUNU | 2024-09-02 | 9:33 | 2024-09-02 | 13:01 | 0.0028691 | 1.3795e-05 | 5 | 1040 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace lv fusing and leads at transformer TP2857 | .
2915 |  | JE24028751 | 4 RANGATAUA STREET WELCOME BAY TAURANGA | Eastern | WELCOME BAY | 2024-09-02 | 9:46 | 2024-09-02 | 17:56 | 0.15452 | 0.00031728 | 115 | 56006 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Resolve problems installed automation retrofit kit on ABB Safelink 13037. Sw/Gear 13037 had to be swapped out due to mechanical issues. | .
2916 |  | JE24030521 | 111 RANGIHAU ROAD COROGLEN WHITIANGA | Eastern | TAIRUA NORTH | 2024-09-02 | 9:00 | 2024-09-02 | 15:51 | 0.053551 | 0.00013243 | 48 | 19410 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV Poles Rangihau Rd Coroglen | .
2917 |  | JE24030847 | 176 COUPER ROAD GLEN OROUA PALMERSTON NORTH | Western | RONGOTEA | 2024-09-02 | 10:05 | 2024-09-02 | 12:20 | 0.0081941 | 6.0697e-05 | 22 | 2970 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Straighten 11KV poles 477912 & 477991 | .
2918 |  | JE24031935 | RANGIKURA | Western | RANGIKURA | 2024-09-02 | 10:15 | 2024-09-02 | 13:08 | 0.0014349 | 8.2769e-06 | 3 | 520 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Not a fuse reload - check for SIS Incorrect Job Location Fuses Location: X558 No. Fuses: 1 Fuse Amp Size: 2 TIME CLOSED: 18:25 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n Leave 2R Open, DDO's need to be replaced to TFR X558, will be done on the 02/09/24 Replaced 3 x DDOs and 1 x 15kva 3 Phase transformer Isolated at Fuses 4117 | .
2919 |  | JE24031966 | WAINGAWA RD | Western | WAINGAWA RD | 2024-09-02 | 8:51 | 2024-09-02 | 20:44 | 0.0039729 | 2.2072e-05 | 5 | 1440 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Fuse switch 11396-2 Blown Fuse Replaced 1 X 6.3 amp Fuse closed Fuse switch Blow again Tested Cable and Transformer Found Fault on Cable Replaced Cable Replaced faulty section of HV Cable between Fuse/Sw 11396/2 towards Transformer T3894 Full Power restored at 20:44 | .
2920 |  | JE24031969 | TE ROTI | Western | TE ROTI | 2024-09-02 | 14:31 | 2024-09-02 | 16:55 | 0.00039798 | 2.759e-06 | 1 | 144 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Voltage & Device ID: 11kV Fuses 5162 Protection flags (nil where none): CAUSE: Floating conductor at pole 733407, Replaced 3 binders & 1 insulator Cause Deterioration Location: Pole 733407 Power Restored 16:54 | .
2921 |  | JE24031972 | RANGIKURA | Western | RANGIKURA | 2024-09-02 | 8:13 | 2024-09-02 | 15:59 | 0.0012837 | 2.759e-06 | 1 | 465 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 356W No. Fuses: 3 Fuse Amp Size: 2 TIME CLOSED: 15:58 Cause: Lightning Weather (wind/rain): Follow up required (select advisory)?n | .
2922 |  | JE24031989 | NO 3 LINE | Western | NO 3 LINE | 2024-09-02 | 9:03 | 2024-09-02 | 11:01 | 0.00032442 | 2.759e-06 | 1 | 118 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: X4191 No. Fuses: 2 Fuse Amp Size:2 TIME CLOSED: 11:00 Cause: Lightning Weather (wind/rain):lightning Follow up required (select advisory)?n | .
2923 |  | JE24032022 | MOUNT BRUCE | Western | MOUNT BRUCE | 2024-09-02 | 10:27 | 2024-09-02 | 12:28 | 0.00033508 | 2.759e-06 | 1 | 121 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T665 No. Fuses: 2 Fuse Amp Size:3A TIME CLOSED: 12:28 Cause: Lightning Weather (wind/rain):lightning Follow up required (select advisory)?n | .
2924 |  | JE24032026 | STRATHMORE | Western | STRATHMORE | 2024-09-02 | 10:42 | 2024-09-02 | 16:45 | 0.0010016 | 2.759e-06 | 1 | 363 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 3253T No. Fuses: 3 Fuse Amp Size:2 TIME CLOSED: 16:45 Cause: lightning Weather (wind/rain): lightning Follow up required (select advisory)?n on barrel replaced 2 R | .
2925 |  | JE24032057 | MAKIRIKIRI | Western | MAKIRIKIRI | 2024-09-02 | 12:38 | 2024-09-03 | 13:39 | 0.074473 | 0.0001076 | 39 | 26993 | Unplanned | HUMAN ERROR - POTENTIAL WORKMANSHIP | REGULATORY INFORMATION Voltage & Device ID: Rec 2995 Protection flags (nil where none):B & C Phase E/F CAUSE: Tree in Lines Location: 790082 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Loggers cutting Trees and it fall wrong Way CAC84599 Opened Dave Hickford 027 644 5534 Cashmore Contracting Replaced Pole with Digger and Repaired 3 Span Of Conductor SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2926 |  | JE24032066 | KATERE 9 | Western | KATERE 9 | 2024-09-02 | 15:37 | 2024-09-02 | 22:15 | 0.0021946 | 5.5179e-06 | 2 | 795 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: Fuses 6707 CAUSE: Defective Tfr 457 Temp generation (stage details when used): n PERFORMANCE DETAIL DNO (number or state no): n Circuit patrolled & type: cursory Weather (wind/rain): Lightning Follow up required (select advisory)? Additional fault restoration comments: Also replaced 2 x termination cross arms and replaced Tfr 457 | .
2927 |  | JE24032075 | RANGIKURA | Western | RANGIKURA | 2024-09-02 | 8:46 | 2024-09-02 | 13:58 | 0.0017174 | 5.5179e-06 | 2 | 622 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: X2806 No. Fuses: 2 Fuse Amp Size: 2 TIME CLOSED: 13:57 Cause: lightning Weather (wind/rain): lightning Follow up required (select advisory)?n | .
2928 |  | JE24032103 | HAURAKI RD | Eastern | HAURAKI RD | 2024-09-02 | 15:45 | 2024-09-02 | 16:46 | 0.0011685 | 1.9313e-05 | 7 | 424 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Fuses Location: Transformer TC2862 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 16:45 Cause: Tractor Hit Pole Weather (wind/rain): Calm Follow up required (select advisory)? Customer Disconnected - Tag A41557 Downer will repair under SRC Tomorrow | .
2929 |  | JE24032105 | TE KIRI | Western | TE KIRI | 2024-09-02 | 17:29 | 2024-09-03 | 15:00 | 0.0071267 | 5.5179e-06 | 2 | 2583 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: T7450 Fuses CAUSE: Lightning Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: Yes / Cursory Weather (wind/rain): Lightning Follow up required (select advisory)? Additional fault restoration comments: Replaced 30/11/3ph Transformer | .
2930 |  | JE24032115 | INLAND COAST | Western | INLAND COAST | 2024-09-02 | 19:15 | 2024-09-03 | 12:41 | 0.0028854 | 2.759e-06 | 1 | 1046 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: Fuses 8187 CAUSE: Lightning Temp generation (stage details when used): n PERFORMANCE DETAIL DNO (number or state no): n Circuit patrolled & type: cursory Weather (wind/rain): lightning Follow up required (select advisory)? Additional fault restoration comments: Replace Tfr 1535 in morning. Replaced 15/11/1ph | .
2931 |  | JE24032126 | 540 HORRELL ROAD, MORRINSVILLE, 3374 | Eastern | HORRELLS RD | 2024-09-02 | 21:25 | 2024-09-02 | 22:23 | 0.00047827 | 8.2769e-06 | 3 | 173 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: TX TC4722 Fuses CAUSE: Tank ruptured (Leaking oil) Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Calm Follow up required (select advisory)? Yes Additional fault restoration comments: Transformer TC4722 is leaking oil and has to be changed immediately. Les is arranging traffic management. Work being carried out under AP 2126-01 Transformer replaced and Full Power restored at 22:22 SAFETY MANAGER for oil leaking/spill. Field Switcher estimates a few liter's of oil leaked out the Transformer. | .
2932 |  | JE24032140 | MARTINBOUROUGH SUB - CB C894 - Recloser C625 | Western | DYERVILLE | 2024-09-02 | 19:41 | 2024-09-02 | 23:15 | 0.028381 | 0.00013243 | 48 | 10287 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC C625/2 Protection flags (nil where none): B & C Ø Trip Flag CAUSE: Tree fell over (Inside Zone) Location: Pole 816 101 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Tree Branch came down across HV Lines at Pole 816 101 Field Switcher organized tree trimmers to come to site. Repairs being carried out under AP 2140-01 All repairs carried out and Full Power restored at 23:15 | .
2933 |  | JE24028006 | 10 WILSON ROAD SOUTH PAENGAROA TE PUKE | Eastern | MAKETU | 2024-09-01 | 23:30 | 2024-09-02 | 3:02 | 0.034644 | 0.00052144 | 189 | 12557 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Isolate both CB 3 and CB 5 and install Line breaks. Work is part of enabling works for upcoming 11kV switchboard replacement at Paeangaroa Substation which will require the 11kV bus and all incoming cables to be isolated. | .
2934 |  | JE24031531 | 109 KURIPUNI STREET, KURIPUNI, MASTERTON, 5810 | Western | COLOMBO RD | 2024-09-01 | 10:01 | 2024-09-01 | 11:36 | 0.03389 | 0.00035315 | 128 | 12284 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB C823, ABS S81 Protection flags (nil where none): Nil CAUSE: Car V Pole Location: Pole 833183 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): Rain LFI (Y/N + Comments): Nil Follow up Required (select advisory)? No Additional fault restoration comments: Faultman assessed the pole and confirmed pole has cracks but can wait until tomorrow. There is no electrical services on the pole besides telecom. Job will be done during daytime. NDR to follow 1 x 11m pole 1 x HV pin cross arm complete assembly 1 x LV pin cross arm complete assembly | .
2935 |  | JE24031603 | MANGATEPARU | Eastern | MANGATEPARU | 2024-09-01 | 3:04 | 2024-09-01 | 8:06 | 0.10139 | 0.00033659 | 122 | 36750 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV TAH CB 2 Protection flags (nil where none): Nil CAUSE: Car vs Pole Location: Pole K0793 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Rain/wind/lightning. LFI (Y/N + Comments): No Follow up Required (select advisory)? Yes, NDR to follow Additional fault restoration comments: ETA 30min, Fire Coms informed. No Feeder fault - Car drove into the Pole. New Pole is being installed under an AP 1 x 11m pole 1 x double HV pin cross arm complete assembly 1 x double LV pin cross arm complete assembly SAFETY MANAGER | .
2936 |  | JE24031618 | PARAPARA | Western | PARAPARA | 2024-09-01 | 0:08 | 2024-09-04 | 14:32 | 0.14818 | 0.00044419 | 147 | 53707 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Lots of Lightning around, faultman told to hold off patrol until lightning has stopped by Control REGULATORY INFORMATION Voltage & Device ID: 11KV REC 284 Protection flags (nil where none): E/F CAUSE: Lines down in Gorge Location: 785219 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: Operational patrol Weather (wind/rain): lightning & rain, wind LFI (Y/N + Comments): n Follow up Required (select advisory)? Additional fault restoration comments: Line was isolated at ABS 768 & ABS 4621/1 & Links 4621/4 to cut a Temp Line Break at pole 785191. 04/09/2024 Line Repairs completed Line was isolated at ABS 768 & ABS 4621/1 & Links 4621/4 to close Temp Line Break at pole 785191. | .
2937 |  | JE24031620 | JUNCTION RD | Western | JUNCTION RD | 2024-09-01 | 0:07 | 2024-09-01 | 14:57 | 0.0098246 | 1.1036e-05 | 4 | 3561 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Transformer 793 No. Fuses: 3 Fuse Amp Size: 2A TIME CLOSED: 14:57 Cause: Lightning Weather (wind/rain): Stormy Follow up required (select advisory)? | .
2938 |  | JE24031622 | HUIROA | Western | HUIROA | 2024-09-01 | 0:10 | 2024-09-02 | 16:55 | 0.17315 | 0.00021796 | 77 | 62761 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: Tfr 2487T Fuses & Fuses 6245 to Tfr 3348T CAUSE: Lightning Temp generation (stage details when used): n PERFORMANCE DETAILn DNO (number or state no): N Circuit patrolled & type: cursory Weather (wind/rain): Lightning Follow up required (select advisory)? Additional fault restoration comments: REC 12328/2 tripped on C ph O/C & E/F, line was patrolled and 2 blown Tfr's 2487T & 3348T were found have been isolated.Replaced 3348T2/09/24 @ 16:55 Replaced TX 2487T Repaced TX 3348T | .
2939 |  | JE24031624 | RANGIKURA | Western | RANGIKURA | 2024-09-01 | 0:12 | 2024-09-01 | 14:21 | 0.12936 | 0.00027866 | 82 | 46887 | Unplanned | LIGHTNING - LIGHTNING STRIKE | REGULATORY INFORMATION Voltage & Device ID: REC 4867/2 Protection flags (nil where none): EF, OC B CAUSE: Faulty Transformer 4845w Location: Transformer 4845w Temp generation (state details when used): NIL PERFORMANCE DETAIL DNO (number or state No): NIL Circuit patrolled and type: Cursory Weather (wind/rain): Lightning LFI (Y/N + Comments): NIL Follow up Required (select advisory)? NIL Additional fault restoration comments: Fault On Transformer 4845w - Replaced and power Restored | .
2940 |  | JE24031627 | BROOKLANDS 12 | Western | BROOKLANDS 12 | 2024-09-01 | 0:19 | 2024-09-01 | 13:10 | 0.040418 | 5.242e-05 | 19 | 14650 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Transformer 734 No. Fuses: 3 & Holders Replaced Fuse Amp Size: 15A TIME CLOSED: 13:10 Cause: Lightning Weather (wind/rain): Stormy Follow up required (select advisory)? | .
2941 |  | JE24031631 | BRUNSWICK | Western | BRUNSWICK | 2024-09-01 | 0:48 | 2024-09-01 | 4:25 | 0.0017954 | 8.2769e-06 | 3 | 651 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: X1230 No. Fuses: 2 Fuse Amp Size: 2 TIME CLOSED: 04:25 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n | .
2942 |  | JE24031636 | WAITARA RD | Western | WAITARA RD | 2024-09-01 | 0:54 | 2024-09-01 | 17:36 | 0.0055266 | 5.5179e-06 | 2 | 2003 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 1598 No. Fuses: 3 Fuse Amp Size:3 TIME CLOSED: 17:35 Cause: lightning Weather (wind/rain): Follow up required (select advisory)?n | .
2943 |  | JE24031637 | STRATHMORE | Western | STRATHMORE | 2024-09-01 | 0:59 | 2024-09-02 | 14:08 | 0.24999 | 0.00021796 | 79 | 90612 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 7121 Protection flags (nil where none): E/F, O/C B CAUSE: Tree through lines Location: 739333 - Past Fuses 5453 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: cursory Weather (wind/rain): Lightning LFI (Y/N + Comments): n Follow up Required (select advisory)? Additional fault restoration comments: Line isolated at Fuses 5453 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): 01/09/23 - Advised Phil Webby Regarding the new call for lines down by Rd Marker #5 / 8km down Puniwhakau Rd Repaired tree through lines Pole 739333 | .
2944 |  | JE24031638 | MAIN ST 14 | Western | MAIN ST 14 | 2024-09-01 | 1:12 | 2024-09-01 | 2:00 | 0.008993 | 0.00018485 | 67 | 3260 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: CB 14 Protection flags (nil where none): E/F, O/C CAUSE: Cable fault Location: Between Sw/Gear G2/F & G41/B Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): 2409001 Circuit patrolled and type: op Weather (wind/rain): wind, rain LFI (Y/N + Comments): y Sw/Gear G2/F Follow up Required (select advisory)? Additional fault restoration comments: Cable fault, find and fix under DNO SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2945 |  | JE24031639 | MISSION RD | Western | MISSION RD | 2024-09-01 | 5:05 | 2024-09-01 | 11:40 | 0.0032698 | 8.2769e-06 | 3 | 1185 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Faulty TFR 4509W due to Lightning strike Isolated at Fuses 4207 - Tfr 4509W replaced. | .
2946 |  | JE24031640 | MAHOE | Western | MAHOE | 2024-09-01 | 1:19 | 2024-09-01 | 12:36 | 0.18681 | 0.00081114 | 294 | 67711 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB Q21 Protection flags (nil where none): O/C A, B & C CAUSE: Broken cross arm Location: 730629 Temp generation (state details when used): NIL PERFORMANCE DETAIL DNO (number or state No): NIL Circuit patrolled and type: 11kV CB Q21 Cursory Patrol Weather (wind/rain): Lightning LFI (Y/N + Comments): NIL Follow up Required (select advisory)? NIL Additional fault restoration comments: Fault Found at Pole 730629 | .
2947 |  | JE24031643 | MAKIRIKIRI | Western | MAKIRIKIRI | 2024-09-01 | 1:37 | 2024-09-01 | 15:33 | 0.057393 | 8.001e-05 | 25 | 20802 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 2713 Protection flags (nil where none): O/C A & C CAUSE: Line stuck on branch Location: 844123 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: cursory Weather (wind/rain): wind LFI (Y/N + Comments): n Follow up Required (select advisory)? Additional fault restoration comments: what line could be seen has been patrolled, left off, day time patrol needed, may require a helicopter patrol due to terrain Line was flown with a drone and a line was found stuck on at branch, line was removed, supply restored. NCTL NDR Required for trees, If line hooked on Branch trees must be in zone | .
2948 |  | JE24031644 | JUNCTION RD | Western | JUNCTION RD | 2024-09-01 | 1:48 | 2024-09-01 | 21:05 | 0.012769 | 1.1036e-05 | 4 | 4628 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Fuses at Pole 746675 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 21:00 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? Fuses Location: 917 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 21:04 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? | .
2949 |  | JE24031645 | TURAKINA | Western | TURAKINA | 2024-09-01 | 1:50 | 2024-09-01 | 18:34 | 0.009279 | 1.1036e-05 | 4 | 3363 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: X2697 No. Fuses: 3 Fuse Amp Size: 2 TIME CLOSED: 18:33 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n | .
2950 |  | JE24031647 | PUTORINO | Western | PUTORINO | 2024-09-01 | 2:10 | 2024-09-02 | 17:25 | 0.053001 | 0.0001683 | 52 | 19210 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11KV REC 4246/2 Protection flags (nil where none): A & C ph O/C & E/F CAUSE: Line down in Pine forest Location: 806906 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: cursory Weather (wind/rain): Rain & wind LFI (Y/N + Comments): n Follow up Required (select advisory)? Additional fault restoration comments: Line was isolated at Fuses 4078 to cut a Temp Line Break at pole 806983, will return Monday to move trees and repair lines. LInes Repaired and Temp line break removed off Pole 806983 Line Break was removed at and live at 17:24 2/9/24 | .
2951 |  | JE24031648 | HUIROA | Western | HUIROA | 2024-09-01 | 2:31 | 2024-09-01 | 16:46 | 0.016501 | 1.9313e-05 | 7 | 5981 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 5718 No. Fuses: 2 Fuse Amp Size: 8 TIME CLOSED: 16:45 Cause: lightning Weather (wind/rain): Follow up required (select advisory)?N | .
2952 |  | JE24031664 | BROOKLANDS 12 | Western | BROOKLANDS 12 | 2024-09-01 | 4:53 | 2024-09-01 | 15:56 | 0.014632 | 2.2072e-05 | 8 | 5303 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 1071 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 15:55 Cause: lightning Weather (wind/rain): Follow up required (select advisory)? | .
2953 |  | JE24031671 | TE ROTI | Western | TE ROTI | 2024-09-01 | 5:20 | 2024-09-01 | 18:03 | 0.0021054 | 2.759e-06 | 1 | 763 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 5162 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 18:03 Cause: lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n | .
2954 |  | JE24031673 | MANAWAPOU RD | Western | MANAWAPOU RD | 2024-09-01 | 10:13 | 2024-09-01 | 15:19 | 0.0067492 | 2.2072e-05 | 8 | 2446 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Part Power to Lines down, called the SMC to advise. Lines down and broken X-arms pole 728431 Advised Rhys Wineera of another lines down call - Confirmed that this is the same one he is already aware of. Faultman found lines down and broken cross arm at pole 728431, line was isolated at Fuses WH157 to repair lines down & replace cross arm. | .
2955 |  | JE24031675 | PAPANUI ST | Eastern | PAPANUI ST | 2024-09-01 | 15:31 | 2024-09-02 | 0:31 | 0.0059606 | 1.1036e-05 | 4 | 2160 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: Transformer TC1644 Fuses CAUSE: Lightning Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Cursory Weather (wind/rain): Lightning Follow up required (select advisory)? No Additional fault restoration comments: Job logged at TP1781 but was at TC1644 Transformer replaced, Power Restored 00:30Hrs | .
2956 |  | JE24031677 | OAONUI | Western | OAONUI | 2024-09-01 | 12:15 | 2024-09-01 | 16:39 | 0.0021822 | 8.2769e-06 | 3 | 791 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Broken cross arm at pole 372869 Fuses TA785 Isolated. Fault crew replace broken cross arm, supply restored. | .
2957 |  | JE24031679 | OTAUTU | Western | OTAUTU | 2024-09-01 | 16:06 | 2024-09-01 | 17:29 | 0.0043587 | 5.242e-05 | 19 | 1580 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faultman found lines down at pole 727035. Line was isolated at Fuses LI182 to repair the lines. | .
2958 |  | JE24031680 | BRISTOL RD | Western | BRISTOL RD | 2024-09-01 | 6:00 | 2024-09-01 | 6:01 | 0.00025551 | 0.00020968 | 76 | 93 | Unplanned | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | Voltage & Device ID: 11kV Rec 12556/2 Protection flags (nil where none): E/F, O/C B Weather (wind/rain): wind, rain Follow up required (select advisory): n LFI Activation: N | .
2959 |  | JE24031681 | MCKEE SOUTH 33KV | Western | MCKEE SOUTH 33KV | 2024-09-01 | 6:00 | 2024-09-01 | 6:04 | 0.0080477 | 0.0067401 | 2443 | 2917 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 33KV CB 191 Protection flags (nil where none): A & C ph O/C CAUSE: Suspect tripping caused by fault on ING CB I51 tripping Location: ? Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: cursory Weather (wind/rain): Rain LFI (Y/N + Comments): Y - Poles 760621 & 760328 Follow up Required (select advisory)? n Additional fault restoration comments: Line patrolled and sectionalized no fault was found. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Inglewood Circuit that tripped: CB 191 DTF (KM): Nil | .
2960 |  | JE24031683 | BRISTOL RD | Western | BRISTOL RD | 2024-09-01 | 6:01 | 2024-09-03 | 12:00 | 0.060498 | 0.0003697 | 78 | 21928 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11KV REC 12556/2 Protection flags (nil where none): B ph O/C & E/F CAUSE: Duck Strike Location: 759734 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: cursory Weather (wind/rain): caim LFI (Y/N + Comments): n Follow up Required (select advisory)? Additional fault restoration comments: Line was isolated at ABS 5394 to repair line down, 2 Blown Tfr's also found Tfr 2452T & 5051T Tfr 5051T has a new JE 24031921 to have it replaced. TX 5051t Replaced TX 2452t Replaced SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2961 |  | JE24031695 | LINDERMANN RD | Eastern | LINDERMANN RD | 2024-09-01 | 6:42 | 2024-09-01 | 11:06 | 0.011562 | 4.4143e-05 | 16 | 4191 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Fuses SB2-119 No. Fuses: 2 Fuse Amp Size: 15A TIME CLOSED: 11:05 Cause: Lightning Weather (wind/rain): Stormy Follow up required (select advisory)? Advised JE24031790, JE24031700 & JE24031716 are all checked to have been restored under this job | .
2962 |  | JE24031703 | PAREWANUI | Western | PAREWANUI | 2024-09-01 | 6:57 | 2024-09-01 | 11:04 | 0.13623 | 0.00055179 | 200 | 49378 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 4461/6 No. Fuses: 2 Fuse Amp Size: 50 TIME CLOSED: 11;03 Cause: lightning Weather (wind/rain): rain & lightning Follow up required (select advisory)? | .
2963 |  | JE24031710 | CLOTON RD SOUTH | Western | CLOTON RD SOUTH | 2024-09-01 | 18:40 | 2024-09-02 | 15:27 | 0.017196 | 1.3795e-05 | 5 | 6233 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Not a fuse reload - check for SIS Fuses Location: Transformer 2540T TIME CLOSED: 15:27 (off overnight) Cause: Lightning Weather (wind/rain): Stormy Follow up required (select advisory)? Replaced faulty TFR 2540T due to lightning strike | .
2964 |  | JE24031713 | HUNTERVILLE 22KV | Western | HUNTERVILLE 22KV | 2024-09-01 | 7:09 | 2024-09-01 | 15:55 | 0.0029034 | 5.5179e-06 | 2 | 1052 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 2706 No. Fuses: 2 Fuse Amp Size:6 TIME CLOSED:15:55 Cause: lightning Weather (wind/rain): Follow up required (select advisory)?n | .
2965 |  | JE24031729 | MOUNTAIN RD | Western | MOUNTAIN RD | 2024-09-01 | 19:14 | 2024-09-02 | 13:55 | 0.021653 | 1.9313e-05 | 7 | 7848 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: TX 3238T CAUSE: Lightning Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): n Circuit patrolled & type: cursory Weather (wind/rain): lightning Follow up required (select advisory)?N Additional fault restoration comments 3 PH 30 KVA Changed due to weather / Lightning Field switcher Seth hunuhunu | .
2966 |  | JE24031754 | MANAWAPOU RD | Western | MANAWAPOU RD | 2024-09-01 | 17:31 | 2024-09-02 | 11:21 | 0.0059034 | 5.5179e-06 | 2 | 2140 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: Tfr 5065W CAUSE: Lightning Temp generation (stage details when used): n PERFORMANCE DETAIL DNO (number or state no): n Circuit patrolled & type: cursory Weather (wind/rain): Rain & Lightning Follow up required (select advisory)?n Additional fault restoration comments: Replaced Transformer 3 PH 15KVA 5065W | .
2967 |  | JE24031755 | TARATA | Western | TARATA | 2024-09-01 | 11:30 | 2024-12-06 | 12:50 | 0.76668 | 3.3108e-05 | 7 | 277885 | Unplanned | VEGETATION - OUTSIDE ZONE | 13:49 - SMC Requested Jacob Off-Site - Chris Vivier is trying to organise a crew to attend under 2R 09/09 - Chris Vivier discussed with Spelly and Konagh on Friday 06/09 - FM coming out on Monday 09/09 to scoop for requirements to get repaired (Do we need helicopter etc) 13/09/2024 - Trees cut 12/09 and maybe 13/09. Urgent NAPA to be put in next week to get a helicopter out to run the new line. - HM 18/09/2024 - Phil Webby did a site visit 16/09, trees have been cut. Helicopter to be booked for next Wednesday 25/09, with an emergency permit to be put in for next Wednesday 25/09 - HM 04/10/2024 - Chopper to be organised for further date. Phil Webby to do site visit next week some time. - HM 23 Oct 24 - NAPA 116412 booked in for 06 Nov with Alt Date 08 Nov. 14/11/2024 - Copied to new NAPA 117295 on the 02/12/2024. MDP 06/12/2024 - Helicopter used to replace lines under NAPA 117295 refer JE24041324 | .
2968 |  | JE24031763 | PAPANUI ST | Eastern | PAPANUI ST | 2024-09-01 | 17:29 | 2024-09-01 | 22:11 | 0.0023326 | 8.2769e-06 | 3 | 845 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: TC4347 Fuses CAUSE: Lightning Temp generation (stage details when used): PERFORMANCE DETAIL Weather (wind/rain): Lightning Transformer replaced Power restored 22:10Hrs | .
2969 |  | JE24031766 | PIONEER RD | Western | PIONEER RD | 2024-09-01 | 19:00 | 2024-09-02 | 14:01 | 0.03262 | 5.7938e-05 | 21 | 11823 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: Fuses 8464 CAUSE: Lightning Temp generation (stage details when used): n PERFORMANCE DETAIL DNO (number or state no): n Circuit patrolled & type: cursory Weather (wind/rain): lighting Follow up required (select advisory)?n Additional fault restoration comments: TX Replaced 3 PH 50KVA | .
2970 |  | JE24031773 | IRIRANGI | Western | IRIRANGI | 2024-09-01 | 8:43 | 2024-09-01 | 13:44 | 0.0091337 | 3.0349e-05 | 11 | 3311 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 2563 No. Fuses: 2 Fuse Amp Size:6 TIME CLOSED: 13:43 Cause: lightning Weather (wind/rain): Follow up required (select advisory)?n | .
2971 |  | JE24031792 | PIONEER RD | Western | PIONEER RD | 2024-09-01 | 9:11 | 2024-09-01 | 17:00 | 0.0012962 | 2.759e-06 | 1 | 470 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 8403 No. Fuses: 2 Fuse Amp Size:3 TIME CLOSED: 17:00 Cause: Lightning Weather (wind/rain): lightning Follow up required (select advisory)? | .
2972 |  | JE24031794 | KAPANGA ROAD | Eastern | KAPANGA ROAD | 2024-09-01 | 7:00 | 2024-09-01 | 9:00 | 0.0019827 | 1.6554e-05 | 6 | 719 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location:TC4487 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 09:00 Cause: lightning Weather (wind/rain): lightning Follow up required (select advisory)? | .
2973 |  | JE24031815 | OTAKEHO | Western | OTAKEHO | 2024-09-01 | 10:01 | 2024-09-01 | 15:04 | 0.016663 | 0.00095736 | 347 | 6040 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2 blown transformers beyond Fuses MA298- M2050 & M2052 - Isolated at transformer No. Fuses: 2 Fuse Amp Size: 20 TIME CLOSED: 13:28 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? On re-livening Fuses MA298 CB 6 tripped, Fuses MA298 were isolated and line patrolled and a blown insulator was found on pole 717500, also 2 blown Tfr's M2050 & M2052 were found when line was re-livened, both Tfr's were Isolated. | .
2974 |  | JE24031819 | OTAMARAKAU | Eastern | OTAMARAKAU | 2024-09-01 | 14:40 | 2024-09-01 | 17:10 | 0.0016513 | 1.1036e-05 | 4 | 599 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 2, Fuses SE8-012 Protection flags (nil where none): Nil CAUSE: Burning HV cable termination Location: 227364 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4, Not patrolled. Weather (wind/rain): Calm LFI (Y/N + Comments): Yes, no operation Follow up Required (select advisory)? No Additional fault restoration comments: HV termination replaced due to corona discharge 1 x 25mm² single HV termination kit SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
2975 |  | JE24031820 | LAKE ALICE | Western | LAKE ALICE | 2024-09-01 | 10:05 | 2024-09-01 | 13:35 | 0.0011451 | 5.5179e-06 | 2 | 415 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 2767T No. Fuses: 2 Fuse Amp Size:2 TIME CLOSED: 13:29 Cause: lightning Weather (wind/rain): lightning Follow up required (select advisory)? Fuses Location: X506 No. Fuses: 2 Fuse Amp Size:2 TIME CLOSED: 13:35 Cause: Lightninhg Weather (wind/rain): Follow up required (select advisory)? | .
2976 |  | JE24031832 | MISSION RD | Western | MISSION RD | 2024-09-01 | 14:42 | 2024-09-01 | 18:50 | 0.00046047 | 1.6554e-05 | 3 | 167 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Transformer Faulty due to lightning strike - Returning in 2 hours or so with generator to restore power Installed Generator - Feeding Freezer and a few sockets Transformer X46 Needs replacing Isolated at TFR X46 Fuses Generator connected, 15:32 TFR Replaced, Generator removed, 18:45 full power restored 18:50 | .
2977 |  | JE24031841 | PIONEER RD | Western | PIONEER RD | 2024-09-01 | 11:01 | 2024-09-01 | 17:30 | 0.0021453 | 5.5179e-06 | 2 | 778 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 6543 No. Fuses: 2 Fuse Amp Size:10 TIME CLOSED: 17:30 Cause: lightning Weather (wind/rain): Follow up required (select advisory)?n | .
2978 |  | JE24031843 | RIVERSDALE GEN | Western | RIVERSDALE GEN | 2024-09-01 | 11:13 | 2024-09-01 | 14:21 | 0.00051971 | 2.759e-06 | 1 | 188 | Unplanned | WILDLIFE - BIRD | Fuses Location: 8164 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 14:20 Cause: Bird strike Pole 365611 Weather (wind/rain): High wind Follow up required (select advisory)? No | .
2979 |  | JE24031856 | MAIN RD MOTONUI | Western | MAIN RD MOTONUI | 2024-09-01 | 0:22 | 2024-09-01 | 11:30 | 0.0036851 | 5.5179e-06 | 2 | 1336 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 3937T No. Fuses: 2 Fuse Amp Size: 3Amp TIME CLOSED: 11:29 Cause: Lightning Weather (wind/rain): Rain, Lightning Follow up required (select advisory)? No | .
2980 |  | JE24031858 | MANGATARATA | Eastern | MANGATARATA | 2024-09-01 | 8:38 | 2024-09-01 | 9:00 | 0.00041504 | 1.9313e-05 | 7 | 150 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: TC2407 No. Fuses: 2 Fuse Amp Size:3 TIME CLOSED: 09:00 Cause: Lightening Weather (wind/rain):lightening Follow up required (select advisory)? | .
2981 |  | JE24031859 | IHURAUA | Western | IHURAUA | 2024-09-01 | 11:45 | 2024-09-03 | 15:54 | 0.031949 | 0.00022072 | 77 | 11580 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kv CB I4 Protection flags (nil when none): CAUSE: Tree Location: P20977 P10802 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state no): n Circuit patrolled & type: cursory Weather (wind/rain): Wind & Rain & Lightening Follow up required (select advisory)? Additional fault restoration comments: Tree through lines, Installed 2 Line breaks at poles P20977 & P10802 and got everyone back on. Then had to isolate at ABS I40 & ABS 10802 to remove trees and repair lines and close line breaks when Repair was done SUBTRANSMISSION DETAIL LOS to sub (no or sub name): Circuit that tripped: DTF (KM): | .
2982 |  | JE24031866 | MAIN RD MOTONUI | Western | MAIN RD MOTONUI | 2024-09-01 | 15:19 | 2024-09-02 | 12:21 | 0.045522 | 0.00035315 | 128 | 16500 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: Tfr 2695T CAUSE: Lightning Temp generation (stage details when used): n PERFORMANCE DETAIL DNO (number or state no): n Circuit patrolled & type: cursory Weather (wind/rain): rain & lightning Follow up required (select advisory)? Additional fault restoration comments: Replace Tfr 2695T 3 PH 15KVA | .
2983 |  | JE24031868 | KATERE 5 | Western | KATERE 5 | 2024-09-01 | 12:01 | 2024-09-02 | 15:44 | 0.0045892 | 2.759e-06 | 1 | 1663 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Open, Removed, & Tagged Fault Transformer Replace Tfr 1796N, line isolated at Fuses 6626 Restored 15:44 | .
2984 |  | JE24031870 | TOTARA ST | Western | TOTARA ST | 2024-09-01 | 10:12 | 2024-09-01 | 12:32 | 0.00038556 | 2.759e-06 | 1 | 140 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T2959 No. Fuses: 3 Fuse Amp Size:3A TIME CLOSED: 12:31 Cause: Lightening Weather (wind/rain):lightening Follow up required (select advisory)? | .
2985 |  | JE24031879 | INLAND COAST | Western | INLAND COAST | 2024-09-01 | 7:54 | 2024-09-01 | 14:43 | 0.0011285 | 2.759e-06 | 1 | 409 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 8474 No. Fuses: 2 Fuse Amp Size:3 TIME CLOSED: 14:43 Cause: lightning Weather (wind/rain): lightning Follow up required (select advisory)? | .
2986 |  | JE24031882 | TIROHIA-KARANGAHAKE | Eastern | TIROHIA-KARANGAHAKE | 2024-09-01 | 13:22 | 2024-09-01 | 13:45 | 6.5539e-05 | 2.759e-06 | 1 | 24 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: FC2360 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 13:45 Cause: Lightning Weather (wind/rain): Storm Follow up required (select advisory)? No Risk of flooding. Please call Steve Clark 021 535 061 once supply is restored | .
2987 |  | JE24031883 | LAKE ALICE | Western | LAKE ALICE | 2024-09-01 | 13:30 | 2024-09-01 | 20:45 | 0.0012005 | 2.759e-06 | 1 | 435 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 4709 No. Fuses: 2 Fuse Amp Size: 2 TIME CLOSED: 20:45 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n | .
2988 |  | JE24031892 | KAIMAI DRIVE | Eastern | KAIMAI DRIVE | 2024-09-01 | 14:06 | 2024-09-01 | 16:00 | 0.0006287 | 5.5179e-06 | 2 | 228 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: SE2-017 No. Fuses: 2 Fuse Amp Size:6 TIME CLOSED: 16:00 Cause: Lightning Weather (wind/rain): Follow up required (select advisory)?n | .
2989 |  | JE24031900 | KATERE 9 | Western | KATERE 9 | 2024-09-01 | 7:45 | 2024-09-01 | 13:51 | 0.0020172 | 5.5179e-06 | 2 | 731 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 457 No. Fuses: 3 Fuse Amp Size:3 TIME CLOSED: 13:45 Cause: lightning Weather (wind/rain):lightning Follow up required (select advisory)? Fuses Location: 6707 No. Fuses: 3 Fuse Amp Size: 8 TIME CLOSED: 13:50 Cause: lightning Weather (wind/rain): Follow up required (select advisory)? 2 Barrels replaced | .
2990 |  | JE24031902 | MAIN RD MOTONUI | Western | MAIN RD MOTONUI | 2024-09-01 | 14:32 | 2024-09-01 | 18:29 | 0.00065345 | 2.759e-06 | 1 | 237 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 3108T No. Fuses: 2 Fuse Amp Size: 2 TIME CLOSED: 18:29 Cause: lightning Weather (wind/rain): lightning Follow up required (select advisory)?n | .
2991 |  | JE24031907 | BROOKLANDS 12 | Western | BROOKLANDS 12 | 2024-09-01 | 4:30 | 2024-09-01 | 15:01 | 0.015669 | 2.4831e-05 | 9 | 5679 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Transformer 625 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 15:00 Cause: Lightning Weather (wind/rain): Stormy Follow up required (select advisory)? | .
2992 |  | JE24031914 | RANGIKURA | Western | RANGIKURA | 2024-09-01 | 15:40 | 2024-09-01 | 17:48 | 0.00035282 | 2.759e-06 | 1 | 128 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: X2310 No. Fuses: 3 Fuse Amp Size:2 TIME CLOSED: 17:48 Cause: lightning Weather (wind/rain): Follow up required (select advisory)?n | .
2993 |  | JE24031932 | OKOROIRE | Eastern | OKOROIRE | 2024-09-01 | 16:53 | 2024-09-01 | 19:45 | 0.00047642 | 2.759e-06 | 1 | 173 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Fuses FC873 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 19:45 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? No | .
2994 |  | JE24031946 | OKOROIRE | Eastern | OKOROIRE | 2024-09-01 | 21:27 | 2024-09-02 | 8:48 | 0.0037529 | 5.5179e-06 | 2 | 1360 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: FP1007 No. Fuses: 2 Fuse Amp Size:6 TIME CLOSED: 08:47 Cause: Weather / LIne Clash Weather (wind/rain):Wind Follow up required (select advisory)?n | .
2995 |  | JE24028550 | 30 CENTENNIAL DRIVE MOTUROA NEW PLYMOUTH | Western | CENTENNIAL DR | 2024-08-31 | 8:45 | 2024-08-31 | 15:34 | 0.036408 | 9.1046e-05 | 33 | 13196 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Northpower to, replace pole 748448 & ABS 192. Downer to repair DNO2406016 on cable termination at links 12380. Downer will sign onto Northpower permit and complete repairs. | .
2996 |  | JE24031334 | HOE-O-TAINUI | Eastern | HOE-O-TAINUI | 2024-08-31 | 9:31 | 2024-08-31 | 10:48 | 0.010043 | 0.00012967 | 47 | 3640 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Job to be done under Urgent Works on Saturday 30/08/24 JE24031504 LV & HV Cross arms replaced at Pole K2338 E00149 advertised 30/08 at 12:20, outage is unplanned | .
2997 |  | JE24031491 | IHURAUA | Western | IHURAUA | 2024-08-31 | 7:28 | 2024-08-31 | 9:01 | 0.0027951 | 3.0349e-05 | 11 | 1013 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: I8 No. Fuses: 2 Fuse Amp Size: 8 TIME CLOSED: 09:00 Cause: unknown Weather (wind/rain): calm Follow up required (select advisory)? | .
2998 |  | JE24031495 | WESTMERE GLADSTONE | Western | WESTMERE GLADSTONE | 2024-08-31 | 8:05 | 2024-08-31 | 14:15 | 0.032686 | 0.00044419 | 94 | 11847 | Unplanned | LIGHTNING - LIGHTNING STRIKE | REGULATORY INFORMATION Voltage & Device ID: Recloser 7417 Protection flags (nil where none): EF, Phase A Fault CAUSE: Faulty Transformer T1825 Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Lightning LFI (Y/N + Comments): Follow up Required (select advisory)? No Additional fault restoration comments: Transformer T1825 was just replaced 24hrs earlier on 30/08/24 Transformer replaced, Power ON @ 14:15 Hrs | .
2999 |  | JE24031510 | WHITIANGA-COROMANDEL 66KV | Eastern | WHITIANGA-COROMANDEL 66KV | 2024-08-31 | 10:33 | 2024-08-31 | 10:40 | 0.05529 | 0.0082934 | 3006 | 20040 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: TAI CB 60 Protection flags (nil where none): EF, Phase A Fault CAUSE: Seagulls Location: Pole CGNTAI011 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: Cursory Weather (wind/rain): Rainy LFI (Y/N + Comments): At Poles CGNWHT037, 858511, (both indicating RED pointing towards Tairua Sub, CGNTAI018 indicating Green Middle Phase pointing towards Whitianga Follow up Required (select advisory)? No. Additional fault restoration comments: No fault found on lines but two seagulls at Pole CGNTAI001 one dead and another still alive. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Coromandel Circuit that tripped: TAI CB 60/ WHT CB 50 DTF (KM): Nil | .
3000 |  | JE24031521 | MANGATAINOKA | Western | MANGATAINOKA | 2024-08-31 | 13:41 | 2024-08-31 | 14:51 | 0.00019414 | 2.759e-06 | 1 | 70 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: Fuses 10025 CAUSE:Blown transformers 7070P Temp generation (stage details when used): n PERFORMANCE DETAIL DNO (number or state no): n Circuit patrolled & type: cursory Weather (wind/rain): wind, Lightning Follow up required (select advisory)?n Additional fault restoration comments:n | .
3001 |  | JE24031543 | JUNCTION RD | Western | JUNCTION RD | 2024-08-31 | 17:58 | 2024-08-31 | 19:45 | 0.0011833 | 1.1036e-05 | 4 | 429 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 793 No. Fuses: 3 Fuse Amp Size: 3 TIME CLOSED: 19:45 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n | .
3002 |  | JE24031544 | JUNCTION RD | Western | JUNCTION RD | 2024-08-31 | 17:55 | 2024-08-31 | 20:40 | 0.016234 | 0.00011588 | 42 | 5884 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 8605 No. Fuses: 2 Fuse Amp Size: 15 TIME CLOSED: 20:10 Cause: lightning Weather (wind/rain): lightning Follow up required (select advisory)?n Fuses Location: 2052N No. Fuses: 3 Fuse Amp Size: 2 TIME CLOSED: 20:30 Cause: lightning Weather (wind/rain): lightning Follow up required (select advisory)?n Fuses Location: 2196N No. Fuses: 1 Fuse Amp Size: 3 TIME CLOSED: 20:40 Cause: lightning Weather (wind/rain): lightning Follow up required (select advisory)?n | .
3003 |  | JE24031550 | INLAND COAST | Western | INLAND COAST | 2024-08-31 | 18:58 | 2024-09-01 | 11:36 | 0.0027511 | 2.759e-06 | 1 | 997 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 8187 No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 11:35 Cause: Lighting Weather (wind/rain):lighting Follow up required (select advisory)?na | .
3004 |  | JE24031554 | TOTMANS RD | Eastern | TOTMANS RD | 2024-08-31 | 19:38 | 2024-08-31 | 21:24 | 0.034164 | 0.0011891 | 431 | 12383 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 13260/2 Protection flags (nil where none): A Ø O/C CAUSE: Tree Branch on the O/H Line (Touching/causing sparks) Location: Between Poles E1595 & E1596 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Rain + Lightning LFI (Y/N + Comments): Yes, at Pole E13009. ( This really helped us sectionalize and find the faulty spur line) Follow up Required (select advisory)? Yes, major tree trimming is required as per the field switcher on site. We will keep having similar faults on this spur line unless the trees are trimmed ASAP. Additional fault restoration comments: Feeder fault tripped and the LFI's activated at Pole E13009 - Field Switcher informed. NOC was able to put in a back feed by opening REC 13085/2 and then closing SEC 14818/2 (TIR5) Once the Field Switcher arrived on site and confirmed the LFI's were flashing, NOC advised field switcher to open ABS 808 which was then carried out. NOC then closed in REC 13260/2 at 20:16 Tree branch was then removed/cut away from ground level using insulated tools. Remaining ICP's Power was restored by closing in ABS 808 at 21:24 | .
3005 |  | JE24031555 | KOHETE RD | Western | KOHETE RD | 2024-08-31 | 19:44 | 2024-09-01 | 12:15 | 0.0054677 | 5.5179e-06 | 2 | 1982 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Transformer 2236T No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 12:15 Cause: Lightning Weather (wind/rain): Stormy Follow up required (select advisory)? | .
3006 |  | JE24031556 | KOHETE RD | Western | KOHETE RD | 2024-08-31 | 19:46 | 2024-08-31 | 22:01 | 0.001491 | 1.1036e-05 | 4 | 540 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 3053T No. Fuses: 3 Fuse Amp Size: 3 TIME CLOSED: 22:00 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n | .
3007 |  | JE24031557 | TE MIRO RD | Eastern | TE MIRO RD | 2024-08-31 | 20:02 | 2024-09-01 | 16:33 | 0.13738 | 0.0010263 | 372 | 49793 | Unplanned | LIGHTNING - LIGHTNING STRIKE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 9121/2 Protection flags (nil where none): E/F CAUSE: Blown Transformer TC4561 Location: TC4561 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Rain, Wind & Lightning. LFI (Y/N + Comments): Yes, at Poles I13129 & I13174 Follow up Required (select advisory)? Additional fault restoration comments: Feeder fault with two LFI's active at Poles I13129 & I13174 Field switcher opened ABS 2606 and NOC closed in REC 9121/2 at 20:51 Upon further fault-finding it was determined that the fault was beyond ABS 1302 and the access and conditions were not very suitable. Field Switcher will return during daylight hours to continue looking for the fault. ABS 1302 is left Open, Locked & Tagged Blown transformer TC4561 found during fault finding. 1 x 15kVA 1 Ø transformer replaced. | .
3008 |  | JE24031559 | STRATHMORE | Western | STRATHMORE | 2024-08-31 | 20:07 | 2024-09-02 | 13:00 | 0.23986 | 0.00016002 | 58 | 86940 | Unplanned | LIGHTNING - LIGHTNING STRIKE | REGULATORY INFORMATION Voltage & Device ID: Rec 4915 had tripped on arrival Protection flags (nil where none): nil CAUSE: Lines down Location: Pole 708707 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No):n Circuit patrolled and type: Operational patrolled Weather (wind/rain): Lighting / Storm LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Also Reload reliven TX 4148T 1 Fuse 3 Amp Closed 13:00 lightning SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3009 |  | JE24031560 | TE ROTI | Western | TE ROTI | 2024-08-31 | 22:16 | 2024-09-01 | 13:55 | 0.012961 | 1.3795e-05 | 5 | 4698 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Line down at Pole 733670, unable to fix tonight due to weather Isolated at Fuses 5982 Lines Down at Pole 733670 Restored at 13:55 Phil Webby - Brent LAnders | .
3010 |  | JE24031562 | TARATA | Western | TARATA | 2024-08-31 | 20:11 | 2024-09-01 | 14:02 | 0.023632 | 2.2072e-05 | 8 | 8565 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Fuses 8600 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 14:02 Cause: Lightning Weather (wind/rain): Fine Follow up required (select advisory)? NIL | .
3011 |  | JE24031563 | KOHETE RD | Western | KOHETE RD | 2024-08-31 | 20:18 | 2024-09-01 | 12:51 | 0.0027389 | 2.759e-06 | 1 | 993 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 4412T No. Fuses: 3 Fuse Amp Size:2A TIME CLOSED: 12:50 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? | .
3012 |  | JE24031564 | PIAKOITI RD | Eastern | PIAKOITI RD | 2024-08-31 | 20:26 | 2024-09-01 | 0:21 | 0.003546 | 1.6554e-05 | 6 | 1285 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: FC1487 No. Fuses: 3 Fuse Amp Size: 10 Amp TIME CLOSED: 23:30 Cause: Lightning Weather (wind/rain): Rain/wind/lightning. Follow up required (select advisory)? No Fuses Location: TX TC295 No. Fuses: 3 Fuse Amp Size: 3 Amp TIME CLOSED: 23:50 Cause: Lightning Weather (wind/rain): Rain/wind/lightning. Follow up required (select advisory)? Fuses Location: TX TC3956 No. Fuses: 3 Fuse Amp Size: 3 Amp TIME CLOSED: 00:20 Cause: Lightning Weather (wind/rain): Rain/wind/lightning. Follow up required (select advisory)? | .
3013 |  | JE24031567 | OKOROIRE | Eastern | OKOROIRE | 2024-08-31 | 20:35 | 2024-09-01 | 17:06 | 0.0067965 | 5.5179e-06 | 2 | 2463 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: TC2726 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 17:06 Cause: lightning Weather (wind/rain): Follow up required (select advisory)?n | .
3014 |  | JE24031569 | HUKANUI | Western | HUKANUI | 2024-08-31 | 20:37 | 2024-08-31 | 22:52 | 0.00037191 | 2.759e-06 | 1 | 135 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T8/240 No. Fuses: 2 Fuse Amp Size: 2 TIME CLOSED: 22:52 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n | .
3015 |  | JE24031571 | OKOROIRE | Eastern | OKOROIRE | 2024-08-31 | 20:43 | 2024-09-01 | 18:04 | 0.01413 | 1.1036e-05 | 4 | 5121 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Fuses 1477 No. Fuses: 3 Fuse Amp Size: 3A TIME CLOSED: 18:03 Cause: Lightning Weather (wind/rain): Fine Follow up required (select advisory)? NIL | .
3016 |  | JE24031581 | TAWHITI RD | Western | TAWHITI RD | 2024-08-31 | 21:21 | 2024-09-02 | 12:17 | 0.28818 | 0.00253 | 888 | 104454 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 5 Protection flags (nil where none): E/F, O/C A & B CAUSE: 2 x Faults - #1 - Lines Down - # 2 - Broken DDO's at Fuses CA426 Location: # 1 - 723255 - # 2 - Fuses CA426 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): lightning LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Gas/Sw 8726 failed to operate remotely(faulty batteries) This job had 2 faults as above. JE24031599 Child job outage step removed and outage step added to JE24031581 as power was isolated at 22.25 during the time of this outage | .
3017 |  | JE24031589 | CLIMIE RD | Western | CLIMIE RD | 2024-08-31 | 21:56 | 2024-09-01 | 17:10 | 0.015914 | 1.3795e-05 | 5 | 5768 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: TX 2885T No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 17:10 Cause: lightning Weather (wind/rain): Follow up required (select advisory)?n | .
3018 |  | JE24031592 | MANGAWEKA | Western | MANGAWEKA | 2024-08-31 | 23:45 | 2024-09-02 | 13:39 | 0.14429 | 6.3456e-05 | 23 | 52300 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: Fuses 2813 Protection flags (nil where none): Nil CAUSE: Lines Down in four sites Tree clearing Brocken Cross arms Location: Down Stream of Pole 810401 Temp generation (state details when used):na PERFORMANCE DETAIL DNO (number or state No):n Circuit patrolled and type: Operational patrol Weather (wind/rain): Lightning Storm LFI (Y/N + Comments): na Follow up Required (select advisory)? n Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3019 |  | JE24031595 | TOKO | Western | TOKO | 2024-08-31 | 23:03 | 2024-09-01 | 10:27 | 0.53598 | 0.0014071 | 293 | 194268 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | REGULATORY INFORMATION Voltage & Device ID: 11kV CB D31 Protection flags (nil where none): O/C B & C CAUSE: Bark On Line Location: Pole 739663 Temp generation (state details when used): NIL PERFORMANCE DETAIL DNO (number or state No): NIL Circuit patrolled and type: Cursory Patrol Weather (wind/rain): Wind, Lightning LFI (Y/N + Comments): NIL Follow up Required (select advisory)? NIL Additional fault restoration comments: | .
3020 |  | JE24031596 | PUNGAREHU | Western | PUNGAREHU | 2024-08-31 | 23:14 | 2024-09-01 | 13:40 | 0.035825 | 4.1384e-05 | 15 | 12985 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: PU303 No. Fuses: 2 Fuse Amp Size: 15A TIME CLOSED: 13:39 Cause: lightning Weather (wind/rain): lightning Follow up required (select advisory)?NA | .
3021 |  | JE24031600 | PARK RD | Western | PARK RD | 2024-08-31 | 23:17 | 2024-09-01 | 1:20 | 0.014234 | 0.00011588 | 42 | 5159 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Fuses 7600 No. Fuses: 2 Fuse Amp Size: 20 Amp TIME CLOSED: 01:20 Cause: Lightning Weather (wind/rain): Rain/Lightning Follow up required (select advisory)? No | .
3022 |  | JE24031601 | PARIHAKA | Western | PARIHAKA | 2024-08-31 | 23:29 | 2024-09-03 | 20:19 | 0.14976 | 0.0016443 | 227 | 54282 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: Tfr P4205 Fuses CAUSE: Lightning Temp generation (stage details when used): n PERFORMANCE DETAIL DNO (number or state no): n Circuit patrolled & type: cursory Weather (wind/rain): Rain & Lightning Follow up required (select advisory)? Additional fault restoration comments: Replace Tfr P4205 03/09/2024 - 16:20 - 80 year old man, without power from the 31/08/2024 - Have escalated this to the SMC to be resolved ASAP. MDP 16:40 - SMC advised crew on the way to have the transformer replaced tonight. MDP | .
3023 |  | JE24031602 | BROOKLANDS 7 | Western | BROOKLANDS 7 | 2024-08-31 | 23:21 | 2024-09-01 | 15:52 | 0.29908 | 0.00035867 | 130 | 108404 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11KV REC 12596/2 Protection flags (nil where none): C ph O/C & E/F CAUSE: Tree through lines Location: 701817 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: cursory Weather (wind/rain): Lightning & rain LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Line was isolated at ABS's 295 & 376 to repair the lines Called Hub to Advise of the lines down on the road and multiple calls coming in 08:47 | .
3024 |  | JE24031605 | PIONEER RD | Western | PIONEER RD | 2024-08-31 | 23:29 | 2024-09-02 | 17:07 | 0.045394 | 0.00014071 | 51 | 16453 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: Tfr 1131 CAUSE: Lightning Temp generation (stage details when used): n PERFORMANCE DETAIL DNO (number or state no): n Circuit patrolled & type: cursory Weather (wind/rain): Rain & lighting Follow up required (select advisory)? Additional fault restoration comments: Tfr 1131 isolated to be replaced Transformer 1131 Replaced | .
3025 |  | JE24031617 | CLOTON RD INDUSTRIAL | Western | CLOTON RD INDUSTRIAL | 2024-08-31 | 23:55 | 2024-09-02 | 19:43 | 0.23082 | 0.00056283 | 114 | 83660 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11KV REC 4848/2 Protection flags (nil where none): E/F CAUSE: Broken insulator Location: 738160 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: cursory Weather (wind/rain): Lightning LFI (Y/N + Comments): n Follow up Required (select advisory)? Additional fault restoration comments: Line was patrolled and sectionalized and a broken insulator was found on pole 738160, line was isolated at Fuses 4978 to replace insulator. Faultman also found 3 blown Tfr's 2737T, 3406T & 2734T, all 3 Tfr's have been isolated. 2R used to Replace Insulator New 2R's for Transformer replacement, Blown Transformers - 2737T, 2406T & 2734T + other damaged equipment. 02/09/24 Tx 2734T 30KVA tx replaced isolation 31/08 23:55-02/09 15:50 02/09/24 Tx 2737T 30KVA tx replaced isolation 31/08 23:55-02/09 13:57 Tx 2406 replacement under child JE24032132 | .
3026 |  | JE24028322 | 204 BRIDGE STREET BULLS BULLS | Western | BULLS 33KV | 2024-08-30 | 23:30 | 2024-08-30 | 23:31 | 0.0036308 | 0.0036308 | 1316 | 1316 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Offload Bulls Sub then Transfer Bulls Sub to Ohakea Sub - Break Make required | .
3027 |  | JE24028845 | 135 MCBETH ROAD HIKUAI HIKUAI | Eastern | HIKUAI | 2024-08-30 | 9:46 | 2024-08-30 | 14:40 | 0.02194 | 7.4492e-05 | 27 | 7952 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install fibre between poles U0560/U12881 & 388039 | .
3028 |  | JE24030775 | 102 HENDERSONS LINE MARTON MARTON | Western | CROFTON | 2024-08-30 | 9:33 | 2024-08-30 | 15:18 | 0.0047516 | 1.3795e-05 | 5 | 1722 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Urgent - Straighten pole 793825 and concrete foundation, apply temporary stay. | .
3029 |  | JE24031108 | INGLEWOOD NORTH 33KV | Western | INGLEWOOD NORTH 33KV | 2024-08-30 | 10:50 | 2024-08-30 | 13:19 | 0.010646 | 7.1733e-05 | 26 | 3859 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Voltage & Device ID: 33kV CB 191 Protection flags (nil where none): A, B, C Ph O/C E/F Weather (wind/rain): Lightning Follow up required (select advisory): LFI Activation: Y/N Y Poles 760621 & 760322 Ing Sub auto change over activated Cracked Isolator at Pole 760315, Replaced 3 x Pin Insulators Isolated at ABS's 166 & 211 FM to return in day light for repairs beyond Fuses 5402. Ing sub transferred back to HUI GXP | .
3030 |  | JE24031207 | BAINESSE | Western | BAINESSE | 2024-08-30 | 1:17 | 2024-08-30 | 12:10 | 0.0072081 | 1.1036e-05 | 4 | 2613 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Transformer T2/494 found to be faulty Isolated at Transformer fuses FM to return in day light to replace transformer, due to Lightning Isolated at TFR T2/494 Fuses TFR Replaced, Full power restored | .
3031 |  | JE24031212 | MOUNT BRUCE | Western | MOUNT BRUCE | 2024-08-30 | 11:20 | 2024-08-30 | 12:15 | 0.00015266 | 2.759e-06 | 1 | 55 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Faulty TFR T659 due to Lightning strike Isolated at TFR T659 Fuses TFR Replaced, Full power restored | .
3032 |  | JE24031227 | OTAUTU | Western | OTAUTU | 2024-08-30 | 9:30 | 2024-08-30 | 15:01 | 0.002737 | 8.2769e-06 | 3 | 992 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: 11kV DTX L4295 3 phase 30 KVA Blown CAUSE: Lightning PERFORMANCE DETAIL Weather (wind/rain): Lightnning Follow up required (select advisory)? No Additional fault restoration comments: Livened 15:00 | .
3033 |  | JE24031237 | TIKORANGI | Western | TIKORANGI | 2024-08-30 | 11:46 | 2024-08-30 | 15:02 | 0.0016203 | 8.2769e-06 | 3 | 587 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Customer still has no power to his freezer fridges and animals has no water Please call James - 027 441 0437 with an update on when the FM will attend? Konagh to advise. Orbotech onsite changing the TX 3 phase 30kVA Customer has been advised and he spoke to the contractors that is onsite. Replaced @ 15:01 | .
3034 |  | JE24031246 | WAREA | Western | WAREA | 2024-08-30 | 11:51 | 2024-08-30 | 15:40 | 0.00063346 | 2.759e-06 | 1 | 230 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: 6475 Failed 3 phase 50kVA DTX 5250E CAUSE: Lightning PERFORMANCE DETAIL Weather (wind/rain): Lightning Follow up required (select advisory)? Additional fault restoration comments: New 3 phase 50kVA Replaced | .
3035 |  | JE24031247 | WAREA | Western | WAREA | 2024-08-30 | 5:42 | 2024-08-30 | 10:30 | 0.0015873 | 5.5179e-06 | 2 | 575 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: PU235 No. Fuses: 2 Fuse Amp Size:3 TIME CLOSED: 10:29 Cause: Lightening Weather (wind/rain): Lightening Follow up required (select advisory)? | .
3036 |  | JE24031250 | WAITARA RD | Western | WAITARA RD | 2024-08-30 | 14:13 | 2024-08-30 | 17:53 | 0.0006049 | 2.759e-06 | 1 | 219 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: DTX 2171N 3 phase 30kVA Replaced CAUSE: Lightning PERO FORMANCE DETAIL Weather (wind/rain): Lightning Follow up required (select advisory)? No Additional fault restoration comments: Livened 17:52 | .
3037 |  | JE24031251 | TOTMANS RD | Eastern | TOTMANS RD | 2024-08-30 | 6:21 | 2024-08-30 | 9:03 | 0.0011884 | 8.2769e-06 | 3 | 431 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: TP2598 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 08:24 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? offline tx did not make job - No customers on tx TP2598 no outage step Fuses Location: FP1382 No. Fuses: 3 Fuse Amp Size: 6 TIME CLOSED: 08:36 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?v Fuses Location: tp2336 No. Fuses: 3 Fuse Amp Size: 2 TIME CLOSED: 08:45 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?v Fuses Location: TP4286 No. Fuses: 3 Fuse Amp Size: 3 TIME CLOSED: 09:03 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?v | .
3038 |  | JE24031253 | WAREA | Western | WAREA | 2024-08-30 | 6:33 | 2024-08-30 | 13:50 | 0.0012061 | 2.759e-06 | 1 | 437 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: PU214 No. Fuses: 3 Fuse Amp Size:3 TIME CLOSED: 13:49 Cause: lightning Weather (wind/rain): lightning Follow up required (select advisory)?n | .
3039 |  | JE24031256 | DUTHIE RD | Western | DUTHIE RD | 2024-08-30 | 5:06 | 2024-08-30 | 7:26 | 0.034238 | 0.00024555 | 89 | 12410 | Unplanned | THIRD PARTY INTERFERENCE - VANDALISM/THEFT | Padlock cut off the ABS 6013 & ABS opened by unknown persons. No lock found. This has happened in this area before. ABS closed Power restored. First Call 05:06. Lock taken !!! | .
3040 |  | JE24031258 | WAITARA RD | Western | WAITARA RD | 2024-08-30 | 6:55 | 2024-08-30 | 13:10 | 0.0020741 | 5.5179e-06 | 2 | 752 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 1598 No. Fuses: 3 Fuse Amp Size:3 TIME CLOSED: 13:10 Cause: lightning Weather (wind/rain): lightning Follow up required (select advisory)? | .
3041 |  | JE24031276 | MAURICEVILLE | Western | MAURICEVILLE | 2024-08-30 | 9:40 | 2024-08-30 | 12:50 | 0.0010503 | 5.5179e-06 | 2 | 381 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Faulty TFR T8/67 due to Lightning Strike Isolated at TFR T8/67 Fuses TFR Replaced, Full power restored | .
3042 |  | JE24031278 | MOUNT BRUCE | Western | MOUNT BRUCE | 2024-08-30 | 7:46 | 2024-08-30 | 11:09 | 0.0011208 | 5.5179e-06 | 2 | 406 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T646 No. Fuses: 2 Fuse Amp Size: 3 Time closed 11:09 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n | .
3043 |  | JE24031283 | TOTMANS RD | Eastern | TOTMANS RD | 2024-08-30 | 8:04 | 2024-08-30 | 9:33 | 0.00098287 | 1.1036e-05 | 4 | 356 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: TC335 No. Fuses: 2 Fuse Amp Size:2 TIME CLOSED: 09:32 Cause: lightening Weather (wind/rain): Follow up required (select advisory)? | .
3044 |  | JE24031292 | TOTARA ST | Western | TOTARA ST | 2024-08-30 | 8:39 | 2024-08-30 | 10:03 | 0.0013996 | 1.6554e-05 | 6 | 507 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 7750 No. Fuses: 3 Fuse Amp Size: 8 TIME CLOSED: 10:03 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n | .
3045 |  | JE24031300 | BAINESSE | Western | BAINESSE | 2024-08-30 | 8:54 | 2024-08-30 | 10:00 | 0.00054803 | 8.2769e-06 | 3 | 199 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T2/80 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 10:00 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n | .
3046 |  | JE24031301 | MOUNT BRUCE | Western | MOUNT BRUCE | 2024-08-30 | 8:54 | 2024-08-30 | 9:09 | 4.0573e-05 | 2.759e-06 | 1 | 15 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T2320 No. Fuses: 3 Fuse Amp Size:3 TIME CLOSED: 09:09 Cause: lightening Weather (wind/rain): lightening Follow up required (select advisory)? | .
3047 |  | JE24031322 | TOKO | Western | TOKO | 2024-08-30 | 14:36 | 2024-08-30 | 18:11 | 0.0011881 | 5.5179e-06 | 2 | 431 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: Failed dtx 3690T 3 phase 15kVA CAUSE: lightning Temp generation (stage details when used): PERFORMANCE DETAIL Weather (wind/rain): Lightning Follow up required (select advisory)? No Additional fault restoration comments: Livened 18:10 | .
3048 |  | JE24031330 | PUNGAREHU | Western | PUNGAREHU | 2024-08-30 | 9:57 | 2024-08-30 | 13:36 | 0.00060426 | 2.759e-06 | 1 | 219 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Fuses 6993 No. Fuses: 3 Fuse Amp Size: 2A TIME CLOSED: 13:35 Cause: Lightning Weather (wind/rain): Rain Follow up required (select advisory)? No | .
3049 |  | JE24031333 | CHESTER RD | Western | CHESTER RD | 2024-08-30 | 10:58 | 2024-08-30 | 11:05 | 2.0021e-05 | 2.759e-06 | 1 | 7 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Job at Incorrect Location, Correct Location is T2938 Fuses Location: T2938 No. Fuses: 2 Fuse Amp Size: 2 TIME CLOSED: 11:05 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n | .
3050 |  | JE24031353 | TOTMANS RD | Eastern | TOTMANS RD | 2024-08-30 | 6:22 | 2024-08-30 | 8:46 | 0.00039633 | 2.759e-06 | 1 | 144 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: tp2336 No. Fuses: 3 Fuse Amp Size: 2 TIME CLOSED: 08:45 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?v | .
3051 |  | JE24031366 | MANGATAINOKA | Western | MANGATAINOKA | 2024-08-30 | 11:17 | 2024-08-30 | 13:45 | 0.0075374 | 6.6215e-05 | 24 | 2732 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: R15 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 13:05 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? Fuses Location: T7/35 No. Fuses: 1 Fuse Amp Size: 2 TIME CLOSED: 13:10 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? Fuses Location: T7/33 No. Fuses: 3 Fuse Amp Size: 2 TIME CLOSED: 13:45 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? | .
3052 |  | JE24031368 | MANGATAINOKA | Western | MANGATAINOKA | 2024-08-30 | 11:28 | 2024-08-30 | 14:16 | 0.0056508 | 3.5867e-05 | 13 | 2048 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: R27 No. Fuses: 1 Fuse Amp Size: 10 TIME CLOSED: 13:56 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n Fuses Location: T7/97 No. Fuses: 2 + Replaced 1 x Barrel Fuse Amp Size: 2 TIME CLOSED: 14:15 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n | .
3053 |  | JE24031369 | WESTMERE GLADSTONE | Western | WESTMERE GLADSTONE | 2024-08-30 | 14:00 | 2024-08-30 | 17:56 | 0.0030726 | 0.00025934 | 94 | 1114 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Faulty TFR T1825 due to Lightning strike Isolated at TFR T1825 Fuses TFR Replaced, Full power restored | .
3054 |  | JE24031377 | KAKARAMEA | Western | KAKARAMEA | 2024-08-30 | 14:51 | 2024-08-30 | 18:29 | 0.00060072 | 2.759e-06 | 1 | 218 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Transformer L4477 found to be faulty Isolated at Transformer fuses Transformer replaced. Power restored 18:28 | .
3055 |  | JE24031379 | MANGAMAIRE | Western | MANGAMAIRE | 2024-08-30 | 11:49 | 2024-08-30 | 12:01 | 9.6834e-05 | 8.2769e-06 | 3 | 35 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T8/284 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 12:00 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n | .
3056 |  | JE24031390 | MAUNGARANGI RD | Eastern | MAUNGARANGI RD | 2024-08-30 | 16:16 | 2024-09-09 | 14:40 | 0.0018543 | 1.6554e-05 | 3 | 672 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Reload reliven failing on closing Fuses SE6-200 even with Transformer TE6-247 Fuses open. Suspect Cable Fault. Generator connected at TE6-247 at 19:05 DNO 2409007 Created 09/09/24 Cable repair 25-95mm Repair Kit Single HV Cable - tx TE6-247 fuses Isolated 10:38 Generator removed 13:45 TE6-247 Fuses closed 14:40 | .
3057 |  | JE24031392 | EKETAHUNA | Western | EKETAHUNA | 2024-08-30 | 12:34 | 2024-08-30 | 14:24 | 0.0030508 | 2.759e-05 | 10 | 1106 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T8/23 No. Fuses: 1 Fuse Amp Size: 2 TIME CLOSED: 14:01 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n Fuses Location: U9 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 14:24 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n | .
3058 |  | JE24031393 | WAREA | Western | WAREA | 2024-08-30 | 18:10 | 2024-08-30 | 23:53 | 0.0099217 | 0.00011312 | 39 | 3596 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses PU225 found damaged & Transformer P1200 Blown Isolated at Fuses 5068 to replace Fuses PU225 Fuses for Transformer Fuses replaced, Transformer Replaced | .
3059 |  | JE24031420 | MANGATAINOKA | Western | MANGATAINOKA | 2024-08-30 | 14:30 | 2024-08-30 | 14:42 | 3.4507e-05 | 2.759e-06 | 1 | 13 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T7/72 No. Fuses: 2 Fuse Amp Size: 2 TIME CLOSED: 14:42 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n | .
3060 |  | JE24031446 | TAVERNER ST | Western | TAVERNER ST | 2024-08-30 | 15:58 | 2024-08-31 | 15:20 | 0.0045573 | 1.1036e-05 | 4 | 1652 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location:7536 No. Fuses: 1 Fuse Amp Size: 8 TIME CLOSED: 17:55 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n TFR T3234 faulty due to Lightning strike Isolated at TFR T3234 Fuses Will be left off over night as only feeds a pump, farmer OK with this Transformer replaced, Power ON 15:20 (31/08/24) | .
3061 |  | JE24031455 | MAURICEVILLE | Western | MAURICEVILLE | 2024-08-30 | 16:45 | 2024-08-30 | 18:05 | 0.00066457 | 8.2769e-06 | 3 | 241 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T8/86 No. Fuses: 3 Fuse Amp Size: 2 TIME CLOSED: 18:05 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n | .
3062 |  | JE24031463 | TARATA | Western | TARATA | 2024-08-30 | 17:01 | 2024-08-30 | 19:36 | 0.0017167 | 1.1036e-05 | 4 | 622 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 3435T No. Fuses: 2 Fuse Amp Size: 2 Amp TIME CLOSED: 19:36 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? N | .
3063 |  | JE24031467 | MANGATEPARU | Eastern | MANGATEPARU | 2024-08-30 | 19:03 | 2024-08-30 | 19:13 | 0.00045026 | 4.4143e-05 | 16 | 163 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: took loop readings they where fine - checked connections unsure what the problem 100kVA Transformer. Having problems with IS 2R required? Yes Additional Info: Fuses checked at FP1220 No fuses: 3 + Broken barrel Size: 20 Amp Power OFF: 19:02 Power ON: 19:12 Cause: Deterioration Weather: Calm Follow up required: No | .
3064 |  | JE24031468 | MOUNT BRUCE | Western | MOUNT BRUCE | 2024-08-30 | 17:48 | 2024-08-30 | 19:30 | 0.00056423 | 5.5179e-06 | 2 | 205 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: TX T678 No. Fuses: 3 Fuse Amp Size: 2 Amp TIME CLOSED: 19:30 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? No | .
3065 |  | JE24031470 | BRISTOL RD | Western | BRISTOL RD | 2024-08-30 | 19:59 | 2024-08-31 | 10:56 | 0.026322 | 0.00015726 | 57 | 9541 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Transformer 3585T found to be faulty Isolated at Transformer fuses FM to return tomorrow to replace transformer FM is onsite replacing TX Line was isolated at ABS 5378 to replace Tfr 3585T, line was isolated due to line been to close to replace Tfr safely. | .
3066 |  | JE24028110 | 22 PRINCES STREET PUTARURU PUTARURU | Eastern | BENT ST | 2024-08-29 | 23:30 | 2024-08-30 | 3:05 | 0.049811 | 0.00023175 | 84 | 18054 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Omexom - RMU 11kv oil maintenance IC2035-FC5021-IC1571 Northpower - Work on Sw/ Gear IC2039-IC1594-IC1579-IC1590-FC5036 "works to remove DNO 2406007" | .
3067 |  | JE24028266 | 201 BLACK ROAD PAENGAROA TE PUKE | Eastern | ROYDEN DOWNS RD | 2024-08-29 | 8:45 | 2024-08-29 | 13:57 | 0.052534 | 0.0001683 | 61 | 19041 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv overhead conductors with 3 W Squirrel between poles 495814 & 221740. 11kv isolation @ ABS 14861.issuer earths @ pole 495814 ( 33kv isolation's @ ABS 3162, CB 3112, ABS 76, AB S66. Issuer earths @ pole 483546(483569 side), pole 483546(483554 side) & earth switch 3119. | .
3068 |  | JE24028267 | 350 PLYMOUTH ROAD KORU NEW PLYMOUTH | Western | PIONEER RD | 2024-08-29 | 9:00 | 2024-08-29 | 15:03 | 0.04973 | 0.00014347 | 52 | 18025 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 755174,755180,755183,755184,755186,755189,755190,755191. | .
3069 |  | JE24028268 | 942 HORRELL ROAD TE PUNINGA MORRINSVILLE | Eastern | TE PUNINGA | 2024-08-29 | 8:31 | 2024-08-29 | 13:50 | 0.061659 | 0.00019313 | 70 | 22349 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV Pole K0343 with new pole and new ABS 901. | .
3070 |  | JE24028278 | 3376 TARATA ROAD PURANGI INGLEWOOD | Western | TARATA | 2024-08-29 | 9:30 | 2024-08-29 | 15:10 | 0.015953 | 4.6902e-05 | 17 | 5782 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace various crossarms in between poles 762287 - 762308 | .
3071 |  | JE24028548 | 654A STATE HIGHWAY 3 KAI IWI WANGANUI | Western | MISSION RD | 2024-08-29 | 9:30 | 2024-08-29 | 11:45 | 0.0029863 | 2.2072e-05 | 8 | 1082 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Defected 11KV X-Arm on pole 782838 | .
3072 |  | JE24029692 | 20 KEILLER PLACE FITZHERBERT PALMERSTON NORTH | Western | RUAPEHU DR | 2024-08-29 | 8:50 | 2024-08-29 | 16:24 | 0.23792 | 0.00054627 | 198 | 86235 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | INSTALLATION OF NEW CFC SWITCHGEAR10929 AT 20 KEILLER PLACE WITH 11KV CABLE JOINTS AND TERMINATIONS, REPLACE FAULTY TRANSFORMER T2/311 AND INSTALL 11KV LIGHTNING ARRESTERS AT POLE P44462 | .
3073 |  | JE24030110 | Tatua Substation, Tatua Dariy Factory, SH26 Tatuanui | Eastern | TATUA 33kV | 2024-08-29 | 8:16 | 2024-08-29 | 15:12 | 0.0022933 | 5.5179e-06 | 2 | 831 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Tatua Enabling Works Relocate 11kV Cable to TTU CB2 and 400V Cable from LST to ACDB in TTU yard Transformers TP561 & TP2844 both associated with Tatua | .
3074 |  | JE24030901 | 42 LORNE STREET MORRINSVILLE MORRINSVILLE | Eastern | LORNE ST | 2024-08-29 | 0:43 | 2024-08-29 | 1:27 | 0.00073276 | 1.6554e-05 | 6 | 266 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Checked phasing at Sw/Gear 13596/4 - not ok after completing NAPA 114080. Additional switching carried out to fix the phasing. Unplanned outage to customers on tx TC6047 - Additional outage for NAPA 114080 | .
3075 |  | JE24030905 | PARK RD | Western | PARK RD | 2024-08-29 | 5:28 | 2024-08-29 | 6:18 | 0.0098531 | 0.00019589 | 71 | 3571 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Floating Conductor at Pole 848276, repaired | .
3076 |  | JE24030946 | TAIRUA NORTH | Eastern | TAIRUA NORTH | 2024-08-29 | 11:07 | 2024-08-29 | 11:56 | 0.019589 | 0.00039453 | 143 | 7100 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: 11kV Sw/Gear 13340/3 & ABS 356 & ABS IP716 CAUSE: Deterioration Location: Pole 264015 Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Calm Follow up required (select advisory)? No Additional fault restoration comments: 2 Broken binders on the 11kV O/H Lines at Pole 264015 Fault was repaired and full Power restored at 11:56 | .
3077 |  | JE24030958 | TE KIRI | Western | TE KIRI | 2024-08-29 | 10:03 | 2024-08-29 | 12:35 | 0.018432 | 0.00012139 | 44 | 6681 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV DTX T7165 Pole 716007 Protection flags (nil where none): nil CAUSE: Lead out of Failed D/Outs Location: DTX T7165 Pole 716007 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Wind Rain LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Lead out of d/Outs, Old D/Outs replaced as well SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3078 |  | JE24030965 | REVANS ST | Western | REVANS ST | 2024-08-29 | 12:45 | 2024-08-29 | 13:30 | 0.00049845 | 1.1036e-05 | 4 | 181 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Broken Jumper at Fuses 7262 Isolated at Fuses 7262 Jumper repaired, Full power restored | .
3079 |  | JE24030991 | HUKANUI | Western | HUKANUI | 2024-08-29 | 9:00 | 2024-08-29 | 11:10 | 0.0093627 | 7.1733e-05 | 26 | 3394 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: S11 No. Fuses: 2 Fuse Amp Size:15A TIME CLOSED: 11:10 Cause: Weather Weather (wind/rain): windy raining Follow up required (select advisory)? | .
3080 |  | JE24031024 | CHURCH ST | Western | CHURCH ST | 2024-08-29 | 12:37 | 2024-08-29 | 14:09 | 0.00076129 | 8.2769e-06 | 3 | 276 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: 7645 No. Fuses: 2 Fuse Amp Size:6A TIME CLOSED: 14:08 Cause: Line clash Weather Weather (wind/rain): wind rain Follow up required (select advisory)? | .
3081 |  | JE24031041 | LANGDALE | Western | LANGDALE | 2024-08-29 | 13:15 | 2024-08-29 | 16:39 | 0.0078955 | 3.8625e-05 | 14 | 2862 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: 7889 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 16:38 Cause: Weather / Line clash Weather (wind/rain): wind, rain Follow up required (select advisory)?n Line patrolled | .
3082 |  | JE24031048 | BELVEDERE | Western | BELVEDERE | 2024-08-29 | 13:31 | 2024-08-29 | 15:53 | 0.019926 | 0.00014071 | 51 | 7222 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | Please check JE24031052 & JE24031053 & JE24031056 on completion. JE24031057 is not on the same feeder but it is close by. Maybe call customer when Power is restored to check they are part of this Job Fuses Location: 7570 No. Fuses: 3 Fuse Amp Size: 10 TIME CLOSED: 15:52 Cause: Brach on line at pole 817686 Weather (wind/rain): wind, rain Follow up required (select advisory)?n Branch removed with hotstick | .
3083 |  | JE24031073 | WHAKAMARA | Western | WHAKAMARA | 2024-08-29 | 14:57 | 2024-08-29 | 16:00 | 0.016756 | 0.00033659 | 122 | 6073 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV ABS WH293 Centre Contacts Failed P/P Feeder Protection flags (nil where none): nil CAUSE: ABS WH293 Centre Contacts Failed Location: BS WH293 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): 2408015 Circuit patrolled and type: oper Weather (wind/rain): Wind Rain LFI (Y/N + Comments): Nil Follow up Required (select advisory)? Additional fault restoration comments: Orig thought it was ABS WH229 , But fault was ABS WH293 Centre Contacts Failed Isolation from CB2/ABS WH293 part of the feeder already off on linked related job | .
3084 |  | JE24031078 | MVILLE SOUTH | Eastern | MVILLE SOUTH | 2024-08-29 | 21:15 | 2024-08-29 | 23:28 | 0.087312 | 0.00067595 | 245 | 31647 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Faultman found 11kV cable at pole I1020 has come out of the cable clamp and was hanging on LV lines, line was isolated at ABS's IC588, 1189, IC1291, IC1280 & Sw/Gear's 13854/3 & 14245/1 to refasten the cable and put new cable braces and opossum guards. | .
3085 |  | JE24031088 | 7 NO. 9 ROAD, SPRINGDALE | Eastern | TE PUNINGA | 2024-08-29 | 18:52 | 2024-08-29 | 18:56 | 9.7483e-06 | 2.759e-06 | 1 | 4 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Customer complaining of high voltages blowing light bulbs all the time. Faultman found voltages at 240 volte's, Faultman tapped transformer down from Tap 3 to tap2 voltage 235v. | .
3086 |  | JE24031107 | RONGOKOKAKO | Western | RONGOKOKAKO | 2024-08-29 | 17:32 | 2024-08-29 | 19:45 | 0.00072951 | 5.5179e-06 | 2 | 264 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T8/367 No. Fuses: 2 Fuse Amp Size: 2 Amp TIME CLOSED: 19:44 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? N | .
3087 |  | JE24031109 | LANGDALE | Western | LANGDALE | 2024-08-29 | 19:50 | 2024-08-29 | 21:10 | 0.0031171 | 3.8625e-05 | 14 | 1130 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faultman found blown fuses at Fuses 7889, line was isolated and operational control handed to Faultman to locate fault. Floater Fault was found at pole 360416 due to broken binder. | .
3088 |  | JE24031110 | MAURICEVILLE | Western | MAURICEVILLE | 2024-08-29 | 17:39 | 2024-08-29 | 19:06 | 0.00048229 | 5.5179e-06 | 2 | 175 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T8/100 No. Fuses: 2 Fuse Amp Size: 2 Amp TIME CLOSED: 19:06 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? N | .
3089 |  | JE24031114 | TARATA | Western | TARATA | 2024-08-29 | 17:49 | 2024-08-30 | 10:00 | 0.016089 | 1.6554e-05 | 6 | 5832 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Transformer 2803T No. Fuses: 3 Fuse Amp Size: 3A TIME CLOSED: 10:00 Cause: Lightning Weather (wind/rain): Rain Follow up required (select advisory)? No | .
3090 |  | JE24031119 | JE24031119 | Western | PUNGAREHU | 2024-08-29 | 23:45 | 2024-08-30 | 12:06 | 0.0081768 | 1.1036e-05 | 4 | 2964 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: P2005 No. Fuses: 3 Fuse Amp Size: 3 TIME CLOSED: 12:05 Cause: lightning Weather (w/rain): l.ightning Follow up required (select advisory)? | .
3091 |  | JE24031120 | BAINESSE | Western | BAINESSE | 2024-08-29 | 17:57 | 2024-08-29 | 19:29 | 0.0010053 | 1.1036e-05 | 4 | 364 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: B52 No. Fuses: 2 Fuse Amp Size: 10 Amp TIME CLOSED: 19:28 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? N | .
3092 |  | JE24031121 | MANGAMAIRE | Western | MANGAMAIRE | 2024-08-29 | 17:58 | 2024-08-30 | 11:40 | 0.0058617 | 5.5179e-06 | 2 | 2125 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T8/286 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 11:40 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n | .
3093 |  | JE24031129 | KATERE 5 | Western | KATERE 5 | 2024-08-29 | 18:21 | 2024-08-29 | 20:29 | 0.0028283 | 2.2072e-05 | 8 | 1025 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 731 No. Fuses: 2 Fuse Amp Size: 3 Amp TIME CLOSED: 20:28 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? N | .
3094 |  | JE24031133 | WAITARA RD | Western | WAITARA RD | 2024-08-29 | 18:26 | 2024-08-29 | 22:47 | 0.0043199 | 1.6554e-05 | 6 | 1566 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 358 No. Fuses: 3 Fuse Amp Size: 3 Amp TIME CLOSED: 22:46 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? N | .
3095 |  | JE24031134 | TOKO | Western | TOKO | 2024-08-29 | 18:26 | 2024-08-29 | 20:36 | 0.008818 | 7.4492e-05 | 27 | 3196 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 4957 No. Fuses: 2 Fuse Amp Size: 15 Amp TIME CLOSED: 20:23 Cause: Lightning Weather (wind/rain): Follow up required (select advisory)? Fuses Location: 2567T No. Fuses: 1 Fuse Amp Size: 2 Amp TIME CLOSED: 20:35 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? N | .
3096 |  | JE24031135 | TIKORANGI | Western | TIKORANGI | 2024-08-29 | 18:28 | 2024-08-30 | 9:30 | 0.012451 | 1.3795e-05 | 5 | 4513 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 4091T No. Fuses: 2 Fuse Amp Size:2 TIME CLOSED: 09:30 Cause: Lightening Weather (wind/rain): Follow up required (select advisory)? | .
3097 |  | JE24031139 | TIKORANGI | Western | TIKORANGI | 2024-08-29 | 18:30 | 2024-08-30 | 11:03 | 0.0027394 | 2.759e-06 | 1 | 993 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: TX 5117T No. Fuses: 2 Fuse Amp Size:10 TIME CLOSED: 11:02 Cause: lightening Weather (wind/rain):lightening Follow up required (select advisory)?n | .
3098 |  | JE24031140 | TARATA | Western | TARATA | 2024-08-29 | 18:30 | 2024-08-30 | 9:47 | 0.012653 | 1.3795e-05 | 5 | 4586 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Transformer 2341T No. Fuses: 3 Fuse Amp Size: 3A TIME CLOSED: 09:40 Cause: Lightning Weather (wind/rain): Rain Follow up required (select advisory)? No | .
3099 |  | JE24031143 | RONGOKOKAKO | Western | RONGOKOKAKO | 2024-08-29 | 18:32 | 2024-08-30 | 9:41 | 0.0025075 | 2.759e-06 | 1 | 909 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T8/366 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 09:40 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? Could not create job opening links | .
3100 |  | JE24031144 | MAURICEVILLE | Western | MAURICEVILLE | 2024-08-29 | 18:33 | 2024-08-29 | 20:56 | 0.00078665 | 5.5179e-06 | 2 | 285 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T8/63 No. Fuses: 2 Fuse Amp Size: 2 Amp TIME CLOSED: 20:55 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? N | .
3101 |  | JE24031145 | TIKORANGI | Western | TIKORANGI | 2024-08-29 | 18:37 | 2024-08-30 | 0:10 | 0.0018413 | 5.5179e-06 | 2 | 667 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 3093T No. Fuses: 2 Fuse Amp Size: 3 Amp TIME CLOSED: 00:10 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? N | .
3102 |  | JE24031152 | PARIHAKA | Western | PARIHAKA | 2024-08-29 | 18:46 | 2024-08-30 | 9:39 | 0.0049255 | 5.5179e-06 | 2 | 1785 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 6518 No. Fuses: 2 Fuse Amp Si8ze: TIME CLOSED:09:39 Cause: Lightening Weather (wind/rain): Follow up required (select advisory)? Not TX logged to wrong ICP | .
3103 |  | JE24031153 | WAITOTARA | Western | WAITOTARA | 2024-08-29 | 18:48 | 2024-08-29 | 21:16 | 0.0081328 | 5.5179e-05 | 20 | 2948 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 2732 No. Fuses: 2 Fuse Amp Size: 20 Amp TIME CLOSED: 21:15 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? N | .
3104 |  | JE24031157 | IHURAUA | Western | IHURAUA | 2024-08-29 | 18:56 | 2024-08-29 | 21:11 | 0.00074382 | 5.5179e-06 | 2 | 270 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T9/322 No. Fuses: 2 Fuse Amp Size: 2 Amp TIME CLOSED: 21:10 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? N | .
3105 |  | JE24031167 | SOUTH RD NGARIKI | Western | SOUTH RD NGARIKI | 2024-08-29 | 22:22 | 2024-08-30 | 11:59 | 0.0067697 | 8.2769e-06 | 3 | 2454 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses at transformer N3305 Blown Transformer faulty, Fuses ORT Transformer to be replaced tomorrow Dairy Shed Disconnected Meter Board Failed with Lightning Dis A42733 Transformer N3305 replaced | .
3106 |  | JE24031168 | MAIN RD MOTONUI | Western | MAIN RD MOTONUI | 2024-08-29 | 19:21 | 2024-08-29 | 22:21 | 0.00099674 | 5.5179e-06 | 2 | 361 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 2695T No. Fuses: 2 Fuse Amp Size: 2 Amp TIME CLOSED: 22:21 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? N | .
3107 |  | JE24031174 | RAETIHI | Western | RAETIHI | 2024-08-29 | 19:30 | 2024-08-29 | 21:26 | 0.00095768 | 8.2769e-06 | 3 | 347 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: X4070 No. Fuses: 2 Fuse Amp Size: 2 Amp TIME CLOSED: 21:25 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? N | .
3108 |  | JE24031182 | 91 FALLOON SETTLEMENT ROAD, MASTERTON, 5888 | Western | MOUNT BRUCE | 2024-08-29 | 20:41 | 2024-08-30 | 9:58 | 0.0022005 | 2.759e-06 | 1 | 798 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: T2905 CAUSE: Lightning Strike Temp generation (stage details when used): n PERFORMANCE DETAIL DNO (number or state no): n Circuit patrolled & type: n Weather (wind/rain): rain & lightning Follow up required (select advisory)? Additional fault restoration comments: Transformer T2905 isolated, Crew will return in morning to replace Tfr T2905 30/08/24 - TFR T2905 Replaced, Full power restored | .
3109 |  | JE24031185 | MOUNT BRUCE | Western | MOUNT BRUCE | 2024-08-29 | 19:45 | 2024-08-29 | 21:12 | 0.00048171 | 5.5179e-06 | 2 | 175 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T1543 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 21:12 Cause: Lightning Weather (wind/rain): rain & lightning Follow up required (select advisory)?n | .
3110 |  | JE24031186 | TAVERNER ST | Western | TAVERNER ST | 2024-08-29 | 19:47 | 2024-08-29 | 22:10 | 0.0015864 | 1.1036e-05 | 4 | 575 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Fuses 7536 & T2825 No. Fuses: 2 & 2 Fuse Amp Size: 6 & 3 TIME CLOSED: 22:10 Cause: Lightning Weather (wind/rain): Rain & lightning Follow up required (select advisory)? | .
3111 |  | JE24031189 | TAVERNER ST | Western | TAVERNER ST | 2024-08-29 | 19:53 | 2024-08-29 | 21:21 | 0.0014694 | 1.6554e-05 | 6 | 533 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T2759 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 21:21 Cause: Lightning Weather (wind/rain): rain & lightning Follow up required (select advisory)?n | .
3112 |  | JE24031194 | MAURICEVILLE | Western | MAURICEVILLE | 2024-08-29 | 20:04 | 2024-08-29 | 20:18 | 7.663e-05 | 5.5179e-06 | 2 | 28 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T8/57 No. Fuses: 3 Fuse Amp Size: 2 Amp TIME CLOSED: 20:18 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? N | .
3113 |  | JE24031196 | CHESTER RD | Western | CHESTER RD | 2024-08-29 | 20:19 | 2024-08-29 | 23:41 | 0.0050073 | 2.4831e-05 | 9 | 1815 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 7659 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 23:40 Cause: Lightning Weather (wind/rain): Rain & lightning Follow up required (select advisory)? | .
3114 |  | JE24031202 | MOUNT BRUCE | Western | MOUNT BRUCE | 2024-08-29 | 20:33 | 2024-08-29 | 22:58 | 0.0011976 | 8.2769e-06 | 3 | 434 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 7722 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 22:57 Cause: Lightning Weather (wind/rain): Rain & Lightning Follow up required (select advisory)? | .
3115 |  | JE24031205 | MOUNT BRUCE | Western | MOUNT BRUCE | 2024-08-29 | 20:38 | 2024-08-29 | 23:00 | 0.0011753 | 8.2769e-06 | 3 | 426 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T3403 No. Fuses: 2 Fuse Amp Size: 2 TIME CLOSED: 23:00 Cause: Lightning Weather (wind/rain): Rain & Lightning Follow up required (select advisory)? | .
3116 |  | JE24031210 | TAVERNER ST | Western | TAVERNER ST | 2024-08-29 | 21:01 | 2024-08-29 | 22:21 | 0.0013316 | 1.6554e-05 | 6 | 483 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T1876 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 22:20 Cause: Lightning Weather (wind/rain): Rain & lightning Follow up required (select advisory)? | .
3117 |  | JE24031222 | BAINESSE | Western | BAINESSE | 2024-08-29 | 21:25 | 2024-08-30 | 0:20 | 0.0058757 | 3.5867e-05 | 13 | 2130 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: B50 No. Fuses: 2 Fuse Amp Size: 10 Amp TIME CLOSED: 00:07 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? N Fuses Location: T2/381 No. Fuses: 1 Fuse Amp Size: 3 Amp TIME CLOSED: 00:20 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? N | .
3118 |  | JE24031230 | RAETIHI | Western | RAETIHI | 2024-08-29 | 22:23 | 2024-08-30 | 10:16 | 0.0077796 | 1.1036e-05 | 4 | 2820 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: X1697 No. Fuses: 2 Fuse Amp Size:2 TIME CLOSED: 10:15 Cause: Ligtening Weather (wind/rain):lightening Follow up required (select advisory)?Lightening | .
3119 |  | JE24031303 | WAITARA RD | Western | WAITARA RD | 2024-08-29 | 23:10 | 2024-08-30 | 11:44 | 0.0273 | 0.00013243 | 48 | 9895 | Unplanned | LIGHTNING - LIGHTNING STRIKE | 29/08/24 Transformer 1540 found to be faulty, Isolated at transformer fuses 23:10 30/08/24 Isolated at ABS 305 to replace 1540 transformer fuses. Replaced 3 x D/Outs FM to return in morning. Restored 30/08/24 11:43 | .
3120 |  | JE24031305 | MOUNT BRUCE | Western | MOUNT BRUCE | 2024-08-29 | 19:39 | 2024-08-30 | 9:16 | 0.0090111 | 1.1036e-05 | 4 | 3266 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T662 No. Fuses: 3 Fuse Amp Size: 3 TIME CLOSED: 09:15 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n | .
3121 |  | JE24027764 | 42 LORNE STREET MORRINSVILLE MORRINSVILLE | Eastern | LORNE ST | 2024-08-28 | 20:30 | 2024-08-29 | 0:34 | 0.0040291 | 1.6554e-05 | 6 | 1460 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | CONNECT NEW 11KV CABLE BETWEEN 13596/4 AND FC2702 LIVEN AND TEST (PHASING) - (To Remove DNO 2404003) | .
3122 |  | JE24027779 | 47 OHAWE ROAD TOKAORA HAWERA | Western | KETEMARAE RD | 2024-08-28 | 9:16 | 2024-08-28 | 15:11 | 0.1323 | 0.00037246 | 135 | 47954 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 1. 11kV Reconductor â€“ Replace conductor between 846037 â€“ 840266 and install SVDS (200M 4 Span ) 2. 11kV Reconductor â€“ Replace conductor between 846045 â€“ 846052 and install SVDS (205M 6 Span ) | .
3123 |  | JE24027880 | 14 MATAVAI STREET MOUNT MAUNGANUI TAURANGA | Eastern | MOUNT | 2024-08-28 | 9:00 | 2024-08-28 | 16:30 | 0.20928 | 0.00047454 | 172 | 75855 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Disconnect cable at SD5 083,9588/3, SD5-061 & at TD5-128. Test cable for these two circuits. Cut cable from SD5 083 ,swing & terminate to 14926/3. Cut cable from 9588/3 and joint to 14926/1 . Connect cable from 14926/2 to 14930/3 Connect TD5-128 to new 35mm cable & terminate at 14930/4. Transfer TD5-145 to 9588/4 . Connect new cable from 14930/2 to TD5-127 . At TD5 -094 disconnect cable towards TD5-127. Liven 14926/14930 , phasing check across 14926 | .
3124 |  | JE24027891 | 133R PEMBROKE ROAD, CARDIFF | Western | CARDIFF RD | 2024-08-28 | 9:41 | 2024-08-28 | 15:15 | 0.19231 | 0.00057662 | 209 | 69703 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove ABS 5665 and replace HV/LV arms, install new entec switch 12717/2, links /4. Used as Open Point. | .
3125 |  | JE24027908 | 1956 Williamson Road West, Waituna | Western | WAITUNA | 2024-08-28 | 9:48 | 2024-08-28 | 14:06 | 0.0242 | 9.3805e-05 | 34 | 8771 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11KV pole P07932 replace ABS K27 with new Tavrida new links & ABS & vt 28/08/2024 New ABS 10896/1 Installed. Links and Recloser still to be installed | .
3126 |  | JE24028003 | 715 MURIMOTU ROAD HUNTERVILLE HUNTERVILLE | Western | HUNTERVILLE 22KV | 2024-08-28 | 10:00 | 2024-08-28 | 13:08 | 0.0088255 | 4.6902e-05 | 17 | 3199 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Defected 11KV Pole & X-Arm 806831 | .
3127 |  | JE24028007 | 50 COOK STREET PALMERSTON NORTH PALMERSTON NORTH | Western | PASCAL ST 4 | 2024-08-28 | 23:16 | 2024-08-29 | 3:16 | 0.015528 | 0.0001076 | 39 | 5628 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | AP01-Perform magnefix maintenance at G133 & G236. AP02-Perform magnefix maintenance at G149 | .
3128 |  | JE24028033 | 7245 STATE HIGHWAY 4 TOHUNGA JUNCTION RAETIHI | Western | RAETIHI | 2024-08-28 | 9:31 | 2024-08-28 | 12:59 | 0.0028721 | 1.3795e-05 | 5 | 1041 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Running new LV conductor next to TX X4048 HV bushings. | .
3129 |  | JE24028210 | 42 CENTRAL ROAD SOUTH NGATEA THAMES | Eastern | MANGATARATA | 2024-08-28 | 9:29 | 2024-08-28 | 13:13 | 0.0012396 | 5.5179e-06 | 2 | 449 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE 11KV XARMS BEYOND FUSES FC768 & STRAIGHTEN POLE O3269 | .
3130 |  | JE24028238 | 14 BETHLEHEM ROAD BETHLEHEM TAURANGA | Eastern | WESTMORELAND | 2024-08-28 | 23:31 | 2024-08-29 | 2:43 | 0.03134 | 0.00016278 | 59 | 11359 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - IP392-FP468-IP395 | .
3131 |  | JE24028262 | 407 PLYMOUTH ROAD KORU NEW PLYMOUTH | Western | PIONEER RD | 2024-08-28 | 8:53 | 2024-08-28 | 14:57 | 0.049179 | 0.00014347 | 52 | 17825 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 755165,755168,755170,840660,755172,755173,755175,755177,755178,755179. | .
3132 |  | JE24030724 | PAPANUI ST | Eastern | PAPANUI ST | 2024-08-28 | 5:15 | 2024-08-28 | 6:34 | 0.0010858 | 1.3795e-05 | 5 | 394 | Unplanned | WILDLIFE - BIRD | Fuses Location: FC1441 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 06:34 Cause: Duck Strike Weather (wind/rain): Wind Rain Follow up required (select advisory)? | .
3133 |  | JE24030728 | OHAKEA | Western | OHAKEA | 2024-08-28 | 9:22 | 2024-08-28 | 10:30 | 0.0056131 | 8.2769e-05 | 30 | 2035 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Blown Jumper found at Transformer T1/34 Isolated at ABS's L44, L42, & L43 Back feed installed Jumper Repaired FM to defect cross arm at Pole P27162 | .
3134 |  | JE24030730 | KAKARIKI | Western | KAKARIKI | 2024-08-28 | 7:03 | 2024-08-28 | 9:04 | 0.0026706 | 2.2072e-05 | 8 | 968 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: M36 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 09:04 Cause: Faulty Cable Weather; Drizzly Address of Blown cable at T3/447 Copper /AL Transition join replaced . FM does not believe that was the reason the M36 Fuses Blew . 2R Required unknown cause for ddo Deterioration for Blown cable | .
3135 |  | JE24030744 | TAWHITI RD | Western | TAWHITI RD | 2024-08-28 | 8:17 | 2024-08-28 | 9:33 | 0.017003 | 0.00022348 | 81 | 6163 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Pole 357262 Ampac Connection Failed onto 11kV Cable. Replaced with Parallel Groove Clamp. Protection flags (nil where none): CAUSE: Ampac Connection Failed Location: Pole 357262 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Wind Rain LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3136 |  | JE24030779 | PONATAHI | Western | PONATAHI | 2024-08-28 | 14:19 | 2024-08-28 | 18:53 | 0.004998 | 4.9661e-05 | 18 | 1812 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 28/08/2024 FM advised pole 819317 does required replacement. Trying to find a digger to be able to access site. Isolated at ABS S519, Fuses 11493 installed at Pole 819311 Fuses used as Isolation for pole replacement Pole replaced, full power restored 18:53 | .
3137 |  | JE24030795 | RAETIHI | Western | RAETIHI | 2024-08-28 | 10:26 | 2024-08-28 | 11:15 | 0.022069 | 0.00045247 | 164 | 7999 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV DTX X4064 Tree against lines cut away Protection flags (nil where none): B, O/C E/F CAUSE: DTX X4064 Tree against lines Location: DTX X4064 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Curse Weather (wind/rain): Wind Rain LFI (Y/N + Comments): nil Follow up Required (select advisory)? Additional fault restoration comments: HLT on Recloser at the time ( Sensitive ) SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): Fault occured while NAPA 111880 taking place | .
3138 |  | JE24030803 | NGATEA | Eastern | NGATEA | 2024-08-28 | 10:57 | 2024-08-28 | 16:26 | 0.15518 | 0.0012802 | 464 | 56245 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV KPE CB6 Protection flags (nil where none): A & C Ø E/F & O/C CAUSE: HV Cable fault Location: Between Sw/Gear 13536/1 towards TX TC2259 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes, Cursory Patrol. Weather (wind/rain): Light rain and wind. LFI (Y/N + Comments): Yes, at Sw/Gear 13536/1 & /4 Follow up Required (select advisory)? Yes Additional fault restoration comments: Field Switcher is busy with a Line Patrol from KPE S/S Section from KPE S/S CB6 towards ABS IC2134 - Power ON at 11:42 Section from ABS IC2134 towards ABS 471 - Power ON at 11:55 Section from ABS 471 towards ABS 472 - Power ON at 12:15 Section from ABS 472 down River Rd towards ABS 486 & Check if LFI's at Sw/Gear 13536/4 have operated. - Confirmed LFI's did operate. Power restored from ABS 472 to Sw/Gear 13536/1 at 12:49 Isolated at the remote end of HV Cable at Sw/Gear 13120/3 Back feed was then put in place via KPE7 using ABS 441 closed at 13:04 Suspected a HV Cable fault between Sw/Gear 13536/1 and Sw/Gear 13120/3 AP was taken to disconnect the Cable and carry out testing. After testing was carried out under Test Permit it was found that the HV Cable has faulted between Sw/Gear 13536/1 towards TX TC2259 C | .
3139 |  | JE24030843 | MAUNGAKAWA ROAD | Eastern | MAUNGAKAWA ROAD | 2024-08-28 | 16:50 | 2024-08-28 | 16:55 | 6.4376e-05 | 1.3795e-05 | 5 | 23 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: Incorrect Tap Position Loop tests completed: Yes Test results: O.3 Ohms Voltage at TX: 249V before and after was 240V Voltage at house: 240V Have all connections been checked? Yes PQI Ref #: No Additional Info: Meter installer reported High Voltage Isolation: TX TC1214 Fuses Time OFF: 16:50 Time ON: 16:55 Action: Tapped Transformer down from Tap 4 to Tap 3 | .
3140 |  | JE24030863 | MOAWHANGO | Western | MOAWHANGO | 2024-08-28 | 17:40 | 2024-08-29 | 12:48 | 0.012673 | 1.1036e-05 | 4 | 4593 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation from Fuses 1290 - off overnight due to rough country with no visibility. Pole 787202 11kV Floater Retied. Flounder Conductor . | .
3141 |  | JE24030870 | KAIMAI DRIVE | Eastern | KAIMAI DRIVE | 2024-08-28 | 16:21 | 2024-08-28 | 17:42 | 0.00044746 | 5.5179e-06 | 2 | 162 | Unplanned | WILDLIFE - BIRD | Fuses Location: SD3-181 No. Fuses: 2 Fuse Amp Size: 10 Amp TIME CLOSED: 17;42 Cause: Bird strike Weather (wind/rain): Calm Follow up required (select advisory)? No | .
3142 |  | JE24030878 | COONOOR | Western | COONOOR | 2024-08-28 | 18:08 | 2024-08-29 | 9:21 | 0.15789 | 0.00062077 | 225 | 57228 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Recloser T21 Protection flags (nil where none): B, C Ph O/C, E/F CAUSE: Blown Jumpers Location: at TFR's T7/312 & T7/307 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): wind, rain LFI (Y/N + Comments): n Follow up Required (select advisory)? Additional fault restoration comments: returning in Morning as cnt get to some poles need bike and its to dark Line patrolled in day light hours, Blown Jumpers found at TFR's T7/312 & T7/307 to main line Isolated at Fuses T25 (Replaced 3 x 20A Fuses) Replaced 2 x DDO's and Repaired Jumper at TFR T7/312 & Replaced 1 x DDO and Repaired Jumper at TFR T7/307 Full power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3143 |  | JE24027741 | 81 SCARBOROUGH ROAD PAHIATUA PAHIATUA | Western | MANGAMAIRE | 2024-08-27 | 9:33 | 2024-08-27 | 12:06 | 0.0012654 | 8.2769e-06 | 3 | 459 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace leaking TX T7/143 | .
3144 |  | JE24027778 | 201 BLACK ROAD PAENGAROA TE PUKE | Eastern | ROYDEN DOWNS RD | 2024-08-27 | 8:46 | 2024-08-27 | 14:25 | 0.057039 | 0.0001683 | 61 | 20674 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv overhead conductors with 3W Squirrel between poles 221721& 393453 & between poles 221725 & 221727. Isolation point @ ABS 14861. Issuer earths @pole 221720 (22171 side) | .
3145 |  | JE24027790 | WESTMORELAND | Eastern | WESTMORELAND | 2024-08-27 | 23:30 | 2024-08-28 | 3:05 | 0.018383 | 8.5528e-05 | 31 | 6663 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9299-1/2/3/4 | .
3146 |  | JE24028057 | 385 WHAKAHORO ROAD SPRINGDALE WAITOA | Eastern | TE PUNINGA | 2024-08-27 | 9:01 | 2024-08-27 | 13:20 | 0.01861 | 7.1733e-05 | 26 | 6745 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV Pole K13571 with new pole and new ABS 581. | .
3147 |  | JE24030518 | recloser_4240:2 | Western | MATAROA A | 2024-08-27 | 6:37 | 2024-08-27 | 9:12 | 0.024593 | 0.00018485 | 67 | 8914 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 4240 Protection flags (nil where none): A,B, O/C CAUSE: Unknown Sectionalised Nothing found Location: unknown Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: curse Weather (wind/rain): wind rain LFI (Y/N + Comments): nil Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3148 |  | JE24030537 | LINTON | Western | LINTON | 2024-08-27 | 9:13 | 2024-08-27 | 10:44 | 0.064897 | 0.0018485 | 670 | 23522 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 8 Protection flags (nil where none): A, C Ph O/C CAUSE: Branch on Lines Location: Pole P02937 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Windy, Raining LFI (Y/N + Comments): N Follow up Required (select advisory)? Additional fault restoration comments: Back feed installed via Recloser 10041 Isolated at ABS's H109, H123, & 10107 Branch cleared from lines SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): Tree in Lines - Called in by Sam Hadley Jones - 0272383940 - camp rd | .
3149 |  | JE24030546 | PARAPARA | Western | PARAPARA | 2024-08-27 | 9:48 | 2024-08-27 | 11:18 | 0.00074639 | 8.2769e-06 | 3 | 271 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: X1917 No. Fuses: 2 Fuse Amp Size:2A TIME CLOSED: 11:18 Cause: Weather Weather (wind/rain): Raining windy Follow up required (select advisory)?NA | .
3150 |  | JE24030556 | SMITH ST | Eastern | SMITH ST | 2024-08-27 | 10:14 | 2024-08-27 | 19:10 | 0.83083 | 0.0074795 | 2058 | 301140 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 3 Protection flags (nil where none): O/C E/F CAUSE: Truck V Pole Location: Pole G0608 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F3, cursory patrolled either side of the accident scene Weather (wind/rain): Rain LFI (Y/N + Comments): Fitted no operation Follow up Required (select advisory)? No Additional fault restoration comments: Pole G0608 hit by refuse removal truck 1 x 11m pole replaced 1 x Double HV pin arm complete assembly 1 x Double LV pin arm complete assembly NDR to follow SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3151 |  | JE24030600 | pole_441634 - 588 LAKE FERRY ROAD, MARTINBOROUGH, 5781 | Western | DYERVILLE | 2024-08-27 | 13:42 | 2024-08-27 | 14:12 | 0.0061589 | 0.00020416 | 74 | 2232 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses for Transformer T1102 found floating. Isolated at Links 11132/6 & ABS S506 Fuses reattached | .
3152 |  | JE24030622 | CAMPBELL ST | Eastern | CAMPBELL ST | 2024-08-27 | 15:39 | 2024-08-27 | 18:01 | 0.0089833 | 6.3456e-05 | 23 | 3256 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Broken Cross arm Pole B0232, Guy wire dead end rusted out Loose put extra strain on Rotted HV arm resulting in breakage Protection flags (nil where none): nil CAUSE: Broken Cross arm Pole B0232, Guy wire dead end rusted out Loose put extra strain on Rotted HV arm resulting in breakage Location: Pole B0232 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Wind Rain LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Guy wire restrained also to fix issue SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3153 |  | JE24030628 | 559 HOMEWOOD ROAD, RIVERSDALE BEACH, MASTERTON, 5872 | Western | RIVERSDALE GEN | 2024-08-27 | 13:39 | 2024-08-27 | 15:30 | 0.00030634 | 2.759e-06 | 1 | 111 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Low Voltage - Electrician advises that there is a low voltage issue, at this ICP, pump won't run, 2 electric fences not working, said that voltage going through is 110 volts & should be 230 volts, thanks. Had to recreate JE24030605, no feeder rating was causing the crew requests to get stuck Please close JE24030605 with this job Fuses Location: 7143 No. Fuses: 2 Fuse Amp Size: 8 TIME CLOSED: 15:30 Cause: unknown Weather (wind/rain): Sunny slight wind Follow up required (select advisory)? | .
3154 |  | JE24030643 | MANGATOKI | Western | MANGATOKI | 2024-08-27 | 16:45 | 2024-08-27 | 17:30 | 0.0012484 | 2.759e-05 | 10 | 453 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV DTX 4235T Lead off top of D/Outs Protection flags (nil where none): CAUSE: DTX 4235T Lead off top of D/Out Location: DTX 4235T Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Wind Rain LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Replaced Lock on ABS 6151 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3155 |  | JE24030701 | PURIRI | Eastern | PURIRI | 2024-08-27 | 18:34 | 2024-08-27 | 19:46 | 0.0067574 | 9.3805e-05 | 34 | 2449 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: FP1792 No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 19:15 Cause: Unknown, lines patrolled Weather (wind/rain): Rain Follow up required (select advisory)? No Fuses Location: IC2583 No. Fuses: 2 Fuse Amp Size: 15A TIME CLOSED: 19:45 Cause: Unknown lines patrolled Weather (wind/rain): Rain Follow up required (select advisory)? No | .
3156 |  | JE24024213 | 4 REDWOOD LANE TAURIKO TAURANGA | Eastern | KAIMAI DRIVE | 2024-08-26 | 8:30 | 2024-08-26 | 16:24 | 0.062733 | 0.00013243 | 48 | 22738 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 1: Replace 11kV pole 211521 2: Remove 11kV Poles 211548 to 211523 3: Remove 11kV Conductor 211550 to 211521 4: Remove 11kV TX T4718 5: Remove 11kV TX TD3-084 6: Install SW/Gear 14907 7: Install 11kV TX TP4430 8: Install 11kV Cable between 14907/1 to pole 211521 9: Install 11kV Cable between 14907/2 to TP4430 10: Install 11kV Cable between 14907/3 to 14925/1 | .
3157 |  | JE24027613 | 125 MORIKAU ROAD RANANA WANGANUI | Western | RAETIHI | 2024-08-26 | 8:25 | 2024-08-26 | 13:06 | 0.058865 | 0.00020968 | 76 | 21336 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace digger pole structure 777515 / 777514. | .
3158 |  | JE24027630 | 109 KIRIHAU ROAD KORU NEW PLYMOUTH | Western | PIONEER RD | 2024-08-26 | 9:03 | 2024-08-26 | 14:10 | 0.014399 | 4.6902e-05 | 17 | 5219 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 755330,755331,755332,755333,755334,755336, cross arms 755335 and 755337 | .
3159 |  | JE24030373 | TAVERNER ST | Western | TAVERNER ST | 2024-08-26 | 7:26 | 2024-08-26 | 15:33 | 0.076081 | 0.000309 | 112 | 27576 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11KV Rec C409 Protection flags (nil where none): A Phase O/C E/F CAUSE: Truck Hit Pole Location: Pole 820290 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): no Circuit patrolled and type: Fault Called in Weather (wind/rain): Rain LFI (Y/N + Comments): no Follow up Required (select advisory)? Additional fault restoration comments:No Back feeds Isolated at ABS S317 Replaced 1 Pole complete with 1 X 15kva single phase transformer Repaired 2 Span of Over head Earth wire and replace transformer Earths | .
3160 |  | JE24030480 | TE MAUNGA 3102-PAPAMOA 62 33KV | Eastern | TE MAUNGA 3102-PAPAMOA 62 33KV | 2024-08-26 | 15:46 | 2024-08-26 | 16:37 | 0.47403 | 0.02927 | 9851 | 171816 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: PMA S/S 33/11kV Transformers T6 & T7 Protection flags (nil where none): 33kV CB 3622 & CB 3522 - BZ Trip RCV 11kV CB 36 & CB 37 - A B C Ø Ground Fault, DefT E/F LV2 Trip Flag, CB1, 5, 6 & 8 LOP Warning CAUSE: Under Investigation Location: PMA S/S Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: No Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? Yes Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): PMA S/S Circuit that tripped: PMA S/S 33/11kV Transformers T6 & T7 DTF (KM): N/A Approx. 15:45 NOC was busy with NAPA 111 815 returning TMA S/S T7 back to service after Tap Changer Servicing. Operation No: 34 NOC Closed TMA 33kV CB 3062 at 15:45 to energize Transformer T7 At PMA S/S Transformers T6 & T7 11/33kV CB's tripped at approx. 15:45 on the above protection flags. I knew the Field Switcher was very near and called him up to investigate the tripping at PMA S/S. Nothing abnormal was found on site and NOC suspected the tripping was related to the switching at TMA S/S. Field Switcher then reset all the protection flags at PMA S/S. NOC First energized Transformer's T6 & T7 to prove they were fault free a | .
3161 |  | JE24030322 | RIVERLEA | Western | RIVERLEA | 2024-08-25 | 0:23 | 2024-08-25 | 2:22 | 0.0055819 | 4.6902e-05 | 17 | 2023 | Unplanned | WILDLIFE - BIRD | Fuses Location: 5976 No. Fuses: 3 Fuse Amp Size: 15 TIME CLOSED: 02:22 Cause: bird strike Weather (wind/rain): calm Follow up required (select advisory)?n Line Patrolled 235kVA of TFR's past Fuses 5976, upgraded to 15A from 8A as 8A fuses are loaded in to Fuses 12481 so there was no discrimination (new 100kVA has been added and no protection review of fusing has been carried out CIW) | .
3162 |  | JE24030327 | WELCOME BAY | Eastern | WELCOME BAY | 2024-08-25 | 8:23 | 2024-08-25 | 12:02 | 0.21277 | 0.0043978 | 1594 | 77119 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 3 Protection flags (nil where none): E/F CAUSE: Line down Location: Pole 215263 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F3, cursory patrolled. Weather (wind/rain): Calm LFI (Y/N + Comments): Yes Follow up Required (select advisory)? No Additional fault restoration comments: Line broke midspan to Fuses SD4-224. 15m x Namu conductor 6 x FT sleeves SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3163 |  | JE24030331 | LANGDALE | Western | LANGDALE | 2024-08-25 | 10:40 | 2024-08-25 | 11:41 | 0.0023388 | 3.8625e-05 | 14 | 848 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: Fuses 7889 Protection flags (nil where none): Nil CAUSE: Floating Wire Location: Pole 360416 Temp generation (state details when used): NA PERFORMANCE DETAIL DNO (number or state No):NA Circuit patrolled and type: F5 Patrolled Weather (wind/rain): Fine LFI (Y/N + Comments): NA Follow up Required (select advisory)? Additional fault restoration comments: On Pole 360416 Floating Wire was rebound on one pin Relivened with 2x HV Fuses SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): NA Circuit that tripped: NA DTF (KM):NA | .
3164 |  | JE24030332 | TAWAHA | Western | TAWAHA | 2024-08-25 | 8:49 | 2024-08-25 | 10:40 | 0.0012236 | 1.1036e-05 | 4 | 443 | Unplanned | WILDLIFE - BIRD | Fuses Location: 8044 No. Fuses: 2 Fuse Amp Size:8A TIME CLOSED: 10:39 Cause: Bird Strike Weather (wind/rain): Fine Follow up required (select advisory)?NA | .
3165 |  | JE24030348 | BRUNSWICK | Western | BRUNSWICK | 2024-08-25 | 11:50 | 2024-08-25 | 13:18 | 0.00072751 | 8.2769e-06 | 3 | 264 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 2880 No. Fuses: 3 Fuse Amp Size: 6 TIME CLOSED: 13-18 Cause: Unknown Think Bird Weather (wind/rain): Fine Follow up required (select advisory)? | .
3166 |  | JE24030351 | NGARUA | Eastern | NGARUA | 2024-08-25 | 16:27 | 2024-08-25 | 16:32 | 7.9458e-05 | 1.6554e-05 | 6 | 29 | Unplanned | THIRD PARTY INTERFERENCE - VANDALISM/THEFT | REGULATORY INFORMATION Voltage & Device ID: 11kV ABS IP624 Protection flags (nil where none): Nil CAUSE: Vandalism Location: IP624 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: No Weather (wind/rain): Calm LFI (Y/N + Comments): Nil Follow up Required (select advisory)? No Additional fault restoration comments: ABS IP624 found to be open and the lock had been cut and put back. The ABS was closed and a new lock fitted. Full power to transformer TC1292 was restored. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3167 |  | JE24030361 | MAHOE | Western | MAHOE | 2024-08-25 | 18:00 | 2024-08-25 | 19:51 | 0.0073253 | 6.6215e-05 | 24 | 2655 | Unplanned | WILDLIFE - BIRD | Fuses Location: 6266 No. Fuses: 2 Fuse Amp Size: 20 TIME CLOSED: 19:50 Cause: Duck strike Weather (wind/rain): wind Follow up required (select advisory)?n | .
3168 |  | JE24030265 | BROOKLANDS 8 | Western | BROOKLANDS 8 | 2024-08-24 | 0:09 | 2024-08-24 | 1:11 | 0.0099751 | 0.00065387 | 195 | 3616 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 12238/2 Protection flags (nil where none): E/F, O/C A CAUSE: unknown Location: na Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): unknown LFI (Y/N + Comments): no Follow up Required (select advisory)? n Additional fault restoration comments: no fault in from Sw/Gear 12024/2 so opened and back feed put in place, line patrolled, no fault found, full power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3169 |  | JE24030269 | 422 STANLEY ROAD, TE POPO, STRATFORD, 4394 | Western | CLOTON RD SOUTH | 2024-08-24 | 7:38 | 2024-08-24 | 11:52 | 0.039644 | 0.00066215 | 120 | 14369 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Lines down Faultman found line down from pole 758295 to transformer 2631T - broken strain insulator.. Recloser 8763/2 was opened and Tfr 2631T isolated, Line re-livened. Fault crew returned and line was isolated at Fused ABS 5560 to repair lines down, pole 758295 was on a big hill with foot access only. | .
3170 |  | JE24030278 | MARTON | Western | MARTON | 2024-08-24 | 9:25 | 2024-08-24 | 13:37 | 0.001391 | 5.5179e-06 | 2 | 504 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: TFr 4037W CAUSE: Deuteriation -all rusted lid water in Tfr. Replaced tx X4037 Temp generation (stage details when used): n PERFORMANCE DETAIL DNO (number or state no): n Circuit patrolled & type: n/a Weather (wind/rain): wind Follow up required (select advisory)?n Additional fault restoration comments: | .
3171 |  | JE24030279 | BRUNSWICK | Western | BRUNSWICK | 2024-08-24 | 8:10 | 2024-08-24 | 9:42 | 0.00050929 | 5.5179e-06 | 2 | 185 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Y328 No. Fuses: 2 Fuse Amp Size: 2 TIME CLOSED: 09:42 Cause: Lightning Weather (wind/rain): rain Follow up required (select advisory)? | .
3172 |  | JE24027028 | 58 Matakokiri Drive, Tauriko, Tauranga | Eastern | WINTREBRE LANE | 2024-08-23 | 5:00 | 2024-08-23 | 7:05 | 0.0099746 | 8.001e-05 | 29 | 3615 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Protection relay maintenance testing. Need CB open as there will be no protection on that circuit. Do not need VT isolated. Do not need the CB earthed. | .
3173 |  | JE24027477 | 219 MANGAMAHU ROAD FORDELL WANGANUI | Western | FORDELL | 2024-08-23 | 9:36 | 2024-08-23 | 15:01 | 0.0062737 | 1.9313e-05 | 7 | 2274 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace X arms on pole 791530 Notes from SIS tx X587 was also replaced under this NAPA as it was found that the HV Bushings were cracked | .
3174 |  | JE24027490 | 169 STATE HIGHWAY 27 MANGATARATA THAMES | Eastern | MANGATARATA | 2024-08-23 | 8:30 | 2024-08-23 | 12:38 | 0.05131 | 0.00020692 | 75 | 18598 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV pole O13931 and ABS IC495. | .
3175 |  | JE24027510 | 2967 MOUNTAIN ROAD MIDHIRST STRATFORD | Western | CLOTON RD NORTH | 2024-08-23 | 9:18 | 2024-08-23 | 12:14 | 0.024861 | 0.00014071 | 51 | 9011 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re-sag and repair conductor at pole 761371 Re-sag line at pole 741543 completed during this planned outage Pole 741543 isolated at 11:04-11:43 | .
3176 |  | JE24027534 | 54 NIXS ROAD APITI KIMBOLTON | Western | APITI | 2024-08-23 | 8:30 | 2024-08-23 | 12:26 | 0.0032491 | 1.3795e-05 | 5 | 1178 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace crossarms between and including Pole P01725 and P05443. Reconductor LV from P05405 to P05443 | .
3177 |  | JE24028739 | 2017 PYES PA ROAD OROPI TAURANGA | Eastern | PYES PA | 2024-08-23 | 9:45 | 2024-08-23 | 15:43 | 0.040485 | 0.00011312 | 41 | 14674 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV overhead conductors between Poles 216968 & 217092 with 2W ferret. | .
3178 |  | JE24030065 | 818 THAMES COAST ROAD, THAMES | Eastern | MANAIA COROMANDEL | 2024-08-23 | 10:13 | 2024-08-23 | 10:59 | 0.033409 | 0.0007532 | 273 | 12109 | Unplanned | VEGETATION - OUTSIDE ZONE | Cause: large tree/ log fallen on stay-wire What was replaced? Where was it replaced (pole/TX/pillar box)? Pole Is 2R required? Y 2R Y - What is the timeframe for repairs? Tomorrow Additional Info: Too big for FM chainsaw, coming back tomorrow with something bigger to remove Remove tree stump at pole T1504 Isolate 11kv for safety | .
3179 |  | JE24030132 | TAWHITI RD | Western | TAWHITI RD | 2024-08-23 | 9:12 | 2024-08-23 | 12:51 | 0.0024171 | 1.1036e-05 | 4 | 876 | Unplanned | WILDLIFE - BIRD | Fuses Location: CA432 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 12:50 Cause: Duck Strike Weather (wind/rain): Windy Follow up required (select advisory)? | .
3180 |  | JE24030141 | FAIRWAY DR | Eastern | FAIRWAY DR | 2024-08-23 | 9:34 | 2024-08-23 | 11:06 | 0.00025387 | 2.759e-06 | 1 | 92 | Unplanned | OTHER | Part of NAPA 114201 , Sewer Pump but account is inactive Cleared with network access team - becs Change TX TP4397 from 200kVA to a 100KV - Non outage 23/08/2024 0930-1300 NAPA 114201 | .
3181 |  | JE24030195 | TUTURUMURI | Western | TUTURUMURI | 2024-08-23 | 13:29 | 2024-08-23 | 17:12 | 0.10908 | 0.00051869 | 188 | 39536 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11KV CB C642 Protection flags (nil where none): B & C ph O/C & E/F CAUSE: Lines Down - Suspect due to line clash Location: Poles 810459 & 810460 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: cursory Weather (wind/rain): windy LFI (Y/N + Comments): n Follow up Required (select advisory)? Additional fault restoration comments: Line was isolated at ABS 8094 to repair lines down. | .
3182 |  | JE24030253 | MANUTAHI | Western | MANUTAHI | 2024-08-23 | 23:18 | 2024-08-24 | 0:18 | 0.0013313 | 2.2072e-05 | 8 | 483 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Incorrect customer info, customer is off TFR W1240 NOT 5442E Barrel was burnt out, Tried a Reload/Re-Liven at TFR W1240 and the Bottom of the DDO broke off Isolated at Fuses WH183 3 x DDO's replaced to TFR W1240 (Pole 728165), Full power restored | .
3183 |  | JE24030259 | RAHOTU | Western | RAHOTU | 2024-08-23 | 22:35 | 2024-08-24 | 2:59 | 0.081505 | 0.00060973 | 221 | 29542 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB NG2 Protection flags (nil where none): E/F, O/C A CAUSE: Broken conductor, causing lines down Location: 711278 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): unknown LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Line patrolled, lines down found at Pole 711278, Isolated at ABS NG201 & NG479, conductor broke at the line guard, line repaired, full power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3184 |  | JE24032547 | JAMES LINE | Western | JAMES LINE | 2024-08-23 | 10:48 | 2024-08-23 | 14:45 | 0.10254 | 0.00043316 | 157 | 37165 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Faultman found that they were missing phases at transformer T6/655, line was isolated at Sw/Gear's 10226/4, 10795/1 and Magnefix 504 to replace HV fuses. When transformer was opened, they found that the fuses had melted, so transformer T6/655 was replaced with a temp transformer and a full set of Fuses (10912) were installed so that in future the transformer can be isolated from the main line as before it was hard wired. Finn Parker Added comment 28/08/24 09:16 check why Temp TX Finn Parker Added comment 29/08/24 15:26 Confirmed with David Thompson TX T6/655 was a 300kva. Downer had no spare 300kva and replaced with 500kva that is booked for another job. TX will have to be swapped out once faulty TX is repaired or a 300kva replacement can be sourced . TX is a old fibreglass cover type, if old TX cannot be repaired a new Mini pad 300kva TX we need to be installed which is the preferred option since there is now OH TX fuse installed. Ian Daniels to take over as residual fault with no set repair timeframe. 29/08/2024 - Added into Residual Faults - 111573. MDP | .
3185 |  | JE24024039 | 4 REDWOOD LANE TAURIKO TAURANGA | Eastern | GARGAN RD | 2024-08-22 | 8:31 | 2024-08-22 | 15:47 | 0.068174 | 0.00015726 | 57 | 24710 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 1: Remove conductor from 211529 to 211533 2: Remove 11kV TX TD3-085 3: Remove 11kV Fuses SD3-097 4: Remove 11kV TX TP2696 5: Remove 11kV Fuses SD3-025 6: Remove ABS IP722 7: Replace 11kV poles 211550, 211520 8: Replace 11kV XArm 211517 9: Liven new S/Gear 14910 & 14925 10: Install / Liven new 11kV TX TP4426 11: Joint new 11kV UG Cable from TD3-206 (Link Box) to S/W gear 14910/2 12: Joint new 11kV UG Cable from 14925/2 to pole 211550 | .
3186 |  | JE24027230 | 6 BLAGDON ROAD BLAGDON NEW PLYMOUTH | Western | OMATA RD | 2024-08-22 | 9:31 | 2024-08-22 | 15:20 | 0.13314 | 0.00038074 | 138 | 48256 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace spalling pole ABS 492 Pole 750615 | .
3187 |  | JE24027233 | 36 RICHARDSONS ROAD FORDELL WANGANUI | Western | MAKIRIKIRI | 2024-08-22 | 9:33 | 2024-08-22 | 13:48 | 0.07121 | 0.00027866 | 101 | 25811 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace X arms on poles 791856, 791868, 791848, 791496, 791600 | .
3188 |  | JE24027235 | 204 KIRIHAU ROAD KORU NEW PLYMOUTH | Western | PIONEER RD | 2024-08-22 | 9:01 | 2024-08-22 | 13:55 | 0.013824 | 4.6902e-05 | 17 | 5010 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 755329,755327,755326,755325,755324,755323,755322,755321,755320,755319. | .
3189 |  | JE24027273 | 790 MANAWARU ROAD MANAWARU TE AROHA | Eastern | MAUNGAKAWA ROAD | 2024-08-22 | 9:02 | 2024-08-22 | 13:26 | 0.067221 | 0.00025382 | 92 | 24365 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replacing 2 Poles and various xarms. Worksites Poles C12818, C12835, C12764, C12758, C12754, C12749 & C12750. | .
3190 |  | JE24027284 | 1927 TAIRUA WHITIANGA ROAD COROGLEN WHITIANGA | Eastern | TAIRUA NORTH | 2024-08-22 | 9:30 | 2024-08-22 | 15:28 | 0.09148 | 0.0002621 | 95 | 33157 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles W12725, W1753, W12702/W1739 & W1734/W12683. Install new pole 1 between poles W12719 & W12717 and new pole 2 between poles W12705 & 495954 | .
3191 |  | JE24027291 | 374 MAKOKOMIKO ROAD PUKEOKAHU TAIHAPE | Western | MOAWHANGO | 2024-08-22 | 10:23 | 2024-08-22 | 15:04 | 0.00388 | 1.3795e-05 | 5 | 1406 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Shut 8 Resag lines around poles 786519 & 361847. Trim Trees pole 786494. | .
3192 |  | JE24027293 | 442 KARERE ROAD TIAKITAHUNA PALMERSTON NORTH | Western | BAINESSE | 2024-08-22 | 8:30 | 2024-08-22 | 12:21 | 0.008266 | 3.5867e-05 | 13 | 2996 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Reconductor LV O/H between P31858-P43235. Replace 11kV crossarms P31869-P31865. Remove TEMP links 142. | .
3193 |  | JE24027416 | 47 OHAWE ROAD TOKAORA HAWERA | Western | KETEMARAE RD | 2024-08-22 | 8:30 | 2024-08-22 | 15:24 | 0.023464 | 0.00070629 | 135 | 8505 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Reconductor â€“ Replace conductor between 440032 â€“ 846037 (927M â€“ 17 Span) and install SVDS | .
3194 |  | JE24027436 | 5 PYE PLACE HOT WATER BEACH WHITIANGA | Eastern | TAIRUA NORTH | 2024-08-22 | 9:17 | 2024-08-22 | 16:30 | 0.10049 | 0.00024279 | 88 | 36422 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace existing SDAF3+SDAF+SDAF switchgear 9199 with two Safelink CFCF units 14928 and 14936. Existing drop-out fuses FC2715 to fitted with Solid links and allocated new equipment number 14891. Upgrade TP104 with 200kVA GMT. Fuse FP1093 upgraded to 20A. | .
3195 |  | JE24027445 | 318 PUTORINO ROAD HUNTERVILLE MARTON | Western | PUTORINO | 2024-08-22 | 9:16 | 2024-08-22 | 14:31 | 0.0017414 | 5.5179e-06 | 2 | 631 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Gain AP to replace 3 x Red Tag Poles 805861,805863, 805864 with new 11m Busck poles | .
3196 |  | JE24027634 | 39 BLACK ROAD PAENGAROA TE PUKE | Eastern | ROYDEN DOWNS RD | 2024-08-22 | 9:30 | 2024-08-22 | 14:30 | 0.047212 | 0.00015726 | 57 | 17112 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv/400vt poles,221702,221705,221706,385944. Replace 11kv/400vt cross arms @ pole 221704. lsolation point ABS #14861, issuer earths @ pole 221702(221700 side) | .
3197 |  | JE24029934 | WAIONE | Western | WAIONE | 2024-08-22 | 10:17 | 2024-08-22 | 12:14 | 0.0016154 | 1.3795e-05 | 5 | 586 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: Deterioration What was replaced? OH line to be sagged Where was it replaced (pole/TX/pillar box)? Pole Is 2R required? y 2R Y - What is the timeframe for repairs? tomorrow morning Additional Info: LV left off on one Phase customers advised and happy for the night faultman has contacted affected Customers to confirm ok to turn power off De-energies TFR T9/77 to Pull up / Repair LV conductor at Pole P00080 safely (old TFR structure where LV lines are close to the top of the TFR) LV Lines repaired, full power restored to customer's | .
3198 |  | JE24029951 | KOPU | Eastern | KOPU | 2024-08-22 | 5:42 | 2024-08-22 | 14:51 | 0.10107 | 0.0011974 | 434 | 36634 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: CB 1 Protection flags (nil where none): Phase B OC CAUSE: Car v Pole Location: Pole S12455 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Pole replaced - 11kv restored, Faultman on site with Inspector for 11KV/400V Line clash Inspections SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3199 |  | JE24029994 | RATAPIKO | Western | RATAPIKO | 2024-08-22 | 11:21 | 2024-08-22 | 11:29 | 0.00010944 | 1.3795e-05 | 5 | 40 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Transformer 2446T operating at 252V-250V-250V-Neutral. Tap Setting Tap 4. Lowered to Tap 3 & retested. 243V-242V-242V-Neutral at Txfmr (No Load) Loop Impedance Tests carried out. All ok. | .
3200 |  | JE24030000 | MANGATOKI | Western | MANGATOKI | 2024-08-22 | 13:15 | 2024-08-22 | 14:57 | 0.00028123 | 2.759e-06 | 1 | 102 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: 4235T Fuses CAUSE: Unk Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: N/A Weather (wind/rain): Calm Follow up required (select advisory)? Additional fault restoration comments: Replaced Transformer 4235T with equivalent size. 15/11/3ph | .
3201 |  | JE24030027 | MOAWHANGO | Western | MOAWHANGO | 2024-08-22 | 9:16 | 2024-08-22 | 11:26 | 0.0017903 | 1.3795e-05 | 5 | 649 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Transformer X492 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 11:25 Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)? | .
3202 |  | JE24030042 | KUMENGA | Western | KUMENGA | 2024-08-22 | 13:08 | 2024-08-22 | 15:38 | 0.00041419 | 2.759e-06 | 1 | 150 | Unplanned | WILDLIFE - BIRD | Fuses Location: T3813 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 15:38 Cause: Bird strike Weather (wind/rain): calm Follow up required (select advisory)?n | .
3203 |  | JE24030063 | BURNSIDE | Western | BURNSIDE | 2024-08-22 | 14:58 | 2024-08-22 | 16:30 | 0.00076451 | 8.2769e-06 | 3 | 277 | Unplanned | WILDLIFE - BIRD | Incorrect Job Location Fuses Location: 7440 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 16:30 Cause: Bird Strike Weather (wind/rain): Closing in currently Follow up required (select advisory)? NA | .
3204 |  | JE24030067 | HIKUAI | Eastern | HIKUAI | 2024-08-22 | 15:17 | 2024-08-22 | 15:18 | 0.00090862 | 0.00083872 | 304 | 329 | Unplanned | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | Voltage & Device ID: REC 9643 Protection flags (nil where none): None Weather (wind/rain): Windy Follow up required (select advisory): No LFI Activation: N | .
3205 |  | JE24030074 | OPOUTERE | Eastern | OPOUTERE | 2024-08-22 | 16:24 | 2024-08-22 | 18:02 | 0.029313 | 0.00040005 | 145 | 10625 | Unplanned | ADVERSE ENVIRONMENT - FIRE | Fire comms Requested Crew to Shut off OH lines at the intersection of wehitapaua Lane & Ohui Rd. Fire was said to be getting out of Control . Feeeder Droppped at SEC_13403 ETA advised 45min - Fire comms was also advised Recloser 13403 OPENED - 16:23 ABS 287 Opened 1726.Recloser 13403 Closed 17 :28.Abs left opened until Fire has been cleared by Fire services so that power can be restored ABS 287 CLOSED AFTER FIRE HAD BEEN EXTINGUISHED | .
3206 |  | JE24030083 | 384 PALMER ROAD, KAPUNI, HAWERA, 4679 | Western | PALMER RD | 2024-08-22 | 19:45 | 2024-08-22 | 20:19 | 0.005235 | 0.0001545 | 56 | 1897 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Arm Brace bolt missing from HV crossarm. Crossarm on lean. Please Check for safety Cross arm Twisted at Pole 731635 Isolated at ABS 12263 & Links 6069/4 Cross arm repaired | .
3207 |  | JE24027054 | 47 OHAWE ROAD TOKAORA HAWERA | Western | KETEMARAE RD | 2024-08-21 | 8:31 | 2024-08-21 | 15:30 | 0.023153 | 0.00036418 | 73 | 8392 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 11kv Reconductor â€“ Replace conductor between 721916 â€“ 440032 (1410M â€“ 22 Span) and install SVDS | .
3208 |  | JE24027091 | 2539 MOUNTAIN ROAD TARIKI INGLEWOOD | Western | CLOTON RD NORTH | 2024-08-21 | 9:00 | 2024-08-21 | 14:48 | 0.077721 | 0.00022348 | 81 | 28170 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 761144, resag lines at poles 761057, 761177, replace xarms at pole 761172 and resag | .
3209 |  | JE24027092 | 102 KEREPEHI TOWN ROAD KEREPEHI PAEROA | Eastern | KAIHERE | 2024-08-21 | 13:31 | 2024-08-21 | 13:47 | 0.0010159 | 6.3456e-05 | 23 | 368 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Kerepehi Substation - CB7 Connection of new feeder Connect Cable at Links 14732 ( KPE1 ) carry out phasing checks , close Links 14732 to liven cable up to CB7 . Leave CB7 open ready for final Network configuration at a later date . | .
3210 |  | JE24027093 | 2 BALMEDIE RIDGE BETHLEHEM TAURANGA | Eastern | SHERWOOD ST | 2024-08-21 | 8:35 | 2024-08-21 | 14:40 | 0.19619 | 0.000538 | 195 | 71110 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9152/1/2/3-4/5/6 | .
3211 |  | JE24027098 | 73 WIREMU ROAD, OPUNAKE | Western | IHAIA RD | 2024-08-21 | 9:16 | 2024-08-21 | 15:46 | 0.0053866 | 1.3795e-05 | 5 | 1952 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 715763 and xarms at multiple sites - 715758, 715767, 715737, 715764, 715728, 715745, 715753, 715739, 715741, 715765, 715746, 715761 | .
3212 |  | JE24027109 | 54 NIXS ROAD APITI KIMBOLTON | Western | APITI | 2024-08-21 | 8:46 | 2024-08-21 | 12:57 | 0.0034639 | 1.3795e-05 | 5 | 1256 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace crossarms between and including Pole P01725 and P05443. Replace Pole P05435/P05436 and TX T4/168 with a 30kVA TX (number to remain) | .
3213 |  | JE24027177 | 180 POLSON ROAD KAKATAHI WANGANUI | Western | FORDELL | 2024-08-21 | 9:01 | 2024-08-21 | 15:09 | 0.03556 | 9.6564e-05 | 35 | 12889 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace HV X arms on poles 791313 (two pole structure) 791315 (two pole structure) 791320 (TX pole) 791358 (TX pole) | .
3214 |  | JE24027209 | 135 MCBETH ROAD HIKUAI HIKUAI | Eastern | OPOUTERE | 2024-08-21 | 9:00 | 2024-08-21 | 16:10 | 0.037656 | 8.8287e-05 | 32 | 13649 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install fibre between pole 854119 & links LC4181 | .
3215 |  | JE24029676 | WAITOTARA | Western | WAITOTARA | 2024-08-21 | 13:01 | 2024-08-21 | 14:37 | 0.00026261 | 2.759e-06 | 1 | 95 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: Deterioration Steel bracket is broken What was replaced? TX X546 Where was it replaced (pole/TX/pillar box)? Pole 781544 Is 2R required? Y/N 2R Y - What is the timeframe for repairs? Additional Info: Full power to the house. This can not be done tonight as all teams are already working other sites Isolated at TFR X546 Fuses TFR Replaced, Full power restored | .
3216 |  | JE24029753 | LEEDSTOWN 22KV | Western | LEEDSTOWN 22KV | 2024-08-21 | 6:37 | 2024-08-21 | 8:19 | 0.001116 | 1.1036e-05 | 4 | 405 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses 532 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 08:18 Cause: Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? | .
3217 |  | JE24029754 | dtx_T2/394 | Western | LINTON | 2024-08-21 | 9:50 | 2024-08-21 | 9:59 | 0.00023819 | 2.759e-05 | 10 | 86 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 151 Hewitts Road, Palmerston North. Check for Safety - please Tap down Transformer, Complete voltage tests & carry out loop Impedance tests at Transformer & Customers Take off after tapping. Customer is getting Spikes of 248V at Night & 252 during the Day. The customer has solar . Please Take Voltage Test at supply TX & Property point of supply. This job relates to a PQI under JE24028579. De-energised at TFR T2/394 TFR T2/394 tapped down from tap 3 to tap 2, 238V, 241V, 240V, Data Loggers installed Leave 2R Open | .
3218 |  | JE24029755 | NO 3 LINE | Western | NO 3 LINE | 2024-08-21 | 6:57 | 2024-08-21 | 9:21 | 0.0023725 | 1.6554e-05 | 6 | 860 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: 4234 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 09:20 Cause: unknown Weather (wind/rain): calm Follow up required (select advisory)?n Line patrolled | .
3219 |  | JE24029782 | WAITE ST | Western | WAITE ST | 2024-08-21 | 9:41 | 2024-08-21 | 13:49 | 0.00068441 | 2.759e-06 | 1 | 248 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faulty TFR T3576 Isolated at TFR T3576 Fuses TFR Replaced, other fault on Pole 820461 Fixed, Full power restored | .
3220 |  | JE24029819 | PARIHAKA | Western | PARIHAKA | 2024-08-21 | 10:02 | 2024-08-21 | 12:09 | 0.00034839 | 2.759e-06 | 1 | 126 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 6612 No. Fuses: 2 Fuse Amp Size: 8A TIME CLOSED: 12:08 Cause: Unknown Weather (wind/rain): Showers Follow up required (select advisory)? | .
3221 |  | JE24029938 | MOWBRAY RD | Eastern | MOWBRAY RD | 2024-08-21 | 19:08 | 2024-08-21 | 20:09 | 0.033122 | 0.0013215 | 479 | 12005 | Unplanned | DEFECTIVE EQUIPMENT - ZONE SUBSTATION | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 1 Protection flags (nil where none): Def T, E/F, B Phase, CAUSE: Unknown Fault, CB 1 Circuit Breaker Unable to close, Cause Bent Spring Discharge Pin. Location: WAH CB 1 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): 2408014 Circuit patrolled and type: N/A Weather (wind/rain): N/A LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: CB 1 Circuit Breaker Unable to close, Cause Bent Spring Discharge Pin. Cause for original fault unknown. | .
3222 |  | JE24029947 | CROWN | Western | CROWN | 2024-08-21 | 23:45 | 2024-08-22 | 3:28 | 0.019926 | 0.0004166 | 55 | 7222 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 15 Protection flags (nil where none): A Ph O/C E/F CAUSE: Faulty Cable Location: Between Sw/Gear 10446/1 & Sw/Gear 162 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): 2408013 Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Y at Some Sw/Gear Units Follow up Required (select advisory)? Additional fault restoration comments: Faulty Cable found during Sectionalising SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3223 |  | JE24030256 | CLOTON RD NORTH | Western | CLOTON RD NORTH | 2024-08-21 | 10:41 | 2024-08-23 | 21:42 | 0.0012399 | 0.00011036 | 39 | 449 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Isolated at ABS 5558 Tapped down TFR 2065T from tap 3 to tap 2, Full power restored New Voltages are 242, 242, 244 TFR may need to be tapped down another tap, Data logger required to be installed to monitor Voltage | .
3224 |  | JE24026746 | 2195 WAIHI WHANGAMATA ROAD WAIHI WAIHI | Eastern | WAIHI-WHANGAMATA 33KV | 2024-08-20 | 7:01 | 2024-08-20 | 17:07 | 3.845 | 0.0087073 | 3106 | 1393633 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Helicopter installing fibre between poles R1541 and R13096 Downer - replacing cross arms on pole WHIWGM117 & Insulators on pole WHIWGM125/P13099 . Temp generation installed on TC4848 - Outside work area . | .
3225 |  | JE24026927 | 4 UPPER NEWALL ROAD NEWALL NEW PLYMOUTH | Western | PARIHAKA | 2024-08-20 | 9:31 | 2024-08-20 | 14:00 | 0.022314 | 8.2769e-05 | 30 | 8088 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace various poles and X arms in between poles 709953 - 709927 | .
3226 |  | JE24026934 | 31 LOCKINGTON ROAD AONGATETE | Eastern | LOCKINGTON ROAD | 2024-08-20 | 9:45 | 2024-08-20 | 16:58 | 0.025987 | 0.00024279 | 88 | 9419 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | AP1 Install new 33KV Pole Mounted Links 3589 on to the new 12.5m Pole. Install new 33KV cable from Links 3589 to Structure next CB82, Terminate cable to CB82. Remove O/H line s from New Pole and links to CB82 and remove ABS86 . AP2 Reconnect jumpers on Pole 201612 to close Line Break | .
3227 |  | JE24026956 | 47 GLENMORVEN ROAD MORRISONS BUSH GREYTOWN | Western | PONATAHI | 2024-08-20 | 9:16 | 2024-08-20 | 14:06 | 0.0384 | 0.00013243 | 48 | 13918 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace S516 with new Entec Switch | .
3228 |  | JE24027020 | 442 KARERE ROAD TIAKITAHUNA PALMERSTON NORTH | Western | LINTON | 2024-08-20 | 9:11 | 2024-08-20 | 15:33 | 0.129 | 0.00034211 | 124 | 46757 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Complete all work on Poles P31842/P31843 and P31844. Reconductor LV between P31848 - P31842. | .
3229 |  | JE24027032 | 201 BLACK ROAD PAENGAROA TE PUKE | Eastern | ROYDEN DOWNS RD | 2024-08-20 | 8:45 | 2024-08-20 | 14:05 | 0.050342 | 0.00015726 | 57 | 18247 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv overhead conductors with 3W Squirrel between poles 221702 &221712 : Isolation @ ABS 14861.issuer earths @ pole 221702(221700 side) | .
3230 |  | JE24027034 | 702 GLOUCESTER ROAD PAPAMOA BEACH TAURANGA | Eastern | GLOUCESTER RD | 2024-08-20 | 9:00 | 2024-08-20 | 15:09 | 0.092664 | 0.00025107 | 91 | 33587 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re-level SD switchgear IP318 and minor corosion repairs | .
3231 |  | JE24027037 | 134 ST ANDREWS DRIVE BETHLEHEM TAURANGA | Eastern | MOFFAT RD | 2024-08-20 | 9:16 | 2024-08-20 | 12:27 | 0.027914 | 0.00014623 | 53 | 10118 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9126/1/2/3 | .
3232 |  | JE24027047 | 2143 TAIHAPE-NAPIER ROAD MOAWHANGO TAIHAPE | Western | MOAWHANGO | 2024-08-20 | 10:11 | 2024-08-20 | 15:17 | 0.0042279 | 1.3795e-05 | 5 | 1532 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Resag lines at pole 786773 & trim trees between poles 786781 - 786779. | .
3233 |  | JE24027072 | 52 STRANGE ROAD KOMATA PAEROA | Eastern | BENNETT ST | 2024-08-20 | 9:30 | 2024-08-20 | 15:14 | 0.012342 | 3.5867e-05 | 13 | 4474 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace damage x-arms at poles N12777, N2493, N2494, N2496, N2497, N12780, N2508, N2509, N12787, N12791 | .
3234 |  | JE24027073 | 269 KIRIHAU ROAD KORU NEW PLYMOUTH | Western | PIONEER RD | 2024-08-20 | 9:01 | 2024-08-20 | 15:05 | 0.017077 | 4.6902e-05 | 17 | 6190 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 755318,755317,755293,755296,755298,crossarm 755297, LV conductor 755296 to 755318. | .
3235 |  | JE24027079 | 730 MATUKU ROAD TAUHEI MORRINSVILLE | Eastern | MANGATEPARU | 2024-08-20 | 9:31 | 2024-08-20 | 14:40 | 0.082926 | 0.00026762 | 97 | 30057 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | VARIOUS SITES FOR DEFECTS. POLES K12723, K0986, K1048, K0880. REPLACE ROTTON HV XARMS & POLE. K12688 REPLACE ROTTON LV XARMS | .
3236 |  | JE24028235 | 1507 OPAKI KAIPARORO ROAD MAURICEVILLE MASTERTON | Western | MAURICEVILLE | 2024-08-20 | 9:49 | 2024-08-20 | 12:19 | 0.016543 | 0.00011036 | 40 | 5996 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To rearm TX pole T8/151 replace pole P15945 to lift conductor to legal height across road . | .
3237 |  | JE24028529 | 144 OMANGO VALLEY ROAD HUNTERVILLE HUNTERVILLE | Western | HUNTERVILLE 22KV | 2024-08-20 | 10:45 | 2024-08-20 | 12:22 | 0.00053616 | 5.5179e-06 | 2 | 194 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Repair Spragged 11KV conductors on pole 807131 called by Pole Tech | .
3238 |  | JE24028596 | Waihi Substation | Eastern | WAITAWHETA | 2024-08-20 | 9:01 | 2024-08-20 | 16:13 | 0.0027202 | 0.00025382 | 46 | 986 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Isolate Left hand Bus at Waihi Sub incoming 33KV and outgoing 11KV feeders to install new Goose settings. Install new Fibre cable between CB8 and CB10 and test Fibre. Replace Arc Flash card at CB18 | .
3239 |  | JE24029542 | 81 WAIHI VALLEY ROAD, DANNEVIRKE, 4971 | Western | HOROEKA | 2024-08-20 | 15:05 | 2024-08-20 | 16:00 | 0.00030542 | 5.5179e-06 | 2 | 111 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Returning in Morning to replace Transformer Transformer replaced T9/62 Single Phase replaced | .
3240 |  | JE24029545 | NO 3 LINE | Western | NO 3 LINE | 2024-08-20 | 0:53 | 2024-08-20 | 12:19 | 0.021988 | 0.00020968 | 53 | 7970 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kv Rec177 Protection flags (nil where none): C Phase O/C E/F CAUSE: Line Down Location: Pole 790783 Temp generation (state details when used): Lines repaired PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Wind LFI (Y/N + Comments): No Follow up Required (select advisory)? Additional fault restoration comments: Cut Temp line break as span down over 100m and in trees | .
3241 |  | JE24029547 | BURNSIDE | Western | BURNSIDE | 2024-08-20 | 5:45 | 2024-08-20 | 9:03 | 0.091596 | 0.00070905 | 257 | 33199 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: Recloser C639 Protection flags (nil where none): A, B OC CAUSE: N/A Location: N/A Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Line patrolled, nothing found SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3242 |  | JE24029550 | 872 TE KAPUA ROAD, MANGAWEKA, MANGAWEKA, 4797 | Western | MANGAWEKA | 2024-08-20 | 8:05 | 2024-08-20 | 13:39 | 0.021224 | 6.3456e-05 | 23 | 7693 | Unplanned | ADVERSE ENVIRONMENT - LAND SLIPPAGE | Slip over road with tree in lines Can fault man give Stuart a Call when on Site on027 464 9283 as to weather it is safe to cut tree to open road again Please The slip is just down the road from the address its all coned off. Location: Pole 812195 Isolation: Fuses 2813 Lines dropped so Higgins could cut trees, & then lines reinstated. | .
3243 |  | JE24029627 | WHARAWHARA ROAD | Eastern | WHARAWHARA ROAD | 2024-08-20 | 10:56 | 2024-08-20 | 14:12 | 0.00053883 | 2.759e-06 | 1 | 195 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: SB1-013 No. Fuses: 3 (2 X DDO Barrels) Fuse Amp Size: 20 Amp TIME CLOSED: 14:11 Cause: Line Clash Weather (wind/rain): Windy Follow up required (select advisory)? No | .
3244 |  | JE24029630 | UNION LINE | Western | UNION LINE | 2024-08-20 | 11:06 | 2024-08-20 | 14:46 | 0.061894 | 0.00028417 | 103 | 22434 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Replaced cross arm at pole 793146 | .
3245 |  | JE24029633 | MANGAWEKA | Western | MANGAWEKA | 2024-08-20 | 16:34 | 2024-08-21 | 11:38 | 0.013463 | 6.0697e-05 | 18 | 4880 | Unplanned | LIGHTNING - LIGHTNING STRIKE | FM found low Voltages at Txfmr X1146. Investigated with no cause found so Transformer X1146 was replaced. Voltages were still low, so decision made to return in morning for further investigation. FM returned next day and found 1x blown HV fuse at Fuses 4142. relivened at 11:37 hrs using 1x 6A fuse link. Suspect cause lightning strike. Safety Disconnect carried out at 434 Ruahine Rd. Power was disconnected at Pole 796746 due to no earth neutral MEN link on sw/board. Note left for customer to contact own electrician for repair. Disco Tag #A43392 | .
3246 |  | JE24029716 | MOWBRAY RD | Eastern | MOWBRAY RD | 2024-08-20 | 17:08 | 2024-08-20 | 21:55 | 0.0031629 | 1.1036e-05 | 4 | 1146 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: FC2246 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 21:54 Cause: Unknown Weather (wind/rain): Wind Rain Follow up required (select advisory)? | .
3247 |  | JE24029722 | 269 KIRIHAU ROAD KORU NEW PLYMOUTH | Western | PIONEER RD | 2024-08-20 | 16:15 | 2024-08-20 | 18:19 | 0.0013646 | 1.1036e-05 | 4 | 495 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Replace faulty tx 861. Faulty upon relivening after planned Shutdown NAPA 110167 | .
3248 |  | JE24030167 | WAIHI BEACH RD | Eastern | WAIHI BEACH RD | 2024-08-20 | 9:46 | 2024-08-20 | 15:07 | 0.0026618 | 8.2769e-06 | 3 | 965 | Unplanned | HUMAN ERROR - POTENTIAL SWITCHING ERROR | Offloaded as part of NAPA 110091 not advertised SIS Isolation for CB 4 at links IP689 - notes on SIS: Paddock no access for truck - Tx TC1543 isolated because of this - unplanned outage for customers on this tx | .
3249 |  | JE24026881 | 125 MORIKAU ROAD RANANA WANGANUI | Western | RAETIHI | 2024-08-19 | 8:46 | 2024-08-19 | 10:15 | 0.018798 | 0.00020968 | 76 | 6813 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 2x digger poles 777524 & 777526. Replace HV Xarm pole 777525. Customer not advised of outage - power off for 90 min but work not done. | .
3250 |  | JE24026885 | 304 MANAIA ROAD MANAIA HAWERA | Western | AUROA | 2024-08-19 | 9:15 | 2024-08-19 | 15:17 | 0.046931 | 0.00012967 | 47 | 17010 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace TX structure M1010 and pole 718277 | .
3251 |  | JE24026912 | 3077 TAIRUA WHITIANGA ROAD KAIMARAMA WHITIANGA | Eastern | COROGLEN | 2024-08-19 | 9:23 | 2024-08-19 | 15:54 | 0.12506 | 0.00032004 | 116 | 45329 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 862269, W12471 (TC1106), W1667 & W1668. Replace cross arms on poles W1661, W1662, W1663, W1664, W1666, W1669, W1678, W1677, W1680 and W1681. | .
3252 |  | JE24026916 | 31 LOCKINGTON ROAD AONGATETE | Eastern | LOCKINGTON ROAD | 2024-08-19 | 9:06 | 2024-08-19 | 16:24 | 0.0084685 | 1.9313e-05 | 7 | 3069 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Shut 2 Day 1: Replace 33KV Pole 201001 with a new Double 12.5m Busk pole. install new steel structure next to CB 82 in the Switchyard for new cable | .
3253 |  | JE24026930 | 1 KAIKAHU ROAD NORTH KEREPEHI PAEROA | Eastern | KAIHERE | 2024-08-19 | 8:53 | 2024-08-19 | 11:36 | 0.021039 | 0.00012967 | 47 | 7626 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Repair LV conductors at TC3221 | .
3254 |  | JE24027066 | 983 OROUA VALLEY ROAD APITI KIMBOLTON | Western | RANGIWAHIA | 2024-08-19 | 8:46 | 2024-08-19 | 10:56 | 0.019114 | 0.00014623 | 53 | 6928 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Reconductor LV from Pole P05427 to P05431 | .
3255 |  | JE24029229 | WAIHI NORTH | Eastern | WAIHI NORTH | 2024-08-19 | 4:35 | 2024-08-19 | 10:25 | 0.087928 | 0.00098219 | 166 | 31870 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 9604/2 Protection flags (nil where none): E/F CAUSE: Location 1: HV Lines down at Pole 876602 (B Ø) 16mm Copper Location 2: Broken Binder/conductor at Pole P1524 Location: Poles 876 602 & Poles P1524 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Rain/wind. LFI (Y/N + Comments): No Follow up Required (select advisory)? Yes Additional fault restoration comments: Line Patrol was carried out from REC 9604/2 towards ABS IC278 First fault was found down spur line past ABS 232 which was a HV Lines down at Pole 876602. We then restored the network to normal, a short while after doing this REC 9604/2 tripped on E/F protection, indicating a second fault. Field Switcher found a broken binder at Pole P1524 which was on the main line. Priority was taken to repair the second fault first and get the main line back on and energized. After this fault was repaired the spur line fault past ABS 232 was repaired. Full Power restored to all ICP's at 10:24 | .
3256 |  | JE24029234 | TE PUKE QUARRY RD | Eastern | TE PUKE QUARRY RD | 2024-08-19 | 5:10 | 2024-08-19 | 13:34 | 0.090033 | 0.00052144 | 189 | 32633 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 9274/2 Protection flags (nil where none): O/C C Ø CAUSE: Tree fell across HV Lines Location: Pole 222 985 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Rain/Wind LFI (Y/N + Comments): Yes, none operated. Follow up Required (select advisory)? No Additional fault restoration comments: HV Lines down across the gully due to Trees that fell over at Pole 222 985 Repairs were carried out under AP 9234-01 Full Power was restored at 13:33 | .
3257 |  | JE24029241 | Bruce Rd - Te Maunga Sub - REC 14727 | Eastern | BRUCE RD | 2024-08-19 | 6:32 | 2024-08-19 | 12:51 | 0.20885 | 0.0010843 | 393 | 75697 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 14727/2 Protection flags (nil where none): E/F CAUSE: Tree fell across HV Lines Location: Between Poles 393 078 & 220 105 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Wind/Rain LFI (Y/N + Comments): Yes, none operated. Follow up Required (select advisory)? No Additional fault restoration comments: Repaired 3x Broken HV Lines, 4x LV Lines Broken. Replaced LV Cross-Arm & Hardware & Replaced LV Dead-Ends + Re-Sag Lines Tree brought down HV Lines All repairs were carried out and Full Power ON at 12:50 | .
3258 |  | JE24029258 | HIKUAI | Eastern | HIKUAI | 2024-08-19 | 9:36 | 2024-08-19 | 13:57 | 0.0014451 | 5.5179e-06 | 2 | 524 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Isolation: TX TC1393 Fuses CAUSE: LV Lines down due to line clash from wind Poles: 269 571 & 383 110 Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Rain/wind. Follow up required (select advisory)? No Additional fault restoration comments: Isolate Transformer TC1393 and repair LV Lines down Limited access and will take several hours. Repairs carried out and Full Power ON at 13:57 | .
3259 |  | JE24029259 | IRIRANGI | Western | IRIRANGI | 2024-08-19 | 7:42 | 2024-08-19 | 11:21 | 0.0054272 | 2.4831e-05 | 9 | 1967 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: Fuses 154 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 11:20 Cause: Wind Weather (wind/rain): Windy Follow up required (select advisory)? No | .
3260 |  | JE24029263 | 215 SUTHERLAND ROAD, MANAIA | Western | OTAKEHO | 2024-08-19 | 8:52 | 2024-08-19 | 10:25 | 0.0048454 | 5.242e-05 | 19 | 1756 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Fuses MA574 Protection flags (nil where none): CAUSE: Broken wires Pole 218383 EPO Join Failed Cause Location: Pole 218383 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3261 |  | JE24029264 | IHAIA RD | Western | IHAIA RD | 2024-08-19 | 11:37 | 2024-08-19 | 15:11 | 0.011564 | 7.1733e-05 | 26 | 4191 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: 11kV TA110 CAUSE: Failed DTX T1235, No Earthing Spiggots fitted, Main line isolated & Spiggots installed while transformer being changed. Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: Weather (wind/rain): Lightning Follow up required (select advisory)? Additional fault restoration comments: Multiple A/R at TA1 during fault time | .
3262 |  | JE24029267 | MATAPIHI RD | Eastern | MATAPIHI RD | 2024-08-19 | 8:04 | 2024-08-19 | 12:31 | 0.0088451 | 0.0027424 | 497 | 3206 | Unplanned | HUMAN ERROR - LOAD SHEDDING - NETWORK LOAD | Outage due to Paralleling of ABS SD4-094. Part of non-outage NAPA 114042. See NAPA 114042 for Paperwork | .
3263 |  | JE24029272 | LEPPERTON | Western | LEPPERTON | 2024-08-19 | 8:15 | 2024-08-19 | 10:19 | 0.0010238 | 8.2769e-06 | 3 | 371 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | Fuses Location: Fuses 8447 No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 10:19 Cause: Small Branch in line Weather (wind/rain): Wind / Rain Follow up required (select advisory)? | .
3264 |  | JE24029282 | BAINESSE | Western | BAINESSE | 2024-08-19 | 10:47 | 2024-08-19 | 13:10 | 0.00039462 | 2.759e-06 | 1 | 143 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: B64 - tx T1/579 only tx past these fuses for isolation CAUSE: Lightning Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: Yes / Cursory Weather (wind/rain): Heavy Rain / Lightning Follow up required (select advisory)? Additional fault restoration comments: Replaced 50/11/3ph Transformer T1/579 like for like due to lightning strike | .
3265 |  | JE24029292 | MANOEKA RD | Eastern | MANOEKA RD | 2024-08-19 | 9:05 | 2024-08-19 | 14:12 | 0.0076036 | 2.4831e-05 | 9 | 2756 | Unplanned | VEGETATION - OUTSIDE ZONE | Isolation: 11kV Fuse/Sw 13145/2 CAUSE: HV Lines down due to Trees that fell over. Pole: 223358 & TX TE5-087 Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Rain/wind. Follow up required (select advisory)? No Additional fault restoration comments: HV Lines brought down. Access is very challenging 13:01 - Completed 1R - Levi heading to another job, Clint Johnston to take over under the 2R All repairs completed and the HV Lines were repaired. Full Power ON at 14:11 | .
3266 |  | JE24029305 | MAKIRIKIRI | Western | MAKIRIKIRI | 2024-08-19 | 9:28 | 2024-08-19 | 12:31 | 0.00050273 | 2.759e-06 | 1 | 182 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Transformer 4728W No. Fuses: 2x Fuse Amp Size: 2A TIME CLOSED: 12:30 Cause: Lightning Weather (wind/rain): Stormy Follow up required (select advisory)? | .
3267 |  | JE24029344 | WATERWORKS RD | Western | WATERWORKS RD | 2024-08-19 | 11:00 | 2024-08-19 | 14:33 | 0.0017612 | 8.2769e-06 | 3 | 638 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 16077 No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 14:20 Cause: Unknown - But Suspect Weather Related Weather (wind/rain): Stormy Follow up required (select advisory)? | .
3268 |  | JE24029347 | BRISTOL RD | Western | BRISTOL RD | 2024-08-19 | 11:02 | 2024-08-19 | 12:20 | 0.00021712 | 2.759e-06 | 1 | 79 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 6873 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 12:20 Cause: Unknown Weather (wind/rain): Wind & Rain Follow up required (select advisory)? | .
3269 |  | JE24029363 | SOUTH RD NGARIKI | Western | SOUTH RD NGARIKI | 2024-08-19 | 19:30 | 2024-08-19 | 23:01 | 0.0005809 | 2.759e-06 | 1 | 211 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Replaced Transformer N3180 cause Lightning 3x 3amp fuses replaced | .
3270 |  | JE24029387 | KATIKATI | Eastern | KATIKATI | 2024-08-19 | 12:21 | 2024-08-19 | 13:00 | 0.0060488 | 0.0001545 | 56 | 2192 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: Fuses SC1-005 CAUSE: DDO failed at TX TC1-039 Pole: 208 199 Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Rain/wind. Follow up required (select advisory)? No Additional fault restoration comments: DDO failed at Transformer TC1-039 Full Power restored at 13:00 | .
3271 |  | JE24029394 | 2 SCOTT ROAD, OKAIAWA, HAWERA, 4671 | Western | KETEMARAE RD | 2024-08-19 | 13:11 | 2024-08-19 | 13:50 | 0.00022035 | 5.5179e-06 | 2 | 80 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: Lead off Bottom of D/Outs DTX W5287 Repaired Weather (wind/rain): Wind Rain Lightning Follow up required (select advisory)? | .
3272 |  | JE24029401 | FORDELL | Western | FORDELL | 2024-08-19 | 12:32 | 2024-08-19 | 17:40 | 0.032262 | 0.00040557 | 147 | 11693 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV, Rec 537 Protection flags (nil where none): E/F, B phase CAUSE: Broken Crossarm . Rotten Location: Pole 792688 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Yes / Cursory Weather (wind/rain): Windy LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): Replaced set of 3x HV fuse holders | .
3273 |  | JE24029408 | BRUNSWICK | Western | BRUNSWICK | 2024-08-19 | 10:41 | 2024-08-19 | 14:43 | 0.001337 | 5.5179e-06 | 2 | 485 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 2882 No. Fuses: 2x Fuse Amp Size: 6A TIME CLOSED: 14:42 Cause: Unknown - Possibly Weather Related Weather (wind/rain): Wind & Rain Follow up required (select advisory)? | .
3274 |  | JE24029409 | KAKARIKI | Western | KAKARIKI | 2024-08-19 | 14:00 | 2024-08-19 | 16:35 | 0.015777 | 0.00010208 | 37 | 5718 | Unplanned | VEGETATION - OUTSIDE ZONE | Location: P02431 Cause: Fallen tree outside notice zone bought HV lines down Isolation: Fuses M71 What was replaced? 3x 20A HV fuse links & lines down repaired Weather: Light Rain / Windy Additional Info: | .
3275 |  | JE24029416 | WAIHI BEACH RD | Eastern | WAIHI BEACH RD | 2024-08-19 | 13:03 | 2024-08-19 | 14:41 | 0.013934 | 0.00017933 | 65 | 5050 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV SEC 13200/2 Protection flags (nil where none): B C Ø O/C CAUSE: Unknown Location: Unknown Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Wind/rain. LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Field Switcher busy with a Line Patrol down Woodland Road Line Patrolled and nothing abnormal was found. (No fault found) Full Power restored at 14:41 | .
3276 |  | JE24029461 | NO 3 LINE | Western | NO 3 LINE | 2024-08-19 | 14:41 | 2024-08-19 | 17:30 | 0.024668 | 0.00014623 | 53 | 8941 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | REGULATORY INFORMATION Voltage & Device ID: 11kV, Rec 177 Protection flags (nil where none): E/F, C phase CAUSE: Wind blown debris. Branch on lines bought line down Location: 790783 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Yes / Cursory Weather (wind/rain): Windy LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3277 |  | JE24029466 | MANOEKA RD | Eastern | MANOEKA RD | 2024-08-19 | 16:49 | 2024-08-19 | 19:13 | 0.018165 | 0.00016002 | 58 | 6584 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Isolation: Fuse/Sw 9174/3 CAUSE: Suspect Cable Fault Location: TX TE5-134 Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Windy & rain. Follow up required (select advisory)? No Additional fault restoration comments: HV cables tested OK, patrolled lines no fault could be found. Replaced 3 x 32 HRC fuses at Fused/Sw 9174/3 | .
3278 |  | JE24029484 | REVANS ST | Western | REVANS ST | 2024-08-19 | 16:16 | 2024-08-19 | 18:13 | 0.00032259 | 2.759e-06 | 1 | 117 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 7271 No. Fuses: 2 Fuse Amp Size: 8 Amp TIME CLOSED: 17:58 hrs Fuses Location: T2245 No. Fuses: 2 Fuse Amp Size: 2 Amp TIME CLOSED: 18:12 hrs Cause: Lightning Weather (wind/rain): Heavy Rain / Lightning Follow up required (select advisory)? | .
3279 |  | JE24029490 | BLAKE ST | Western | BLAKE ST | 2024-08-19 | 19:30 | 2024-08-19 | 20:25 | 0.00045592 | 8.2769e-06 | 3 | 165 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3 X DDOs at transformer 3522T Needed Replacing and Jumpers Replaced Isolated at ABS 5073 ABS 5104 & Links 12478 Back feeds in at ABS5054 & rec 12383 | .
3280 |  | JE24029495 | FORDELL | Western | FORDELL | 2024-08-19 | 16:46 | 2024-08-19 | 21:01 | 0.0056404 | 2.2072e-05 | 8 | 2044 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2 Span of Conductor down Burnt Crossarm Replaced Crossarm and Pulled Conductor up Isolated at Fuses 1198 | .
3281 |  | JE24029512 | WHAKAMARA | Western | WHAKAMARA | 2024-08-19 | 18:11 | 2024-08-19 | 22:50 | 0.075956 | 0.00049385 | 179 | 27531 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11KV CB 2 Protection flags (nil where none): A B C O/C E/F CAUSE: Lines down Location: Transformer W2335 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: No Called by Fire Service Weather (wind/rain): Rain LFI (Y/N + Comments): No Follow up Required (select advisory)? Additional fault restoration comments: Found Duck under Line which had twisted lines together causing them to burn Down HV/LV Clash so LV off over night Feeds 1 House and cowshed which court Fire Isolated at ABS WH278 &* WH229 Back feed in at ABS 6537 | .
3282 |  | JE24024468 | 134 LONDON STREET SAINT JOHNS HILL WANGANUI | Western | CARLTON AVE | 2024-08-18 | 6:01 | 2024-08-18 | 12:58 | 0.002501 | 0.00081114 | 147 | 907 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 457236 hit by vehicle | .
3283 |  | JE24028298 | 251 HIGH STREET SOUTH CARTERTON CARTERTON | Western | TAVERNER ST | 2024-08-18 | 9:01 | 2024-08-18 | 11:29 | 0.018821 | 0.00012691 | 46 | 6822 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Upgrade T1902 to 200kva | .
3284 |  | JE24029096 | MANGOREWA | Eastern | MANGOREWA | 2024-08-18 | 0:27 | 2024-08-18 | 11:08 | 0.10807 | 0.0008608 | 312 | 39171 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: CB 2 Protection flags (nil where none): A, B, C OC, Ground Fault CAUSE: Lines Down Trees on lines Location: Pole 221030 to 266680 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Rain & wind. LFI (Y/N + Comments): Yes at Pole 221069 and were misleading, fault was found further upstream near Pole 221030/266680 Follow up Required (select advisory)? Yes Additional fault restoration comments: No Access - lines in Paddocks, need to be attended during daylight, No shackled poles to cut a line break. Busy carrying out Isolation & Earthing to create TLB at Pole 221025 TLB at Pole 221025 created. (Updated on eMap) Earths removed and Power restored via ABS SE6-111 at 11:07 Very wet conditions and access is challenging to carry out repairs. Planned NAPA 114731 for 06/09/24 2R closed out | .
3285 |  | JE24029099 | KATERE 9 | Western | KATERE 9 | 2024-08-18 | 4:10 | 2024-08-18 | 7:35 | 0.041 | 0.0010043 | 364 | 14861 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11KV CB 9 Protection flags (nil where none): B ph O/C & E/F CAUSE: Lines down Hit by Bird Location: 361821 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: cursory Weather (wind/rain): wind & rain LFI (Y/N + Comments): Follow up Required (select advisory)? n Additional fault restoration comments: Line was isolated at Sw/Gear 12376/3 to repair the lines.Replaced about 20m of conductor | .
3286 |  | JE24029100 | KONINI | Western | KONINI | 2024-08-18 | 6:45 | 2024-08-18 | 10:02 | 0.0027088 | 1.3795e-05 | 5 | 982 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Blown Transformer T7/253 Replaced Transformer Isolated at Transformer Fuses | .
3287 |  | JE24029103 | RUAPEHU DR | Western | RUAPEHU DR | 2024-08-18 | 6:17 | 2024-08-18 | 11:48 | 0.18632 | 0.0012636 | 458 | 67533 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11KV CB 10 Protection flags (nil where none): A,B,C ph O/C & E/F CAUSE: Transformer T2/311H/T Bushings blown up and Jumper at pole p444460 Blown as well Location: Transformer T2/311 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): 2408010 Circuit patrolled and type: Weather (wind/rain): Rain LFI (Y/N + Comments): Yes & working Follow up Required (select advisory)? Additional fault restoration comments: Transformer T2/311 Has been Temp removed from Network and back feed from T2/588 2R left open to use IF Fuses at Back feed do not hold | .
3288 |  | JE24029107 | MANAIA COROMANDEL | Eastern | MANAIA COROMANDEL | 2024-08-18 | 9:59 | 2024-08-18 | 17:00 | 0.0021633 | 1.1036e-05 | 2 | 784 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: FC789 No. Fuses: 2 Fuse Amp Size: 5 Amp TIME CLOSED: 11:20 Cause: Deterioration Weather (wind/rain): Wind & rain Follow up required (select advisory)? No Upon further investigation, field switcher found a faulty DDO at Transformer TC5942 at Pole T13075 Isolation: Fuses FC789 Carried out repairs under AP 9107 Repairs carried out and Power restored via Fuses FC789 at 11:20 Found TX TC5942 Fuses were blown on arrival, transformer is faulty. Replaced Transformer TC5942 under AP 9107-02 Full Power restored at 17:00 | .
3289 |  | JE24029113 | COROGLEN | Eastern | COROGLEN | 2024-08-18 | 10:16 | 2024-08-18 | 11:05 | 0.00054149 | 1.1036e-05 | 4 | 196 | Unplanned | VEGETATION - OUTSIDE ZONE | Fuses Location: TX TC1120 No. Fuses: 1 & Barrel Fuse Amp Size: 3 Amp TIME CLOSED: 11:04 Cause: Trees across LV Lines Weather (wind/rain): Windy Follow up required (select advisory)? No Isolation: TX TC1120 Fuses Open to Clear/cut trees across LV Lines Full Power restored at 11:04 | .
3290 |  | JE24029117 | WAIHI NORTH | Eastern | WAIHI NORTH | 2024-08-18 | 8:38 | 2024-08-18 | 10:33 | 0.00031566 | 2.759e-06 | 1 | 114 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | Fuses Location: FC4023 No. Fuses: 2 Fuse Amp Size: 6 Amp TIME CLOSED: 10:32 Cause: Tree branch on the O/H Line Weather (wind/rain): Wind & Rain Follow up required (select advisory)? No | .
3291 |  | JE24029139 | TIRAUMEA | Western | TIRAUMEA | 2024-08-18 | 14:30 | 2024-08-19 | 15:03 | 0.032502 | 2.2072e-05 | 8 | 11780 | Unplanned | VEGETATION - OUTSIDE ZONE | Locations: P04971 & Transformer T9-244 Isolation: V75 Cause: Trees in lines at T9-244 Cause: Trees through lines & lines down at Pole P04971 Weather (wind/rain): Windy / Heavy Rain Follow up required (select advisory)? Additional Information: Treesmart called to site to cut trees | .
3292 |  | JE24029150 | CLOTON RD SOUTH | Western | CLOTON RD SOUTH | 2024-08-18 | 14:05 | 2024-08-18 | 17:16 | 0.0068386 | 3.5867e-05 | 13 | 2479 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Replaced crossarm at Pole 758588 Isolated at Fuses 5552 | .
3293 |  | JE24029154 | WAIOURU 33KV | Western | WAIOURU 33KV | 2024-08-18 | 13:23 | 2024-08-18 | 17:36 | 0.29876 | 0.0016747 | 607 | 108287 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 33KV CB 1112 Protection flags (nil where none): O/C CAUSE: Floating Conductor Location: Pole 779225 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): no Circuit patrolled and type: Weather (wind/rain): Wet & Cold LFI (Y/N + Comments): no Follow up Required (select advisory)? no Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Waiouru Circuit that tripped: CB 1112 DTF (KM):no | .
3294 |  | JE24029175 | NAPLES ST | Western | NAPLES ST | 2024-08-18 | 16:23 | 2024-08-18 | 17:38 | 0.050492 | 0.0006787 | 246 | 18301 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV MAB CB C892 Protection flags (nil where none): B & C Ø O/C CAUSE: Tree branch touching HV Lines Location: Pole 813 737 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Light rain/wind. LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Field crew dispatched. Report called in by the public of a tree that fell over near 52 Oxford Street. 17:25 - Field Switcher on site & NO HV lines are down. Tree branch is touching B & C Phase Conductors. Busy trimming the branches via a hotstick. Full Power restored at 17:37 | .
3295 |  | JE24029188 | CLOTON RD WEST | Western | CLOTON RD WEST | 2024-08-18 | 23:28 | 2024-08-19 | 0:08 | 0.0061504 | 0.00015726 | 57 | 2229 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Faultman found blown LV jumper on LV bushing at transformer 2075T, Tfr 2075T was isolated to repair blown LV jumper. Cause lightning | .
3296 |  | JE24029190 | TOWNSHIP & LS | Eastern | TOWNSHIP & LS | 2024-08-18 | 20:39 | 2024-08-18 | 23:19 | 0.007049 | 4.4143e-05 | 16 | 2555 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: 11kV ABS IC711 CAUSE: Deterioration Pole: L12418 Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Light Rain Follow up required (select advisory)? No Additional fault restoration comments: 1 x HV pin arm 1 x Fuse arm 3 x Fuse bases & holders 3 x 3A HV fuses | .
3297 |  | JE24029216 | PIHAMA | Western | PIHAMA | 2024-08-18 | 20:23 | 2024-08-19 | 16:05 | 0.078822 | 0.00033383 | 121 | 28570 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Faultman found Recloser 12194/2 had tripped open, line was patrolled and sectionalized, and after opening spur line and Tfr fuses broken DDO was found at Tfr T5303, line was isolated at ABS's TA813 & TA840 to cut away the jumper to DDO's, line was re-livened. Crew will return in morning to replace DDO's as to dangerous to complete when found due to lightning and heavy rain. 19/08/2024 Replaced D/outs & fitted Earthing spigots, Livened & Found Transformer T5303 had failed due to the Lightning also. Replaced DTX T5303 3 phase 30KVA. | .
3298 |  | JE24029324 | IHAIA RD | Western | IHAIA RD | 2024-08-18 | 21:20 | 2024-08-19 | 12:06 | 0.0066839 | 2.2072e-05 | 8 | 2423 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation from Fuses TA139 to replace blown TX T1455 - due to lightning | .
3299 |  | JE24029046 | RIVERLEA | Western | RIVERLEA | 2024-08-17 | 0:13 | 2024-08-17 | 2:00 | 0.003551 | 3.3108e-05 | 12 | 1287 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 5896 No. Fuses: 2 Fuse Amp Size: 8A TIME CLOSED: 0200 Cause: Unknown Weather (wind/rain): light rain Follow up required (select advisory)? | .
3300 |  | JE24029051 | KATERE 5 | Western | KATERE 5 | 2024-08-17 | 7:45 | 2024-08-17 | 10:14 | 0.0016427 | 1.1036e-05 | 4 | 595 | Unplanned | WILDLIFE - BIRD | Fuses Location: 8193 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 10-14 Cause: Bird Weather (wind/rain): Showers Follow up required (select advisory)? | .
3301 |  | JE24029063 | COONOOR | Western | COONOOR | 2024-08-17 | 10:54 | 2024-08-17 | 12:11 | 0.00021155 | 2.759e-06 | 1 | 77 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T7/339 No. Fuses: 2 Fuse Amp Size: 2 TIME CLOSED: 12-10 Cause: Lightening last week Weather (wind/rain): Fine today Follow up required (select advisory)? | .
3302 |  | JE24029064 | TAITIMU | Eastern | TAITIMU | 2024-08-17 | 13:10 | 2024-08-17 | 14:52 | 0.00027902 | 2.759e-06 | 1 | 101 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 80A HRC fuse blown in Fused/Sw 13308/4 feeding TP3099 relivened 14:51 Replaced 3 x 80A HRC fuses Fault on customer equipment, where the 400V isolator has been left open for the customer to repair their cables. Leave 2R open for Downer to return for re-livening once repairs have been conducted. 27/08/2024 - Update from hub - Waiting on customer to repair their cables before we re-liven. CG 03/09/2024 - Transformer re-livened - customer left disconnected - Tag A44782 Added to tag registry and retailer emailed | .
3303 |  | JE24029065 | CASTLEPOINT | Western | CASTLEPOINT | 2024-08-17 | 12:05 | 2024-08-17 | 14:07 | 0.14705 | 0.0012277 | 445 | 53300 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV CB C937 Protection flags (nil where none): O/C B Ø CAUSE: Unknown Location: Unknown Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F5, cursory patrolled. Weather (wind/rain): rain LFI (Y/N + Comments): Yes, no activation Follow up Required (select advisory)? No Additional fault restoration comments: Lines patrolled, no fault found. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3304 |  | JE24029085 | KAIMAI DRIVE | Eastern | KAIMAI DRIVE | 2024-08-17 | 19:29 | 2024-08-17 | 22:17 | 0.084315 | 0.0013353 | 484 | 30560 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: Recloser 9275 Protection flags (nil where none): EF O, Phase A OC CAUSE: Tree on Lines Location: Pole 211600 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Tree removed by hot stick SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3305 |  | JE24029086 | MANGAWEKA | Western | MANGAWEKA | 2024-08-17 | 20:13 | 2024-08-17 | 23:27 | 0.031902 | 0.00023727 | 86 | 11563 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11KV REC 4199/2 Protection flags (nil where none): C ph O/C & E/F CAUSE: Line down due to broken insulator Location: Pole 796245 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: cursory Weather (wind/rain): rain LFI (Y/N + Comments): N Follow up Required (select advisory)? N Additional fault restoration comments: Line was isolated at ABS's 1378 & 2953 to repair the line. | .
3306 |  | JE24029090 | MAKETU | Eastern | MAKETU | 2024-08-17 | 21:33 | 2024-08-18 | 0:49 | 0.33283 | 0.0017961 | 651 | 120636 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: Recloser 14788 Protection flags (nil where none): Phase A, C OC CAUSE: Tree on lines Location: Pole 218481 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Removed with hot stick and saws attached SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3307 |  | JE24026780 | Roberts road Mangatautari | Eastern | CAMBRIDGE RD TIRAU | 2024-08-16 | 9:23 | 2024-08-16 | 14:24 | 0.0058135 | 1.9313e-05 | 7 | 2107 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace pole D1157 with new 11m busck at TC1812 replace Las and upgrade TX earthing to Powerco standard | .
3308 |  | JE24026787 | 295 ROBERTS ROAD, MAUNGATAUTARI, CAMBRIDGE | Eastern | CAMBRIDGE RD TIRAU | 2024-08-16 | 9:31 | 2024-08-16 | 12:20 | 0.0014033 | 8.2769e-06 | 3 | 509 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | AT POLE D12674 REPLACE 11KV TRAINER ARM REPLACE 400V FUSE ARM AND FUSING- TX MAY HAVE TO BE LIFTED FROM POLE TO ACCESS | .
3309 |  | JE24026791 | 325 KIRIHAU ROAD KORU NEW PLYMOUTH | Western | PIONEER RD | 2024-08-16 | 9:01 | 2024-08-16 | 14:58 | 0.016761 | 4.6902e-05 | 17 | 6075 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles, 755295,755304(TX855),755305,755306,755307 crossarms,755308,755309,755310,755311. | .
3310 |  | JE24026801 | 983 OROUA VALLEY ROAD APITI KIMBOLTON | Western | RANGIWAHIA | 2024-08-16 | 8:45 | 2024-08-16 | 14:08 | 0.054332 | 0.0001683 | 61 | 19693 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace crossarms between and including Pole P05427 to P05434. Replace P67 & relocate TX T4/141 from P05429 to P05428 | .
3311 |  | JE24026835 | 198 TIMARU ROAD UPPER TATARAIMAKA NEW PLYMOUTH | Western | INLAND COAST | 2024-08-16 | 9:45 | 2024-08-16 | 11:22 | 0.0056181 | 5.7938e-05 | 21 | 2036 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT - Inspection repair at pole 757304 Repair Hv jumper | .
3312 |  | JE24026837 | 2937 CARRINGTON ROAD OKATO NEW PLYMOUTH | Western | INLAND COAST | 2024-08-16 | 13:31 | 2024-08-16 | 14:20 | 0.0012155 | 2.4831e-05 | 9 | 441 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT - Repair low sagging HV wires in between poles 755570 - 755571 | .
3313 |  | JE24028220 | 375 TREMAINE AVENUE TAKARO PALMERSTON NORTH | Western | MAIN ST 15 | 2024-08-16 | 2:00 | 2024-08-16 | 5:13 | 0.042249 | 0.00022072 | 80 | 15313 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Correct phasing T6/483 from the incomer 10920/3. HV cables at 10920/1 and 10920/3 need to be swapped to allow the incomer to be at /1 so it makes sense in the field. | .
3314 |  | JE24028906 | HOROEKA | Western | HOROEKA | 2024-08-16 | 9:21 | 2024-08-16 | 10:25 | 0.0012479 | 1.9313e-05 | 7 | 452 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Part power to the end two transformers. Possibly a blown jumper but will need a Mule to patrol the lines. Will return in the morning Faultman found blown jumper at pole 440912, line was isolated at Fuses V8 to repair the jumper. | .
3315 |  | JE24028928 | SOUTH FEATHERSTON | Western | SOUTH FEATHERSTON | 2024-08-16 | 6:10 | 2024-08-16 | 7:01 | 0.0065719 | 0.00012691 | 46 | 2382 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Faultman found failed jumper at DDO's to transformer T2474, line was isolated at ABS S566 to repair the jumper. | .
3316 |  | JE24028942 | KAIMATA | Western | KAIMATA | 2024-08-16 | 9:59 | 2024-08-16 | 13:30 | 0.0005837 | 2.759e-06 | 1 | 212 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: 5061T CAUSE: Faulted Transformer. Cause unknown Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: N/A Weather (wind/rain): Calm / Light Rain Follow up required (select advisory)? Additional fault restoration comments: 15kVa dual transformer replaced with 30/11/3ph | .
3317 |  | JE24028966 | AWAITI | Eastern | AWAITI | 2024-08-16 | 12:15 | 2024-08-17 | 10:59 | 0.00074989 | 5.5179e-06 | 1 | 272 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Customer cable fault Disconnection for safety done Tag No: A38564 Cable disconnected from the transformer bushings. No LV disconnect on the transformer and has to be fitted in the morning. Retailer notified of Safety Disconnection 17/08/24 - Transformer TC4261 isolated and earthed at FC2303, 400V disconnect isolator fitted and left open and tagged. The transformer was livened and tested. | .
3318 |  | JE24028979 | 288 JEFFERSONS ILNE, MARTON | Western | TUTAENUI | 2024-08-16 | 14:44 | 2024-08-16 | 15:45 | 0.0072111 | 0.00011864 | 43 | 2614 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Location: Pole 804109 Cause: Aged Isolation: Fuses 426 Replaced 11kV Double Termination Arm as was badly rotted. | .
3319 |  | JE24029025 | KAIHERE | Eastern | KAIHERE | 2024-08-16 | 16:57 | 2024-08-16 | 16:59 | 0.00040367 | 0.00025934 | 94 | 146 | Unplanned | HUMAN ERROR - POTENTIAL SWITCHING ERROR | During planned switching for NAPA 114487, Gas/Sw SC08 opened in error. Switching error made by Control, incorrect device opened. | .
3320 |  | JE24026619 | 130 WATERWORKS ROAD MORRINSVILLE MORRINSVILLE | Eastern | TE MIRO RD | 2024-08-15 | 9:00 | 2024-08-15 | 12:45 | 0.0012413 | 5.5179e-06 | 2 | 450 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE HV CROSSARMS AT POLES 860535 & 860544 | .
3321 |  | JE24026662 | 570 WAITARA ROAD HUIRANGI NEW PLYMOUTH | Western | WAITARA RD | 2024-08-15 | 8:45 | 2024-08-15 | 15:36 | 0.014748 | 3.5867e-05 | 13 | 5346 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove pole 456208 and install 2 x new poles and steelwork framing for voltage regulator, install VR bypass ABS 12728-1, install VR links 12728-6 and VR fuses 12728-4. Replace crossarms on pole 456278 and terminate LV OH lines, remove LV lines from pole 456278 to pole 456528. Terminate new LV UG cable from pole 456278 to new DP next to pole 456528 and connect existing services. | .
3322 |  | JE24026673 | 201 BLACK ROAD PAENGAROA TE PUKE | Eastern | ROYDEN DOWNS RD | 2024-08-15 | 8:47 | 2024-08-15 | 14:30 | 0.05774 | 0.0001683 | 61 | 20928 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv overhead conductors with 3W Squirrel between poles 221690 & 221702: Isolation & issuer earths @ ABS 14861 | .
3323 |  | JE24026677 | 696 PAREWANUI ROAD BULLS BULLS | Western | PAREWANUI | 2024-08-15 | 9:46 | 2024-08-15 | 14:34 | 0.15906 | 0.00055179 | 200 | 57653 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV Poles 809855 & 809857. Replace 11kV Crossarms on Pole 809772. Repair damaged 11kV Conductor on Pole 809542. Replace 11kv Crossarms on Pole 809485. | .
3324 |  | JE24026715 | 31 LOCKINGTON ROAD AONGATETE | Eastern | LOCKINGTON ROAD | 2024-08-15 | 9:31 | 2024-08-15 | 17:28 | 0.0092189 | 1.9313e-05 | 7 | 3341 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Shut 1 Day 2: Install 33KV Pole Mounted Links 3592 on new 15.5m Pole ( installed on NAPA112702). Remove 33KV O/H line from new pole (at Links 3592) to Pole 487423 . Install 33KV Cable from pole 487423 to new pole at Links 3592 . Remove H Structure poles 249543 and 249544 , Remove Pole 487169 and stay wire. | .
3325 |  | JE24026720 | 608 MID PUNIHO ROAD OKATO NEW PLYMOUTH | Western | PARIHAKA | 2024-08-15 | 9:30 | 2024-08-15 | 13:25 | 0.0019451 | 8.2769e-06 | 3 | 705 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace lv x arms at poles 704238 + 704242 Safety isolation of Hv fuses TX P4345 . Same switching as NAPA 110589 . | .
3326 |  | JE24026770 | 895 TAIRUA WHITIANGA ROAD COROGLEN WHITIANGA | Eastern | TAIRUA NORTH | 2024-08-15 | 9:16 | 2024-08-15 | 14:58 | 0.049037 | 0.00014347 | 52 | 17774 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV Poles W1885, W1886, W1902 & W13414, Tairua/Whitianga Rd | .
3327 |  | JE24026783 | 18 RUGBY ROAD TARIKI INGLEWOOD | Western | CLOTON RD NORTH | 2024-08-15 | 9:00 | 2024-08-15 | 13:29 | 0.013849 | 5.242e-05 | 19 | 5020 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install new entec 12740 structure at site 358956 | .
3328 |  | JE24026797 | 98 ORCHARD EAST ROAD,NGATEA | Eastern | HAURAKI RD | 2024-08-15 | 8:50 | 2024-08-15 | 13:23 | 0.028644 | 0.00010484 | 38 | 10382 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv pole O12851,11kv Xarms O12853, straighten pole's O3003 & 877171 | .
3329 |  | JE24026804 | 442 KARERE ROAD TIAKITAHUNA PALMERSTON NORTH | Western | LINTON EXPRESSWAY | 2024-08-15 | 8:30 | 2024-08-15 | 11:50 | 0.0022048 | 1.1036e-05 | 4 | 799 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles and crossarms between poles P31857 and P31845. | .
3330 |  | JE24026814 | 456 Rangitikei Valley Road, Waituna West | Western | WAITUNA | 2024-08-15 | 8:50 | 2024-08-15 | 15:35 | 0.0022355 | 5.5179e-06 | 2 | 810 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Switching for Asplundh vegetation contractor to work between P28259 and 467829 | .
3331 |  | JE24026865 | 10 MOANA STREET OHAWE HAWERA | Western | KETEMARAE RD | 2024-08-15 | 9:16 | 2024-08-15 | 15:31 | 0.12542 | 0.00033383 | 121 | 45458 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 1. Replace poles â€“ 846048 ( AGTRANS) , 846050, 846052, 842653, 723040, 723017, 723023 2. Replace Crossarms â€“ 842645, 842642 | .
3332 |  | JE24028798 | WAOTU | Eastern | WAOTU | 2024-08-15 | 5:03 | 2024-08-15 | 6:52 | 0.00030033 | 2.759e-06 | 1 | 109 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: FP1656 No. Fuses: 2 Fuse Amp Size: 8A TIME CLOSED: 06:52 Cause: Suspect Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? | .
3333 |  | JE24028800 | KOPU | Eastern | KOPU | 2024-08-15 | 7:02 | 2024-08-15 | 16:50 | 0.088394 | 0.0026045 | 900 | 32039 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Unplanned Outages associated with NAPA 113551. Half bus non outage shut for Northpower at Kerepehi sub. Jumper blown off at ABS IC442 Reclosers, CB's opened to restore feeders. Repairs to ABS completed under OMS JE24028807. REGULATORY INFORMATION Voltage & Device ID: Recloser 9161 Protection flags (nil where none): CAUSE: Broken jumper at ABS IC442 Location: ABS IC442 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): no Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): Pole O12692 Follow up Required (select advisory)? Additional fault restoration comments: ABS blew jumper while undergoing NAPA 113551 ABS REPAIRED.NAPA JOB postponed (switching started but work not completed due to fault) | .
3334 |  | JE24028816 | MANGATARATA | Eastern | MANGATARATA | 2024-08-15 | 10:00 | 2024-08-15 | 10:26 | 0.00021134 | 8.2769e-06 | 3 | 77 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Opened HV TX Fuses to repair LV bushes at Transformer TP1907 Fuses TP1907 ORT 10:00 Hrs, Closed 10:25Hrs, Tested at Meter board full power restored 10:30Hrs Relates to JE24028807 Feeder Fault | .
3335 |  | JE24028894 | REVANS ST | Western | REVANS ST | 2024-08-15 | 17:20 | 2024-08-15 | 18:15 | 0.0059126 | 0.0001076 | 39 | 2143 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faultman found line down at pole 852044, line was isolated at Fuses 7255 to repair the line. Cause: Due to wind | .
3336 |  | JE24028920 | FIRTH ST | Eastern | FIRTH ST | 2024-08-15 | 19:23 | 2024-08-15 | 20:50 | 0.00047962 | 5.5179e-06 | 2 | 174 | Unplanned | WILDLIFE - OTHER | Fuses Location: FC1472 No. Fuses: 2 Fuse Amp Size: 8A TIME CLOSED: 20:50 Cause: Cattle rubbing loose Guy Wire cause clash. Guy wire restrained . Weather (wind/rain): Windy Follow up required (select advisory)? | .
3337 |  | JE24026386 | 1051 PAPAMOA BEACH ROAD PAPAMOA BEACH TAURANGA | Eastern | SIMPSON RD | 2024-08-14 | 8:46 | 2024-08-14 | 14:16 | 0.12948 | 0.00039453 | 143 | 46932 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install and commission new ENTEC sectionaliser # 14915 @ pole 499841. Isolation's & earths @ links TEMP025, RMU 13002/3 | .
3338 |  | JE24026581 | 11 JAMES LINE WHAKARONGO PALMERSTON NORTH | Western | ROBERTS LINE | 2024-08-14 | 9:04 | 2024-08-14 | 13:47 | 0.041054 | 0.00014623 | 53 | 14880 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RAISE SWITCHGEAR 10506 DUE TO ACCESS ISSUE | .
3339 |  | JE24026589 | 2 SIEMONEK RISE BETHLEHEM TAURANGA | Eastern | GATE PA | 2024-08-14 | 9:16 | 2024-08-14 | 11:40 | 0.013517 | 9.3805e-05 | 34 | 4899 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9040/1/2/3 | .
3340 |  | JE24026593 | 2408 TAIHAPE-NAPIER ROAD MOAWHANGO TAIHAPE | Western | MOAWHANGO | 2024-08-14 | 9:45 | 2024-08-14 | 13:07 | 0.0027822 | 1.3795e-05 | 5 | 1008 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Shut 7 Resag lines at pole 786733 River Cottage & 786751 Springvale Woolshed. | .
3341 |  | JE24026597 | 2 VERBENA GLEN MOUNT MAUNGANUI TAURANGA | Eastern | AVIATION DRIVE | 2024-08-14 | 9:05 | 2024-08-14 | 11:37 | 0.078736 | 0.00051869 | 188 | 28538 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | link box Maintenace on td4-715 and Td4-718 | .
3342 |  | JE24026598 | 31 LOCKINGTON ROAD AONGATETE | Eastern | APATA | 2024-08-14 | 9:50 | 2024-08-14 | 16:46 | 0.0080309 | 1.9313e-05 | 7 | 2911 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Shut 1 Day1 . Install new 15.5 m Double Busk Pole outside Aongatete Substation . Replace pole 263415 with a new 15.5m pole . | .
3343 |  | JE24026639 | 102 HENDERSONS LINE MARTON MARTON | Western | TURAKINA | 2024-08-14 | 9:15 | 2024-08-14 | 17:10 | 0.068089 | 0.00014347 | 52 | 24679 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Shut 2 - Connection of RMU 16139 and replace structure 793825, Change X2155 HV Circuits over. Live LV Permit for jumper/line break of 800846 & 793829 | .
3344 |  | JE24026645 | 95 SANGSTERS ROAD BUNNYTHORPE PALMERSTON NORTH | Western | STONEY CREEK | 2024-08-14 | 10:00 | 2024-08-14 | 12:55 | 0.018338 | 0.00010484 | 38 | 6647 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 33kv crossarm on P41476 and replace crossarms on pole P41482 T6/568 poles have 11kv and 33kv circuits | .
3345 |  | JE24026665 | 983 OROUA VALLEY ROAD APITI KIMBOLTON | Western | RANGIWAHIA | 2024-08-14 | 8:45 | 2024-08-14 | 11:31 | 0.024178 | 0.00014623 | 53 | 8764 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace crossarms between and including Pole P05419 and P05431. Reconductor LV from 449917 to P05423 | .
3346 |  | JE24026762 | 1437 RIVER ROAD AKITIO PONGAROA | Western | WAIONE | 2024-08-14 | 10:31 | 2024-08-14 | 13:51 | 0.0055299 | 2.759e-05 | 10 | 2004 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT work - install fuse savers @ V44 River Rd | .
3347 |  | JE24028671 | MANGAWEKA | Western | MANGAWEKA | 2024-08-14 | 8:45 | 2024-08-14 | 13:47 | 0.027495 | 9.1046e-05 | 33 | 9966 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 2813 No. Fuses: 3 Fuse Amp Size: 10A TIME CLOSED: 13:46 Cause: Unknown Weather (wind/rain): Sunny Follow up required (select advisory)? This is Parent Job i have created Job JE24028746 at correct fuses 2R was being used for replacement of 400v fuses and extra man hours | .
3348 |  | JE24028697 | KUMENGA | Western | KUMENGA | 2024-08-14 | 9:57 | 2024-08-14 | 14:52 | 0.027252 | 0.00068422 | 248 | 9878 | Unplanned | THIRD PARTY INTERFERENCE - OVERHEAD CONTACT | REGULATORY INFORMATION Voltage & Device ID: CB C927 Protection flags (nil where none): A & C phase EF CAUSE: Digger hit the lines Location: Pole 799084 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: cursory Weather (wind/rain): fine LFI (Y/N + Comments): LFI's reduced outage time by indicating fault past ABS S1201 Follow up Required (select advisory)? Additional fault restoration comments: NDR to follow SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3349 |  | JE24028741 | PARIHAKA | Western | PARIHAKA | 2024-08-14 | 13:25 | 2024-08-14 | 13:51 | 0.0031401 | 0.00012139 | 44 | 1138 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Replace broken binder at Pole 704242 Back feed put in place Isolated at ABS PU410 & PU413 Binder replaced, full power restored | .
3350 |  | JE24028742 | POHANGINA | Western | POHANGINA | 2024-08-14 | 13:23 | 2024-08-14 | 15:21 | 0.00032531 | 2.759e-06 | 1 | 118 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses F32 No. Fuses: 1 Fuse Amp Size: 6A TIME CLOSED: 15:20 Cause: Bird strike Weather (wind/rain): Sunny Follow up required (select advisory)? Fuses Location: Transformer T4/216 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 15:20 Cause: Bird Strike Weather (wind/rain): Sunny Follow up required (select advisory)? Fuses blew at the start of spur line and at the transformer - black marks were found between HV bushings on the transformer - Suspect bird went touchy touch on bushing then ceased to exist. 2R to be used for extra set of fuses | .
3351 |  | JE24028771 | TUTURUMURI | Western | TUTURUMURI | 2024-08-14 | 8:32 | 2024-08-14 | 16:22 | 0.0064932 | 1.3795e-05 | 5 | 2354 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: Fuses 7317 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 1622 Cause: line clash Weather (wind/rain): Windy Follow up required (select advisory)? | .
3352 |  | JE24028777 | KONINI | Western | KONINI | 2024-08-14 | 17:39 | 2024-08-14 | 19:01 | 0.001126 | 1.3795e-05 | 5 | 408 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: T7/253 No. Fuses: 2 Fuse Amp Size: 3 Amp TIME CLOSED: 19:00 Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)? N | .
3353 |  | JE24028784 | CARDIFF RD | Western | CARDIFF RD | 2024-08-14 | 18:18 | 2024-08-14 | 19:30 | 0.0033833 | 4.6902e-05 | 17 | 1226 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 5624 No. Fuses: 2 Fuse Amp Size: 10 Amp TIME CLOSED: 19:30 Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)? N | .
3354 |  | JE24028785 | RONGOKOKAKO | Western | RONGOKOKAKO | 2024-08-14 | 18:21 | 2024-08-14 | 20:00 | 0.00027424 | 2.759e-06 | 1 | 99 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Wrong transformer, Transformer T8/389 effected Fuses Location: S41 No. Fuses: 2 Fuse Amp Size: 6 Amps TIME CLOSED: 20:00 Cause: Unknown (Possible bird strike) Weather (wind/rain): Calm Follow up required (select advisory)? N | .
3355 |  | JE24028793 | MAUNGARANGI RD | Eastern | MAUNGARANGI RD | 2024-08-14 | 22:12 | 2024-08-14 | 23:40 | 0.013031 | 0.00014898 | 54 | 4723 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV ABS SF6-007 BiMetal Jumper Connection Failed Protection flags (nil where none): none CAUSE: 7/16 - Namu BiMetal connection Failed Location: ABS SF6-007 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3356 |  | JE24025336 | 2 GRAVATT RD PAPAMOA | Eastern | PAPAMOA BEACH WEST | 2024-08-13 | 23:08 | 2024-08-14 | 3:29 | 0.033855 | 0.00012967 | 47 | 12271 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Disconnect 3c 35mmÂ² cable supplying transformer TP1120 from switch 2 of the temporary CFC TEMP151, relocate cable and terminate to switch 9139/2. | .
3357 |  | JE24026325 | 442 KARERE ROAD TIAKITAHUNA PALMERSTON NORTH | Western | LINTON | 2024-08-13 | 8:31 | 2024-08-13 | 11:55 | 0.0022574 | 1.1036e-05 | 4 | 818 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles and crossarms between P31862 and P31845. | .
3358 |  | JE24026333 | 822 MOAWHANGO VALLEY ROAD MOAWHANGO TAIHAPE | Western | PAPAKAI | 2024-08-13 | 9:48 | 2024-08-13 | 12:52 | 0.0060841 | 3.3108e-05 | 12 | 2205 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | SHUT 4 Replace pole787266 using helicopter. | .
3359 |  | JE24026351 | 58 SURREY ROAD TARIKI INGLEWOOD | Western | CLOTON RD NORTH | 2024-08-13 | 9:05 | 2024-08-13 | 15:16 | 0.072622 | 0.00019589 | 71 | 26322 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | install new entec 12737 structure at site 757850. Remove ABS 5466 & Fuse 6363 SCADA commissioning to be done on the 14/08 | .
3360 |  | JE24026372 | 10 MOANA STREET OHAWE HAWERA | Western | KETEMARAE RD | 2024-08-13 | 8:46 | 2024-08-13 | 15:56 | 0.14366 | 0.00033383 | 121 | 52070 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 1. Replace poles â€“ 846041 ( AGTRANS) â€“ Change over of LV and HV cabling at TX 5048 , 846042, 721985, 846043, 846045 ( AGTRANS), 723014 2. Replace Crossarms â€“ 846046, 846047, 846049 Job ran over due to the HV cable being a different size to what is on record, new cable kit had to be sourced | .
3361 |  | JE24026382 | 1459 TAIRUA WHITIANGA ROAD COROGLEN WHITIANGA | Eastern | COROGLEN | 2024-08-13 | 9:45 | 2024-08-13 | 15:53 | 0.055882 | 0.00015174 | 55 | 20255 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV Poles W1814, W1817, W1818, W1820, W1823, W1832, W1833, 389975, 263994 & 263995, Tairua/Whitianga Rd | .
3362 |  | JE24026388 | 97 MILL ROAD PAEROA PAEROA | Eastern | RAILWAY ST | 2024-08-13 | 9:02 | 2024-08-13 | 14:50 | 0.019323 | 5.7938e-05 | 21 | 7004 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV Pole 269561. Replace LV Pole N1255. Reconductor LV Between LV Poles N1266 & N1251. | .
3363 |  | JE24026389 | 59 CASTLEWOLD DRIVE BETHLEHEM TAURANGA | Eastern | GATE PA | 2024-08-13 | 9:16 | 2024-08-13 | 11:45 | 0.061113 | 0.00040833 | 148 | 22151 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9038-1/2/3 | .
3364 |  | JE24026391 | 201 BLACK ROAD PAENGAROA TE PUKE | Eastern | ROYDEN DOWNS RD | 2024-08-13 | 8:58 | 2024-08-13 | 14:50 | 0.0038852 | 1.1036e-05 | 4 | 1408 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv/400vt poles 221734 & 221732: Replace 11kv cross arms @ poles 221735,221731,221730,221729,221739 221738,221737, 221736.11kv Isolation and issuer earths @ SE6-226.33kv isolations @ ABS3162, CB3112, ABS76, ABS66. Issuer earths @ pole 483546(483569 side), pole 483546(483554 side) & earth switch 3119. | .
3365 |  | JE24026414 | 6736 WILSON ROAD NETHERTON PAEROA | Eastern | AWAITI | 2024-08-13 | 13:51 | 2024-08-13 | 15:31 | 0.010239 | 0.00010208 | 37 | 3711 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Move fibre loop from pole N12642 to pole N12639 . Checked with applicant re works at pole N12639 OK . | .
3366 |  | JE24026606 | 1412 ROTOEHU ROAD OKERE FALLS TE PUKE | Eastern | ROTOEHU | 2024-08-13 | 9:00 | 2024-08-13 | 11:13 | 0.0036634 | 2.759e-05 | 10 | 1328 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV link box maintenance. | .
3367 |  | JE24026936 | 31 LOCKINGTON ROAD AONGATETE | Eastern | LOCKINGTON ROAD | 2024-08-13 | 10:04 | 2024-08-13 | 13:25 | 0.048538 | 0.00024279 | 88 | 17593 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Insulators and jumpers on Pole 201612. Create line break at pole 201612 feeding from CB5 | .
3368 |  | JE24028400 | 802 MARINGI ROAD, MASTERTON, 5871 | Western | BIDEFORD | 2024-08-13 | 13:58 | 2024-08-13 | 15:00 | 0.0020361 | 3.3108e-05 | 12 | 738 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole 485249 , isolation 7774 will be after self issue cancel of permit due to poor comms Repaired leaning pole and added guy | .
3369 |  | JE24028505 | PAHOIA | Eastern | PAHOIA | 2024-08-13 | 9:00 | 2024-08-13 | 10:30 | 0.0017427 | 1.9313e-05 | 7 | 632 | Unplanned | VEGETATION - INSIDE ZONE | Fuses Location: 11kV Fuses SC2-123 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 10:30 Cause: Tree blew against Line, Isolated & Earthed & Trees cut away at Pole 263419. all trees now are clear NDR Weather (wind/rain): Windy overnight Follow up required (select advisory)? | .
3370 |  | JE24028580 | APATA | Eastern | APATA | 2024-08-13 | 12:31 | 2024-08-13 | 14:02 | 0.0005 | 5.5179e-06 | 2 | 181 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: SC2-030 1 x 15A Fuse Replaced @ 12:33 Fuse Location DTX TC2-195 2 x 2A Fuses Replaced @ 14:01 No. Fuses: 3 total @ 2 spots Fuse Amp Size: 1 x 15A & 2 x 2A TIME CLOSED: 12:33 Cause: Lead off DTX TC2-195 Transformer Bushing Caused fuses to blow Weather (wind/rain): Light Winds Follow up required (select advisory)? This job is single phase only for SC2-030 reload reliven at 12:33 - linked related job has two phase outage | .
3371 |  | JE24028627 | PAREWANUI | Western | PAREWANUI | 2024-08-13 | 17:56 | 2024-08-13 | 20:04 | 0.0014182 | 1.1036e-05 | 4 | 514 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: X2162 No. Fuses: 2 Fuse Amp Size: 2 Amp TIME CLOSED: 20:04 Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)? N | .
3372 |  | JE24028632 | HUNTERVILLE 22KV | Western | HUNTERVILLE 22KV | 2024-08-13 | 19:12 | 2024-08-13 | 21:32 | 0.0092886 | 6.6215e-05 | 24 | 3367 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 997 No. Fuses: 2 Fuse Amp Size: 10 Amp TIME CLOSED: 21:32 Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)? N | .
3373 |  | JE24028642 | HAURAKI RD | Eastern | HAURAKI RD | 2024-08-13 | 22:23 | 2024-08-13 | 23:51 | 0.00097843 | 1.1036e-05 | 4 | 355 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: FC4003 No. Fuses: 3 Fuse Amp Size: 6 TIME CLOSED: 23:51 Cause: suspect bird strike but not confirmed Weather (wind/rain): Follow up required (select advisory)? | .
3374 |  | JE24024391 | 1179 STATE HIGHWAY 53 MARTINBOROUGH MARTINBOROUGH | Western | TAWAHA | 2024-08-12 | 9:46 | 2024-08-12 | 12:04 | 0.024885 | 0.00017933 | 65 | 9020 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Carry out insulator repair on 8039 live line | .
3375 |  | JE24025979 | 77 SOUTH ROAD NO 1 EKETAHUNA EKETAHUNA | Western | MAURICEVILLE | 2024-08-12 | 9:32 | 2024-08-12 | 13:32 | 0.024471 | 0.00010208 | 37 | 8870 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To rearm TX Pole T8/63 | .
3376 |  | JE24026058 | 15 TANGAROA STREET WAITARA WAITARA | Western | PRINCESS ST | 2024-08-12 | 9:40 | 2024-08-12 | 12:06 | 0.0012113 | 8.2769e-06 | 3 | 439 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | safety isolation of in and around pole 744838 to retention stays and add Guy strain insulators | .
3377 |  | JE24026189 | 2709B TAIRUA WHITIANGA ROAD KAIMARAMA WHITIANGA | Eastern | COROGLEN | 2024-08-12 | 9:20 | 2024-08-12 | 13:41 | 0.048938 | 0.00018761 | 68 | 17738 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole W12604 | .
3378 |  | JE24026223 | 6170 STATE HIGHWAY 1 WAIOURU MILITARY AREA WAIOURU | Western | RUAPEHU | 2024-08-12 | 9:01 | 2024-08-12 | 13:43 | 0.0061757 | 2.2072e-05 | 8 | 2238 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace ABS 2541 at pole 778518. DNO 2405019 | .
3379 |  | JE24026227 | 815 OPUA ROAD, OPUNAKE | Western | OAONUI | 2024-08-12 | 9:15 | 2024-08-12 | 14:46 | 0.066638 | 0.0002014 | 73 | 24153 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace HV /LV xarms at poles 713492, 713414, 713418, 713416, 713352 | .
3380 |  | JE24026235 | 983 OROUA VALLEY ROAD APITI KIMBOLTON | Western | RANGIWAHIA | 2024-08-12 | 8:46 | 2024-08-12 | 12:50 | 0.035672 | 0.00014623 | 53 | 12929 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace crossarms between and including Pole P05418 and P05431 | .
3381 |  | JE24026633 | 158 BROADWAY MARTON MARTON | Western | MARTON | 2024-08-12 | 9:07 | 2024-08-12 | 13:51 | 0.0007818 | 2.759e-06 | 1 | 283 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace transformer X3112 due to oil leak | .
3382 |  | JE24028202 | MOUNTAIN RD | Western | MOUNTAIN RD | 2024-08-12 | 7:11 | 2024-08-12 | 9:05 | 0.0040962 | 3.5867e-05 | 13 | 1485 | Unplanned | WILDLIFE - BIRD | Fuses Location: 5547 No. Fuses: 2 Fuse Amp Size: 15A TIME CLOSED: 09:04 Cause: Bird Strike Weather (wind/rain): Light Showers Follow up required (select advisory)? NIL | .
3383 |  | JE24028233 | OLD CAMBRIDGE RD | Eastern | OLD CAMBRIDGE RD | 2024-08-12 | 7:58 | 2024-08-12 | 9:40 | 0.0019792 | 1.9313e-05 | 7 | 717 | Unplanned | THIRD PARTY INTERFERENCE - OVERHEAD CONTACT | Fuses Location: TC1839 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 09:40 Cause: High Load Contact with OH Lines Weather (wind/rain): Overcast Follow up required (select advisory)? NIL | .
3384 |  | JE24028269 | KEREONE | Eastern | KEREONE | 2024-08-12 | 12:34 | 2024-08-12 | 14:16 | 0.00027982 | 2.759e-06 | 1 | 101 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: FP178 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 14:15 Cause: Wind Weather (wind/rain): Wind Follow up required (select advisory)? NIL | .
3385 |  | JE24028274 | MANGAMAIRE | Western | MANGAMAIRE | 2024-08-12 | 13:46 | 2024-08-12 | 14:22 | 0.0077266 | 0.00021796 | 79 | 2801 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Blown Jumper found at Pole P27943 Isolated at ABS R52 | .
3386 |  | JE24028280 | REID RD | Eastern | REID RD | 2024-08-12 | 13:24 | 2024-08-12 | 14:42 | 0.012766 | 0.00016278 | 59 | 4627 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: SD5-069 No. Fuses: 2 Fuse Amp Size: 30amp TIME CLOSED: 14:42 Cause: Wind Weather (wind/rain): Wind Follow up required (select advisory)? No | .
3387 |  | JE24028328 | switch_12669:1 | Western | STRATHMORE | 2024-08-12 | 15:17 | 2024-08-12 | 17:07 | 0.059959 | 0.00054352 | 197 | 21732 | Unplanned | HUMAN ERROR - PROTECTION SETTINGS - INCORRECT/ERROR | REGULATORY INFORMATION Voltage & Device ID: 12669/2 Protection flags (nil where none): na CAUSE: Command sent to Enable correct operational mode (Island) on Gen Set and Gas/Sw 12669 opened and locked out, generator not in service Location: Temp generation (state details when used): no PERFORMANCE DETAIL DNO (number or state No): no Circuit patrolled and type: na Weather (wind/rain): unknown LFI (Y/N + Comments): na Follow up Required (select advisory)? y - incorrect gen set setup Additional fault restoration comments: faultman sent to bypass switch, full power restored. All Gen set controls locked out & wouldn't work. This needs to be re SCADA tested to confirm controls. Changing the mode from Grid to Island shouldn't open the Switch 12669. | .
3388 |  | JE24028363 | CHURCH ST | Western | CHURCH ST | 2024-08-12 | 16:19 | 2024-08-12 | 17:16 | 0.0017136 | 3.0349e-05 | 11 | 621 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | Fuses Location: 7650 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 17:15 Cause: Wind /Branch Weather (wind/rain): Windy Follow up required (select advisory)? | .
3389 |  | JE24028364 | PARK RD | Western | PARK RD | 2024-08-12 | 16:20 | 2024-08-12 | 19:48 | 0.040887 | 0.00019589 | 71 | 14820 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: 7607 No. Fuses: 2 Fuse Amp Size: 15 TIME CLOSED: 19:48 Cause: wind Weather (wind/rain): Follow up required (select advisory)? | .
3390 |  | JE24028370 | LANGDALE | Western | LANGDALE | 2024-08-12 | 17:15 | 2024-08-12 | 17:58 | 0.0080874 | 0.0017271 | 626 | 2931 | Unplanned | VEGETATION - OUTSIDE ZONE | Tinui Sub Coms down No Trippings at Sub, Automated Recloser out of sub showing no Voltage FM sent to Sub to Check situation No Power at Sub Back Feed installed via CB C935 33kV line de-energised FM to patrol line in day light Trees through the lines and lines down at Pole 839600. NDR to follow | .
3391 |  | JE24028372 | MOUNT BRUCE | Western | MOUNT BRUCE | 2024-08-12 | 17:41 | 2024-08-12 | 20:05 | 0.0079642 | 5.5179e-05 | 20 | 2887 | Unplanned | VEGETATION - OUTSIDE ZONE | Isolation from Fuses 7702 Tree through lines pole 450615 2x 10A Fuses replaced after line repairs @20:04 | .
3392 |  | JE24028385 | LONGBUSH | Western | LONGBUSH | 2024-08-12 | 16:20 | 2024-08-13 | 17:58 | 0.17775 | 0.00086631 | 314 | 64426 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: Gladstone CB 945 Protection flags (nil where none): CAUSE: LV lines down past HV Fuses 7097 & Tree through lines past Fuses 8189 Location: FUSES 7097/ 8189 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): High Wind LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Due to high winds multiple faults at same time causing feeder fault. Trees through the lines & two different locations. Fuses left open over night feeder restored. Fuses 7097 were isolated due to trees in the customer owned lines and lines down and there no LV fusing. Customer was happy to be left off overnight and the customer owned network was repaired by PRSL and restored. On livening discovered that Tfr T334 was also faulty. Replaced under 2R 2 2r'S DUE TO TWO JOBS & 2 ndr's | .
3393 |  | JE24028388 | BURNSIDE | Western | BURNSIDE | 2024-08-12 | 16:43 | 2024-08-12 | 18:46 | 0.0013603 | 1.1036e-05 | 4 | 493 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | Fuses Location: 7443 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 18:43 Cause: tree branch Weather (wind/rain): wind Follow up required (select advisory)? | .
3394 |  | JE24028389 | TAVERNER ST | Western | TAVERNER ST | 2024-08-12 | 16:43 | 2024-08-12 | 18:38 | 0.0012671 | 1.1036e-05 | 4 | 459 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: 7536 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 18:38 Cause: Wind/Weather Weather (wind/rain): Windy Follow up required (select advisory)? NIL | .
3395 |  | JE24028391 | PUKETIRO | Western | PUKETIRO | 2024-08-12 | 20:46 | 2024-08-13 | 10:41 | 0.013814 | 1.6554e-05 | 6 | 5007 | Unplanned | VEGETATION - OUTSIDE ZONE | TREE THROUGH LINES DOWN POLE 822514 iSOLATION FOR SAFETY fUSES 7635 oPEN REMOVED & Tagged 20:46 Trees removed and full power restored | .
3396 |  | JE24028422 | HUKANUI | Western | HUKANUI | 2024-08-12 | 18:01 | 2024-08-13 | 15:04 | 0.010458 | 8.2769e-06 | 3 | 3791 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Lines down After Fuses S46 Isolated and left off over night due to SRC needing to be signed before Fixing Scanpower completed work and relivened. | .
3397 |  | JE24028452 | LINTON | Western | LINTON | 2024-08-12 | 19:18 | 2024-08-12 | 21:00 | 0.0045026 | 4.4143e-05 | 16 | 1632 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Floating Conductor at Pole Po3628 Isolated at Fuses H153 Used 2 x 10 amp Fuses and binder | .
3398 |  | JE24028454 | COONOOR | Western | COONOOR | 2024-08-12 | 21:31 | 2024-08-14 | 13:15 | 0.021403 | 3.0349e-05 | 6 | 7758 | Unplanned | VEGETATION - OUTSIDE ZONE | Dead tree fell over through the lines, bought lines down, outside notice zone Off Over Night due to cross country and getting to poles Open LB at Pole P46673 only Tfr T7/376 left off. Site is a shed and customer is happy to leave it off. Crew will return tomorrow to repair the lines. 14/8 Outage to repair lines and close TLB | .
3399 |  | JE24028470 | recloser_1406 | Western | WAITOTARA | 2024-08-12 | 18:18 | 2024-08-13 | 14:28 | 0.19766 | 0.00022072 | 69 | 71642 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV Recloser 1406 Protection flags (nil where none): E/F CAUSE: Trees through the lines and lines down Location: Between Poles 841745 & 841749 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): windy LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: NDR to follow | .
3400 |  | JE24028501 | RONGOMAI | Western | RONGOMAI | 2024-08-12 | 16:36 | 2024-08-13 | 11:52 | 0.08569 | 0.00031176 | 113 | 31059 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11KV CB I32 Protection flags (nil where none): A B C Phase E/F CAUSE: Trees in Lines Location: Poles P06967 & P06963 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Wind & Rain LFI (Y/N + Comments): No Follow up Required (select advisory)? Additional fault restoration comments: Isolated At Links I36/4 Back feed in at Gas/Sw 10846 Isolated at ASBS I35 As well and CB I32 Closed Coming back in morning as span down Trees removed and lines repaired Non scadarised CB I32 - Voltage drop at GMCB 10405-2 at 16:36 this is when this would have tripped | .
3401 |  | JE24028523 | LINDERMANN RD | Eastern | LINDERMANN RD | 2024-08-12 | 21:29 | 2024-08-12 | 22:03 | 0.01734 | 0.00054627 | 198 | 6285 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | REGULATORY INFORMATION Voltage & Device ID: ABS SB1-079 Protection flags (nil where none): Nil CAUSE: jumper failure Location: Pole 388714 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): wind LFI (Y/N + Comments): Nil Follow up Required (select advisory)? No Additional fault restoration comments: Isolation ABS SB1-079 TO RECLOSER 9223. | .
3402 |  | JE24025348 | 44 MARU STREET MOUNT MAUNGANUI TAURANGA | Eastern | FLYOVER | 2024-08-11 | 10:28 | 2024-08-11 | 15:58 | 0.031002 | 9.6564e-05 | 35 | 11237 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove Fuses SC4-715 and 25mm HV cable from O/H. Install new crucifix and connect 185mm HV cable direct to O/H line at pole 856184. Connect other end of cable to RMU 14900/1 (installed under NAPA 107272). Install new 35mm HV cable from Fuse Switch 14900/2 to supply Transformer TC4-146. | .
3403 |  | JE24026014 | 9 WAINGAWA ROAD WAINGAWA CARTERTON | Western | WAINGAWA RD | 2024-08-11 | 8:32 | 2024-08-11 | 11:03 | 0.031566 | 0.00020968 | 76 | 11441 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv cross arms at poles 826470, 826474 and 841040 | .
3404 |  | JE24026186 | 291 HIGH STREET SOLWAY MASTERTON | Western | SOUTH RD CHAPEL | 2024-08-10 | 12:30 | 2024-08-10 | 13:59 | 0.0019533 | 2.2072e-05 | 8 | 708 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace defected cross arms at poles 828763 and 828762 | .
3405 |  | JE24026380 | 2844 STATE HIGHWAY 2 AONGATETE KATIKATI | Eastern | REREATUKAHIA RD | 2024-08-10 | 7:26 | 2024-08-10 | 16:48 | 0.0030687 | 5.5179e-06 | 2 | 1112 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Claymark Katikati Create cable break at pole 206216 and isolate supply to Switchgear 13470/1. Install additional Switch 13470/7 to existing Switchgear 13470. Join cable from Switchgear 354 into 13470/7. Transfer Transformer supply TP789 from Fuses FP376 to Fuses/Sw 13470/5. Remove cable from Pole 201216. and connect through to Tavrida CB 14811/2. Connect Links 14811/4 to line and liven through to 13470/1. 2 x EMAP jumpers do not close job until scada/emap update is complet as more jobs may be created by scada redraw and need confirmation emap jumpers removed Job ready to close when redraw/ emap update is completed | .
3406 |  | JE24028114 | WAIRERE RD | Eastern | WAIRERE RD | 2024-08-10 | 9:05 | 2024-08-10 | 13:01 | 0.0013036 | 5.5179e-06 | 2 | 473 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | ***SAFETY MANAGER ON CLOSURE*** ***RED DEFECT*** Cause: What was replaced? Where was it replaced (pole/TX/pillar box)?TX: 3001133 TX on a pad. Is 2R required? Yes 2R Y - What is the timeframe for repairs? 10/08/2024 Additional Info: Site visit -FM also needed to contact a fitter attended for a 2nd opinion, this needs to be change. FM has taken photos Big 3001133 TX. Fitter has also advised this TX is safe for now. | .
3407 |  | JE24028126 | TAVERNER ST | Western | TAVERNER ST | 2024-08-10 | 14:49 | 2024-08-10 | 16:24 | 0.022827 | 0.00035039 | 127 | 8274 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | 11kV recloser C429 A & B OC Branch found across lines pole 821146 LFI past S338 not found on network email sent to scada team to investigate recloser out of scan take 15:41 for close discrepancy between scada and OMS times, scada 14:50 trip OMS 14:49 so likely scada delayed due to out of scan take 14:49 as trip time | .
3408 |  | JE24028145 | HUNTERVILLE 22KV | Western | HUNTERVILLE 22KV | 2024-08-10 | 20:39 | 2024-08-10 | 22:00 | 0.0053682 | 6.6215e-05 | 24 | 1946 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 997 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 22:00 Cause: Unknown Weather (wind/rain): calm Follow up required (select advisory)?n | .
3409 |  | JE24025850 | 553 NO 2 ROAD TE PUKE TE PUKE | Eastern | ROADS | 2024-08-09 | 9:30 | 2024-08-09 | 12:20 | 0.0065715 | 3.8625e-05 | 14 | 2382 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Clean cables and terminations check earthing | .
3410 |  | JE24025935 | 199 REA ROAD TAHAWAI KATIKATI | Eastern | WHARAWHARA ROAD | 2024-08-09 | 9:01 | 2024-08-09 | 10:01 | 0.020712 | 0.00034487 | 125 | 7507 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install new set of line fault indicators between poles 208328 &208326 | .
3411 |  | JE24025988 | 983 OROUA VALLEY ROAD APITI KIMBOLTON | Western | RANGIWAHIA | 2024-08-09 | 8:46 | 2024-08-09 | 13:10 | 0.038652 | 0.00014623 | 53 | 14010 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace crossarms between and including Pole P05419 and P05431. Reconductor LV from pole P05419 to P05421 | .
3412 |  | JE24026239 | 99 PUKEPAPA ROAD MARTON MARTON | Western | MARTON | 2024-08-09 | 9:00 | 2024-08-09 | 13:50 | 0.11975 | 0.00041384 | 150 | 43404 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Shut 1 - Livening of RMU 3 16145 and installation of new 'Structure 5' between poles 800826 & 447505, Change of circuits TX X1252 | .
3413 |  | JE24027988 | NGATEA | Eastern | NGATEA | 2024-08-09 | 4:09 | 2024-08-14 | 13:24 | 0.42622 | 0.0048116 | 735 | 154485 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 6 Protection flags (nil where none): B - C Ø, O/C E/F CAUSE: Cable fault Location: Between Sw/Gear 13536/1 & TC2259 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): 2408004 Circuit patrolled and type: F3/4, Cursory patrolled Weather (wind/rain): Calm LFI (Y/N + Comments): Yes Follow up Required (select advisory)? Yes Additional fault restoration comments: Cable fault between Sw/Gear 13536/1 and the cable break at TC2259, no customers are left without supply. Moved Z Energy to KPE1 due to loading and voltage issues. Backfed Via KPE3. Cable disconnected at TC2259 HV cable ends and earthed. | .
3414 |  | JE24028042 | WEST END | Western | WEST END | 2024-08-09 | 11:27 | 2024-08-09 | 11:36 | 0.0031956 | 0.00033935 | 123 | 1158 | Unplanned | VEGETATION - INSIDE ZONE | Defect Number 50438114 Transformer Off At 11-26 & Back on At 11-36 To remove Vine from HT side of transformer | .
3415 |  | JE24028082 | PUKETIRO | Western | PUKETIRO | 2024-08-09 | 18:14 | 2024-08-09 | 19:14 | 0.0078455 | 0.00013243 | 48 | 2844 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses 7640 No. Fuses: 2 Fuse Amp Size: 15A TIME CLOSED: 19:13 Cause: Birds Weather (wind/rain): Calm Follow up required (select advisory)?No | .
3416 |  | JE24028232 | WAIRERE RD | Eastern | WAIRERE RD | 2024-08-09 | 9:03 | 2024-08-09 | 10:17 | 0.0073217 | 9.9323e-05 | 36 | 2654 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove vegetation (Vine) from pole H2704. E00144 outage 09/08/2024 0900-1200 | .
3417 |  | JE24025524 | 307 BRUNSWICK ROAD BRUNSWICK WANGANUI | Western | BRUNSWICK | 2024-08-08 | 10:54 | 2024-08-08 | 13:10 | 0.00037531 | 2.759e-06 | 1 | 136 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Transformer Low Voltage X-Arms & Transformer on pole 706855 | .
3418 |  | JE24025847 | 201 BLACK ROAD PAENGAROA TE PUKE | Eastern | ROYDEN DOWNS RD | 2024-08-08 | 8:47 | 2024-08-08 | 14:37 | 0.059036 | 0.0001683 | 61 | 21398 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv/400vt poles ,221725,221727,.replace 11kv/400vt cross arms @ poles 221723,221722 &221726: replace TX TE7087 @ pole 393453 Isolation point @ 14861. Issuer earths @ pole 221721 (221720 side). | .
3419 |  | JE24025851 | 27 FACTORY ROAD BALLANCE PAHIATUA | Western | MANGATAINOKA | 2024-08-08 | 9:45 | 2024-08-08 | 12:50 | 0.00051027 | 2.759e-06 | 1 | 185 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace 11kv Termination arms and TX arms with steel X Arm | .
3420 |  | JE24025855 | 194 MILL ROAD PAEROA PAEROA | Eastern | TIROHIA-KARANGAHAKE | 2024-08-08 | 9:16 | 2024-08-08 | 13:11 | 0.0090725 | 3.8625e-05 | 14 | 3288 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Reconductor 11kv overhead lines between pole's N1247 & N1266 | .
3421 |  | JE24025856 | 471 PIKO ROAD OKOKI URENUI | Western | MAIN RD MOTONUI | 2024-08-08 | 9:55 | 2024-08-08 | 13:16 | 0.014963 | 7.4492e-05 | 27 | 5423 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replacing arms on pole 763914 and replacing Hv fuses on 3417T | .
3422 |  | JE24025859 | 281 OKOKI ROAD URENUI URENUI | Western | MAIN RD MOTONUI | 2024-08-08 | 9:50 | 2024-08-08 | 11:13 | 0.00045596 | 5.5179e-06 | 2 | 165 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 1 x set of pins and insulators at pole 763672 | .
3423 |  | JE24025862 | 105 OLD TE AROHA ROAD TE POI MATAMATA | Eastern | GORDON | 2024-08-08 | 10:00 | 2024-08-08 | 13:10 | 0.019773 | 0.00010484 | 38 | 7167 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv conductor between Poles F1148 and F12745 | .
3424 |  | JE24025863 | 385 HEADS ROAD CASTLECLIFF WANGANUI | Western | HEADS RD | 2024-08-08 | 18:35 | 2024-08-08 | 21:57 | 0.00055841 | 2.759e-06 | 1 | 202 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 400V switchgear for 3040W | .
3425 |  | JE24025912 | 475 MOUNT STEWART HALCOMBE ROAD HALCOMBE FEILDING | Western | MT STEWART | 2024-08-08 | 8:46 | 2024-08-08 | 15:37 | 0.2589 | 0.00062904 | 228 | 93841 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Aspludh to complete vegetation between poles P18493 and P21709. 3x sites. | .
3426 |  | JE24025916 | 442 KARERE ROAD TIAKITAHUNA PALMERSTON NORTH | Western | BAINESSE | 2024-08-08 | 8:30 | 2024-08-08 | 13:47 | 0.011369 | 3.5867e-05 | 13 | 4121 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles and hardware between P43261 - P31863. Install TEMP 142 11kV line links at pole P31864. | .
3427 |  | JE24025920 | 46 YORK ROAD MIDHIRST STRATFORD | Western | CLOTON RD NORTH | 2024-08-08 | 9:05 | 2024-08-08 | 14:25 | 0.067871 | 0.00021244 | 77 | 24600 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install new Entec structure 12733 at site 466761. Remove Fuses 12351 & Remove ABS 12349 | .
3428 |  | JE24025921 | 1791 TAIRUA WHITIANGA ROAD COROGLEN WHITIANGA | Eastern | COROGLEN | 2024-08-08 | 9:45 | 2024-08-08 | 17:25 | 0.090075 | 0.00019589 | 71 | 32648 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV Poles W1763 & W1774 Tairua/Whitianga Rd | .
3429 |  | JE24025995 | 365 TREMAINE AVENUE TAKARO PALMERSTON NORTH | Western | TREMAINE AVE | 2024-08-08 | 23:01 | 2024-08-09 | 8:39 | 0.12773 | 0.00022072 | 80 | 46295 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace switch 401/402/403 with switch 10920. Ran Late due to Rain and weather Conditions At sw/Gear 10920-40 & 10920-1 the phasing is Wrong and Omexom will return to Fix The cables were put into wrong Units 10920/1 & 10920/3 Photos and paperwork to be put in by Omexom | .
3430 |  | JE24026001 | 128 BRUNSWICK ROAD BRUNSWICK WANGANUI | Western | BRUNSWICK | 2024-08-08 | 9:08 | 2024-08-08 | 15:01 | 0.0066965 | 1.9313e-05 | 7 | 2427 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace all 11KV X-arms on poles 782757 - X2514 & 782763 - X2511 | .
3431 |  | JE24026774 | 47 OHAWE ROAD TOKAORA HAWERA | Western | GLOVER RD WEST | 2024-08-08 | 9:01 | 2024-08-08 | 16:00 | 0.094889 | 0.00058214 | 152 | 34393 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 1. Replace Poles - 721916, 721924, 721926, 851281, 721943, 721949, 721951, 721959, 846037 2. Replace Crossarms â€“ 440034, 846038 3. 11kV Reconductor Between poles 440122 & 721916 | .
3432 |  | JE24027021 | 14 POHUTUKAWA DRIVE TOKOROA TOKOROA | Eastern | RATA ST BAIRD ROAD | 2024-08-08 | 8:31 | 2024-08-08 | 11:25 | 0.05565 | 0.00032004 | 116 | 20170 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9189-1/2/3 & 4 | .
3433 |  | JE24027829 | PUKETIRO | Western | PUKETIRO | 2024-08-08 | 9:24 | 2024-08-08 | 10:15 | 0.0018292 | 3.5867e-05 | 13 | 663 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Check if JE24027830 & JE24027834 Related Faultman found the jumper had come out of the bottom of the Fuses at Fuses 7855, line was isolated at Fuses 7855 to reattach the jumper. | .
3434 |  | JE24027884 | DAIRY FACTORY | Western | DAIRY FACTORY | 2024-08-08 | 12:05 | 2024-08-08 | 13:05 | 0.014675 | 0.00024279 | 88 | 5319 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faultman found insulator on pole 812940 had almost broken off the cross arm, line was isolated at Links 11169/6 & ABS 11169/1 to refit on cross arm, Faultman will defect cross arm to have them replaced under a shut down. | .
3435 |  | JE24027898 | CROFTON | Western | CROFTON | 2024-08-08 | 13:20 | 2024-08-08 | 13:46 | 0.0006948 | 2.759e-05 | 10 | 252 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Faultman isolated transformer X225 for safety to repair LV joint on LV bushing. | .
3436 |  | JE24027974 | KUMENGA | Western | KUMENGA | 2024-08-08 | 19:46 | 2024-08-08 | 22:00 | 0.00036985 | 2.759e-06 | 1 | 134 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses 7302 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 22:00 Cause: Magpies Weather (wind/rain): Rain Follow up required (select advisory)? No | .
3437 |  | JE24024875 | 2 GRAVATT RD PAPAMOA | Eastern | GRAVATT RD | 2024-08-07 | 23:00 | 2024-08-08 | 3:25 | 0.034423 | 0.00012967 | 47 | 12477 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Disconnect 3c 35mmÂ² Al. cable from switch 9139/2, relocate cable and connect to TEMP151/2 | .
3438 |  | JE24025332 | 158 RANGATIRA ROAD HUNTERVILLE HUNTERVILLE | Western | PUTORINO | 2024-08-07 | 9:01 | 2024-08-07 | 13:12 | 0.036011 | 0.00014347 | 52 | 13052 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Defected Poles & X-Arms between 806922 & 806969 | .
3439 |  | JE24025448 | 48 WHANGAPOUA ROAD COROMANDEL COROMANDEL | Eastern | KAPANGA ROAD | 2024-08-07 | 23:16 | 2024-08-08 | 0:30 | 0.033061 | 0.00044419 | 161 | 11983 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Coromandel 11kV Generation Project ,enabling works . On 5/8/24 Disconnect Cable From CB7 to Pole V13061 At Pole V13061 for clearance to install new CB9 onto existing bus on next day. On 7/8/24 Reconnect Cable From CB7 to Pole V13061 At Pole V13061 & restore network to normal. | .
3440 |  | JE24025456 | 81 GROVE ROAD ASHHURST PALMERSTON NORTH | Western | POHANGINA | 2024-08-07 | 8:46 | 2024-08-07 | 12:04 | 0.091025 | 0.00045799 | 166 | 32993 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Perform regulator maintenance at 10081 | .
3441 |  | JE24025486 | 64 DOWNS ROAD HIMATANGI FOXTON | Western | OROUA DOWNS | 2024-08-07 | 9:18 | 2024-08-07 | 11:52 | 0.0072425 | 4.6902e-05 | 17 | 2625 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV crossarms on poles P23615, P23616, P23621 & P05600. | .
3442 |  | JE24025489 | 1171 PAHIATUA PONGAROA ROAD PAHIATUA PAHIATUA | Western | RUAWHATA | 2024-08-07 | 9:45 | 2024-08-07 | 14:16 | 0.019456 | 7.1733e-05 | 26 | 7052 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace 11kv cross arms install 11kv ground stays at pole P47299 | .
3443 |  | JE24025491 | 114 MAKOURA ROAD APITI APITI | Western | APITI | 2024-08-07 | 12:00 | 2024-08-07 | 12:42 | 0.0014932 | 3.5867e-05 | 13 | 541 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Resag HV conductor span between P03570 and P03571 | .
3444 |  | JE24025492 | 1298 MAIN SOUTH ROAD RANGIWAHIA KIMBOLTON | Western | APITI | 2024-08-07 | 9:52 | 2024-08-07 | 11:59 | 0.00034809 | 2.759e-06 | 1 | 126 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | T5/1 isolation and earth to replace LV span between Poles P01790 and P01791 | .
3445 |  | JE24025723 | 34 MILL ROAD PAEROA PAEROA | Eastern | TIROHIA-KARANGAHAKE | 2024-08-07 | 9:15 | 2024-08-07 | 12:08 | 0.0066545 | 3.8625e-05 | 14 | 2412 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Reconductor 11kv overhead lines between Pole's N1240 & N1247 | .
3446 |  | JE24025785 | 491 PAPAMOA BEACH ROAD PAPAMOA BEACH TAURANGA | Eastern | PAPAMOA BEACH WEST | 2024-08-07 | 8:53 | 2024-08-07 | 14:19 | 0.19806 | 0.00061525 | 223 | 71789 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install and commission new 11kv ENTEC sectionaliser # 14873 on pole 421446. | .
3447 |  | JE24025792 | 309 BENNER ROAD PUKEHINA TE PUKE | Eastern | ROTOEHU | 2024-08-07 | 9:31 | 2024-08-07 | 12:54 | 0.0039179 | 1.9313e-05 | 7 | 1420 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Clean hv cables and terminations, check earthing | .
3448 |  | JE24025794 | 1223 TAIRUA ROAD WHANGAMATA WHANGAMATA | Eastern | OPOUTERE | 2024-08-07 | 9:00 | 2024-08-07 | 16:45 | 0.26142 | 0.00056283 | 204 | 94754 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | String fibre between poles R0785 & 422587/424557 | .
3449 |  | JE24025938 | 47 OHAWE ROAD TOKAORA HAWERA | Western | KETEMARAE RD | 2024-08-07 | 9:01 | 2024-08-07 | 15:16 | 0.13989 | 0.00037246 | 135 | 50704 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 1. Replace Poles â€“ 721969, 721968, 840266 â€“ Agtrans Required for pole removal 846040, 723004, 732005, 721979, 721980 2. Replace Crossarms â€“ 846039, 3. LV Reconductor â€“ Between 440108 to 851281 ( 4 Spans of PVC KUTU) | .
3450 |  | JE24027707 | BROOKLANDS 7 | Western | BROOKLANDS 7 | 2024-08-07 | 6:53 | 2024-08-07 | 10:42 | 0.031702 | 0.00028969 | 105 | 11490 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV, Rec 12353 Protection flags (nil where none): E/F, B phase CAUSE: Cracked Insulator Location: 702077 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Y / Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): Yes. Operated correctly but not useful in this case as before tripped recloser. Follow up Required (select advisory)? No Additional fault restoration comments: Line Down called in by member of public. Line broke at Insulator and crossarm burnt. HV crossarm & hardware replaced & line repaired SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3451 |  | JE24027718 | ASHWORTH ST | Eastern | ASHWORTH ST | 2024-08-07 | 8:28 | 2024-08-07 | 9:25 | 0.00031116 | 5.5179e-06 | 2 | 113 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses FC4265 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 09:24 Cause: Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? No | .
3452 |  | JE24027772 | 24 STRASBOURGE STREET, MARTINBOROUGH | Western | COLOGNE ST | 2024-08-07 | 14:43 | 2024-08-07 | 20:45 | 0.38958 | 0.001076 | 390 | 141206 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB C890 Protection flags (nil where none): Nil feeder did not trip CAUSE: Car vs Pole Location: pole 813262 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: n Weather (wind/rain): calm LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Line was isolated at ABS's S510 & S511 to replace pole. 11m Busk Pole installed 20:45 | .
3453 |  | JE24027797 | MAKIRIKIRI | Western | MAKIRIKIRI | 2024-08-07 | 17:12 | 2024-08-07 | 18:57 | 0.010992 | 0.00011864 | 43 | 3984 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | 2 x blown fuses at 586, patrolled line, off loaded TFR X1125 as there had been a fault off that TFR earlier in the day, Reloaded and Re-livened Fuses 586, and closed Fuses to TFR X1125 at 18:57, full power restored, No Fault found, Possible bird strike Fuses Location: 586 No. Fuses: 2 Fuse Amp Size: 15 TIME CLOSED: 18:43 Cause: unknown Weather (wind/rain): calm Follow up required (select advisory)?n | .
3454 |  | JE24027804 | MANAIA | Western | MANAIA | 2024-08-07 | 21:42 | 2024-08-07 | 22:36 | 0.0050185 | 9.3805e-05 | 34 | 1819 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Firecomms Attending F048010812 1 x Fuse Barrel Burnt out and burning at Fuses MA521, Faultman went to reload and re-liven and the bottom of the DDO Broke off, back feed put in place Isolated at ABS 6711, 8762/1 & Links All 3 DDO's Replaced at Pole 718558, Full power restored, feeder restored to normal config | .
3455 |  | JE24027816 | COLVILLE | Eastern | COLVILLE | 2024-08-07 | 20:48 | 2024-08-07 | 22:34 | 0.14077 | 0.0016995 | 616 | 51024 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec RP15 Protection flags (nil where none): A,B,C O/C CAUSE: Unknown Sectionalised nothing found, Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Calm LFI (Y/N + Comments): never operated Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3456 |  | JE24027818 | THAMES COAST | Eastern | THAMES COAST | 2024-08-07 | 21:29 | 2024-08-08 | 3:54 | 0.086521 | 0.00048282 | 175 | 31360 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV Links 13541 Protection flags (nil where none): nil CAUSE: Car V Pole Location: 263584 Temp generation (state details when used): no PERFORMANCE DETAIL DNO (number or state No): no Circuit patrolled and type: Weather (wind/rain): fine LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: New 11m Busk Installed SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3457 |  | JE24020361 | 73 LOWER WAIAU ROAD WAVERLEY WAVERLEY | Western | WAITOTARA | 2024-08-06 | 9:00 | 2024-08-06 | 11:27 | 0.01294 | 8.8287e-05 | 32 | 4690 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace defected 11KV X-Arm on pole 781375 | .
3458 |  | JE24025316 | 1 NURSERY ROAD HOMEBUSH MASTERTON | Western | CHURCH ST | 2024-08-06 | 17:31 | 2024-08-06 | 18:00 | 0.00024403 | 8.2769e-06 | 3 | 88 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace blown lightening arrester at pole 829299 | .
3459 |  | JE24025322 | 175 WAIOMOU ROAD TAPAPA TIRAU | Eastern | RANGITANUKU RD | 2024-08-06 | 9:15 | 2024-08-06 | 11:05 | 0.00060697 | 5.5179e-06 | 2 | 220 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | at pole 489591 replace 11kv lightning arrestors upgrade earth bank to Powerco standard | .
3460 |  | JE24025330 | 535 OKOKI ROAD URENUI URENUI | Western | MAIN RD MOTONUI | 2024-08-06 | 9:46 | 2024-08-06 | 14:40 | 0.059414 | 0.0002014 | 73 | 21535 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace defective HV arms on pole 763692 , 763723 , 763724 , 763725 , 763726 , 763727 | .
3461 |  | JE24025345 | 105 OLD TE AROHA ROAD TE POI MATAMATA | Eastern | GORDON | 2024-08-06 | 8:46 | 2024-08-06 | 14:19 | 0.032159 | 9.6564e-05 | 35 | 11656 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Poles F1155, F1154, F1152, F1150, 878539, F1149 and F1148 | .
3462 |  | JE24025353 | 1164 NO 3 ROAD TE PUKE TE PUKE | Eastern | MANOEKA RD | 2024-08-06 | 9:16 | 2024-08-06 | 10:52 | 0.01242 | 0.00012967 | 47 | 4502 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | clean terminations check connections and earthing | .
3463 |  | JE24025355 | 640 WAIHI WHANGAMATA ROAD WAIHI WAIHI | Eastern | WAIHI-WHANGAMATA 33KV | 2024-08-06 | 7:00 | 2024-08-06 | 17:07 | 4.4702 | 0.010319 | 3715 | 1620258 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Northpower - Helicopter installing fibre between poles WHIWGM097 and P13735/P1572. Replace cross arms on TP572. Downer - Replacing crossarms on poles WHIWGM086, 097, 098, 099, 103, 104, 108. NPE Tech - Defects on poles R12386 , R12383 , R12382 , R12384 . Temp generation installed on TC4848 - Outside work area . | .
3464 |  | JE24025356 | 99 TOWN POINT ROAD MAKETU TE PUKE | Eastern | MAKETU | 2024-08-06 | 12:30 | 2024-08-06 | 14:08 | 0.021389 | 0.00021796 | 79 | 7753 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | clean terminations and checking connections and earthing | .
3465 |  | JE24025357 | 983 OROUA VALLEY ROAD APITI KIMBOLTON | Western | APITI | 2024-08-06 | 10:15 | 2024-08-06 | 15:05 | 0.045509 | 0.00015726 | 57 | 16495 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace crossarms between and including pole P05414 and P05421, Replace ABS P60 & P62 (numbers to remain) | .
3466 |  | JE24025360 | 2 CENTRAL STREET PUTARURU PUTARURU | Eastern | BENT ST | 2024-08-06 | 8:32 | 2024-08-06 | 15:24 | 0.038654 | 9.3805e-05 | 34 | 14010 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace rusted TC3723 with a refurbished 300kVA GMT | .
3467 |  | JE24025367 | 2550 STATE HIGHWAY 27 TAHUNA | Eastern | PATETONGA | 2024-08-06 | 9:48 | 2024-08-06 | 13:56 | 0.0027323 | 1.1036e-05 | 4 | 990 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | remove TC2221 to gain access to replace LV 3m arm at pole K1225-replace 4oov term arm | .
3468 |  | JE24025427 | 129 BURMA HILL ROAD RANGIWAEA WANGANUI | Western | PARAPARA | 2024-08-06 | 9:46 | 2024-08-06 | 13:16 | 0.0092657 | 4.4143e-05 | 16 | 3358 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Repair 11kv cable crutch @ pole 785237 and install new crucifix. | .
3469 |  | JE24025431 | 4325 WAITOTARA VALLEY ROAD NGAMATAPOURI WANGANUI | Western | WAITOTARA | 2024-08-06 | 9:16 | 2024-08-06 | 16:21 | 0.068118 | 0.00016002 | 58 | 24690 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 780559 & re conductor to TX Pole X2991, cut trees between 841742 & 780511, Replace defected pole 844672 | .
3470 |  | JE24025447 | 209 MILL ROAD PAEROA PAEROA | Eastern | RAILWAY ST | 2024-08-06 | 9:45 | 2024-08-06 | 15:02 | 0.0060412 | 1.9313e-05 | 7 | 2190 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE 11KV POLE'S N13247,858341,N13248,N13249,N13250 | .
3471 |  | JE24025473 | 201 BLACK ROAD PAENGAROA TE PUKE | Eastern | ROYDEN DOWNS RD | 2024-08-06 | 9:06 | 2024-08-06 | 15:57 | 0.069077 | 0.0001683 | 61 | 25037 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv/400vt poles ,221715,221720,221721.replace 11kv/400vt cross arms @ poles 221718 & 221719: Isolation point @ 14861. Issuer earths @ pole 221713 (221714 side). | .
3472 |  | JE24025479 | 492 KARERE ROAD TIAKITAHUNA PALMERSTON NORTH | Western | BAINESSE | 2024-08-06 | 8:46 | 2024-08-06 | 14:31 | 0.012373 | 3.5867e-05 | 13 | 4485 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles and hardware between P43270 - P43261. | .
3473 |  | JE24027591 | WAIMAPU | Eastern | WAIMAPU | 2024-08-06 | 5:11 | 2024-08-06 | 7:43 | 0.042807 | 0.00028141 | 102 | 15516 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV recloser 14473 Protection flags (nil where none): EF CAUSE: lines down- loose connection failed OH Location: pole 211184 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Lines repaired, Power restored 07:43 Hrs SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3474 |  | JE24027644 | PIHAMA | Western | PIHAMA | 2024-08-06 | 11:09 | 2024-08-06 | 12:31 | 0.00022618 | 2.759e-06 | 1 | 82 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 12052 No. Fuses: 3 Fuse Amp Size: 2A TIME CLOSED: 12:30 Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)? No | .
3475 |  | JE24027665 | KUMENGA | Western | KUMENGA | 2024-08-06 | 14:23 | 2024-08-06 | 15:03 | 0.00011025 | 2.759e-06 | 1 | 40 | Unplanned | WILDLIFE - BIRD | Fuses Location: 7302 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 15:03 Cause: Bird Strike Weather (wind/rain): calm Follow up required (select advisory)?n | .
3476 |  | JE24027688 | CHESTER RD | Western | CHESTER RD | 2024-08-06 | 17:11 | 2024-08-06 | 20:40 | 0.033669 | 0.0011891 | 431 | 12204 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11KV CB C834 Protection flags (nil where none): None - Feeder did not trip CAUSE: Car vs pole Location: 826283 11m Busk Installed Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: n Weather (wind/rain): calm LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: NOC Controller opened CB C834 as Faultman reported lines were low after car hit pole, line was isolated at ABS S348 and feeder was restored. 2r left Open to repair Street Light Circuit 7/08/24 2R - Street light circuit back up and running. | .
3477 |  | JE24024835 | 157 BLACK ROAD PAENGAROA TE PUKE | Eastern | ROYDEN DOWNS RD | 2024-08-05 | 8:54 | 2024-08-05 | 14:35 | 0.057434 | 0.0001683 | 61 | 20817 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv/400vt poles 221708,221710,221712,221713 &221714: Isolation point @ 14861. Issuer earths @ pole 221708(385944 side). | .
3478 |  | JE24025152 | 364 Okoroire Road Tirau | Eastern | OKOROIRE | 2024-08-05 | 8:46 | 2024-08-05 | 11:15 | 0.0024707 | 1.6554e-05 | 6 | 896 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE DEFECT DOUBLE 11KV PIN ARMS AT POLE D1720 | .
3479 |  | JE24025187 | 6253 STATE HIGHWAY 1 MANGAWEKA MANGAWEKA | Western | MANGAWEKA | 2024-08-05 | 10:51 | 2024-08-05 | 13:03 | 0.0036377 | 2.759e-05 | 10 | 1319 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Transformer X1641. Starting Late estimated 10:30 | .
3480 |  | JE24025189 | 859 HALCOMBE ROAD HALCOMBE FEILDING | Western | MT STEWART | 2024-08-05 | 8:59 | 2024-08-05 | 11:56 | 0.010734 | 6.0697e-05 | 22 | 3891 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Perform regulator maintenance at 10112 | .
3481 |  | JE24025190 | 13667 ROUTE 52 TIRAUMEA EKETAHUNA | Western | BROOKLANDS | 2024-08-05 | 9:41 | 2024-08-05 | 14:07 | 0.017636 | 6.6215e-05 | 24 | 6392 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace pole P10787 and replace 11kv conductor from pole P10787 to P15323 | .
3482 |  | JE24025209 | 2 HUIRAU ROAD TURUA THAMES | Eastern | HAURAKI RD | 2024-08-05 | 9:05 | 2024-08-05 | 14:21 | 0.038304 | 0.00012139 | 44 | 13883 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv pole O1135, Re-Sag/Straighten poles 385580,O1150,877248,321717,O1098. | .
3483 |  | JE24025258 | 1047M PURANGI ROAD COOKS BEACH WHITIANGA | Eastern | PURANGI | 2024-08-05 | 10:01 | 2024-08-05 | 14:03 | 0.018338 | 8.001e-05 | 29 | 6647 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Run AP for Tree cutters to work in area poles 486761/486644 to 485772/485564 vicinity | .
3484 |  | JE24025300 | 85 JUNCTION ROAD PAEROA PAEROA | Eastern | TIROHIA-KARANGAHAKE | 2024-08-05 | 8:35 | 2024-08-05 | 14:01 | 0.0017986 | 5.5179e-06 | 2 | 652 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Rusty LV Box on TC4172 | .
3485 |  | JE24025440 | 48 WHANGAPOUA ROAD COROMANDEL COROMANDEL | Eastern | KAPANGA ROAD | 2024-08-05 | 23:04 | 2024-08-05 | 23:54 | 0.022097 | 0.00044419 | 161 | 8009 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Coromandel 11kV Generation Project ,enabling works . On 5/8/24 Disconnect Cable From CB7 to Pole V13061 At Pole V13061 for clearance to install new CB9 onto existing bus on next day. On 7/8/24 Reconnect Cable From CB7 to Pole V13061 At Pole V13061 & restore network to normal. | .
3486 |  | JE24027056 | 2 CLIVE STREET HAWERA HAWERA | Western | TAWHITI RD | 2024-08-05 | 9:03 | 2024-08-05 | 13:33 | 0.067978 | 0.00062353 | 226 | 24639 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Urgent outage to replace leaking tx C4030. Also to replace old Dominion DDO's as they are dropping open. | .
3487 |  | JE24027394 | 221 BROWN ROAD, BRIXTON, WAITARA, 4382 | Western | DEVON RD | 2024-08-05 | 5:41 | 2024-08-05 | 5:56 | 4.1936e-05 | 2.759e-06 | 1 | 15 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 6693 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 05-56 Cause: Unknown Weather (wind/rain): Rain Follow up required (select advisory)? | .
3488 |  | JE24027395 | KETEMARAE RD | Western | KETEMARAE RD | 2024-08-05 | 5:00 | 2024-08-05 | 6:22 | 0.00022679 | 2.759e-06 | 1 | 82 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Replace Insulator at Pole 721558 Isolated at Fuses 6378 | .
3489 |  | JE24027397 | AWAITI | Eastern | AWAITI | 2024-08-05 | 15:03 | 2024-08-05 | 16:57 | 0.00062573 | 5.5179e-06 | 2 | 227 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation:11kV Fuses FC2396 CAUSE: DTX TC4635 Failed 4Ohm on Yellow Phase Loop Test 0.25 on Red & Blue. Transformer Replaced. Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: Weather (wind/rain): Follow up required (select advisory)? Additional fault restoration comments: | .
3490 |  | JE24027441 | WAITOTARA | Western | WAITOTARA | 2024-08-05 | 7:15 | 2024-08-05 | 9:35 | 0.0050069 | 3.5867e-05 | 13 | 1815 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 684 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 09:34 Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)? No | .
3491 |  | JE24027471 | WESTMERE GLADSTONE | Western | WESTMERE GLADSTONE | 2024-08-05 | 11:20 | 2024-08-05 | 11:59 | 0.00021198 | 5.5179e-06 | 2 | 77 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolate at Fuses 7853 to repair jumper at Pole 855034 | .
3492 |  | JE24027481 | MANGOREWA | Eastern | MANGOREWA | 2024-08-05 | 13:23 | 2024-08-05 | 14:08 | 0.0003726 | 8.2769e-06 | 3 | 135 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Lead off DTX TE6-199 Transformer Bushing Protection flags (nil where none): nil CAUSE: Deterioration Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3493 |  | JE24027494 | MATAROA A | Western | MATAROA A | 2024-08-05 | 12:35 | 2024-08-05 | 16:06 | 0.016187 | 0.00011036 | 40 | 5867 | Unplanned | THIRD PARTY INTERFERENCE - OVERHEAD CONTACT | Cause: Helicopter contacted lines bringing one line down Isolation: Fuses 2611 What was replaced? 40mtrs of conductor & 8x tension sleeves Where was it replaced (pole/TX/pillar box)? Pole 785926 Additional Info: | .
3494 |  | JE24027068 | SIMPSON RD | Eastern | SIMPSON RD | 2024-08-04 | 7:31 | 2024-08-04 | 10:30 | 0.13778 | 0.00076699 | 278 | 49938 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace blown surge arrestors at pole# 249660 install temp fuses 25 between poles 249660 & 499839 | .
3495 |  | JE24027323 | MAIN RD MOTONUI | Western | MAIN RD MOTONUI | 2024-08-04 | 9:53 | 2024-08-04 | 12:21 | 0.0024444 | 1.6554e-05 | 6 | 886 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: 4097T No. Fuses: 2 Fuse Amp Size: TIME CLOSED: Cause: Weather (wind/rain): Follow up required (select advisory)? This was a No Go Returning in Morning once owner has removed all His gear from around Pole 04/08/2024 Transformer OFF LINE on E Map Transformer replaced, power restored 12:20 | .
3496 |  | JE24025036 | 17A BRIDGE STREET BULLS BULLS | Western | SANSONW40-OHAKEA3132 33KV | 2024-08-03 | 9:00 | 2024-08-03 | 9:52 | 0.00027052 | 5.5179e-06 | 2 | 98 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace defect crossarm at pole 803641 | .
3497 |  | JE24025271 | 11 KARORO ROAD CASTLECLIFF WANGANUI | Western | BEACH RD | 2024-08-03 | 8:34 | 2024-08-03 | 11:31 | 0.00048654 | 2.759e-06 | 1 | 176 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Shut down 11kv metering unit to treat rust and replace 11kv fuses in metering unit. | .
3498 |  | JE24027261 | POHANGINA | Western | POHANGINA | 2024-08-03 | 0:03 | 2024-08-03 | 1:49 | 0.0078803 | 7.4492e-05 | 27 | 2856 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: F19 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 01:48 hrs Cause: Unk Weather (wind/rain): Calm Follow up required (select advisory)? | .
3499 |  | JE24027264 | MCCABE ROAD | Eastern | MCCABE ROAD | 2024-08-03 | 6:07 | 2024-08-03 | 7:11 | 0.00069904 | 1.1036e-05 | 4 | 253 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: TC178 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 07:10 Cause: bird strike suspected Weather (wind/rain): Follow up required (select advisory)? | .
3500 |  | JE24027265 | SEAWARD COAST | Western | SEAWARD COAST | 2024-08-03 | 6:53 | 2024-08-03 | 8:23 | 0.0086951 | 9.6564e-05 | 35 | 3152 | Unplanned | WILDLIFE - BIRD | Fuses Location: 8484 No. Fuses: 2 Fuse Amp Size: 20A TIME CLOSED: 08:22 Cause: Birdstrike Weather (wind/rain): Calm Follow up required (select advisory)? N | .
3501 |  | JE24027269 | 186 WEST STREET, FEILDING, 4702 | Western | MAKINO | 2024-08-03 | 10:27 | 2024-08-03 | 14:30 | 0.22026 | 0.00090494 | 328 | 79835 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Notified by Police of damaged pole Pole P21690 Isolated at ABS's M50, J22, & O6 Pole Replaced | .
3502 |  | JE24027297 | TAIHAPE B 33KV | Western | TAIHAPE B 33KV | 2024-08-03 | 11:40 | 2024-08-03 | 21:46 | 0.28396 | 0.0024638 | 893 | 102923 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | CB 4 Open due to report from Fire coms reporting low hanging lines GCB 4537/1 failed to open Isolated at ABS's 1167 & 523 Pole Replaced Car V Pole | .
3503 |  | JE24027314 | GLOVER RD EAST | Western | GLOVER RD EAST | 2024-08-03 | 17:43 | 2024-08-04 | 11:12 | 0.23019 | 0.0030514 | 1068 | 83434 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 11 Protection flags (nil where none): A,B, C Ph O/C CAUSE: Bird strike Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Back Feed installed via Sw/Gear 12746/4 up to Recloser 6728 LFI's at Sw/Gear 12536 found active Sw/Gear 12536/1 Opened CB 11 Closed LFI's at Sw/Gear 12199/1&2 found active Sw/Gear 12199/1 Opened Arcing at Links 12009 noticed Back Feed installed Via ABS CA356 up to ABS CA901 Back Feed install via ABS 6814 Seagull found near Fuses 12034 All power restored Cable found blown away Pole 846555 to Sw/Gear 12536/1 FM advised Cable clear of lines Arcing stopped at Links with low load Back feeds left in place, FM to return in morning. 04/08/2024 Work area Isolated & Earthed Repairs made at Links 12009 & Cable break made at Pole 846555 Power restored Damaged cable to be repaired under planned switching Cable DNO 2408001 Cable to be repaired under planned switching 2R Closed SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3504 |  | JE24027319 | RUAWHATA | Western | RUAWHATA | 2024-08-03 | 18:37 | 2024-08-03 | 20:04 | 0.0016764 | 1.9313e-05 | 7 | 608 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Q87 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 20-04 Cause: Unknown Weather (wind/rain): Cold Follow up required (select advisory)? | .
3505 |  | JE24027326 | WAIMAPU | Eastern | WAIMAPU | 2024-08-03 | 20:27 | 2024-08-03 | 23:28 | 0.00099868 | 5.5179e-06 | 2 | 362 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: TE4-208 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 23:28 Cause: Unknown, lines patrolled Weather (wind/rain): Calm Follow up required (select advisory)? No | .
3506 |  | JE24024800 | 19 MANUKA STREET LANSDOWNE MASTERTON | Western | MIRO ST | 2024-08-02 | 9:16 | 2024-08-02 | 12:03 | 0.046139 | 0.0002759 | 100 | 16723 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace brackets on 11kv crucifix, to change radius of 11kv leads from breakout add in some extra cable brackets. | .
3507 |  | JE24024906 | 346 AWAWA ROAD HALCOMBE FEILDING | Western | WAITUNA | 2024-08-02 | 8:50 | 2024-08-02 | 14:58 | 0.010156 | 2.759e-05 | 10 | 3681 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Switching for Asplundh vegetation contractor to complete works between P07647 and P07625 | .
3508 |  | JE24024969 | 2469 MANGAOHANE ROAD NGAMAHANGA TAIHAPE | Western | MOAWHANGO | 2024-08-02 | 10:00 | 2024-08-02 | 12:47 | 0.0046139 | 2.759e-05 | 10 | 1672 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | SHUT 9 Resag HV Line both sides of pole 786896. | .
3509 |  | JE24024982 | 60 BRIDGE STREET BULLS BULLS | Western | PAREWANUI | 2024-08-02 | 9:16 | 2024-08-02 | 14:45 | 0.11455 | 0.00034763 | 126 | 41519 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install LV 400Amp Disconnectors at pole replace defect pole 803418 | .
3510 |  | JE24025017 | 268 MANGAWHERO ROAD PATETONGA MORRINSVILLE | Eastern | KAIHERE | 2024-08-02 | 9:02 | 2024-08-02 | 12:17 | 0.0021595 | 1.1036e-05 | 4 | 783 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To carry out oil leak repair works on transformer TC2939 | .
3511 |  | JE24025022 | 113 KOPANE ROAD RONGOTEA PALMERSTON NORTH | Western | KOPANE | 2024-08-02 | 8:46 | 2024-08-02 | 11:47 | 0.0069854 | 3.8625e-05 | 14 | 2532 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole and all hardware including 30kVA transformer at P20888/P20889. | .
3512 |  | JE24025043 | 296 STRANGE ROAD OTWAY TE AROHA | Eastern | SPRINGDALE | 2024-08-02 | 8:47 | 2024-08-02 | 15:15 | 0.017151 | 4.4143e-05 | 16 | 6217 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | PQI Case 8871 - To replace pole C2708 and install new 30kVA transformer | .
3513 |  | JE24025045 | 461 PUKEHINA PARADE PUKEHINA TE PUKE | Eastern | TAINUI | 2024-08-02 | 9:18 | 2024-08-02 | 11:03 | 0.070133 | 0.00068974 | 250 | 25420 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace H.V cross arms at poles 324891 & 380066 | .
3514 |  | JE24025124 | 165 WAIKAKA ROAD PATETONGA MORRINSVILLE | Eastern | PATETONGA | 2024-08-02 | 9:00 | 2024-08-02 | 14:26 | 0.0063043 | 1.9313e-05 | 7 | 2285 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | SHUTDOWN FOR FRANKLIN TREES CLEARING TREES FROM OVERHEAD LINES between poles 480437 - K13213 | .
3515 |  | JE24025134 | 105 OLD TE AROHA ROAD TE POI MATAMATA | Eastern | GORDON | 2024-08-02 | 9:21 | 2024-08-02 | 15:55 | 0.040158 | 0.00010484 | 38 | 14555 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles F12745, F12743, F1150 and 878540 | .
3516 |  | JE24025169 | 1060 TAIRUA ROAD WHANGAMATA WHANGAMATA | Eastern | OPOUTERE | 2024-08-02 | 9:30 | 2024-08-02 | 15:00 | 0.18755 | 0.00056835 | 206 | 67977 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install draw rope with drone between poles R0797 & R0798 | .
3517 |  | JE24025193 | 7648 STATE HIGHWAY 2 KARANGAHAKE PAEROA | Eastern | TIROHIA-KARANGAHAKE | 2024-08-02 | 9:45 | 2024-08-02 | 13:51 | 0.0065314 | 2.759e-05 | 10 | 2367 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To open HV jumper on Pole N2122 via liveline methods GB-40 to allow for HV and LV arm change on pole N1719 and reconnect after work completed | .
3518 |  | JE24027147 | TIROHIA-KARANGAHAKE | Eastern | TIROHIA-KARANGAHAKE | 2024-08-02 | 0:45 | 2024-08-02 | 3:31 | 0.046679 | 0.00033383 | 121 | 16919 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11KV SECT. 14235/2 Protection flags (nil where none): B ph O/C CAUSE: Suspect Bird strike Location: unknown Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: Cursory Weather (wind/rain): calm LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Line was patrolled and sectionalized and no fault was found suspect bird strike over the canal area. | .
3519 |  | JE24027163 | TARATA | Western | TARATA | 2024-08-02 | 12:36 | 2024-08-02 | 16:41 | 0.0006765 | 2.759e-06 | 1 | 245 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faulty TFR 3850T, Missing phase and rust hole in the top steel work Isolated at TFR 3850T Fuses TFR Replaced, full power restored Earthing need to be upgraded for TFR 3850T, this will be done in a planned outage | .
3520 |  | JE24027169 | KONINI | Western | KONINI | 2024-08-02 | 11:19 | 2024-08-02 | 11:53 | 0.0033521 | 9.9323e-05 | 36 | 1215 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Replaced 1 X Copper To Ali Joint at Transformer T8/358 Due To Old age Isolated at ABS S27 & ABS S44 Back feed in at ABS S24 | .
3521 |  | JE24027221 | FORDELL | Western | FORDELL | 2024-08-02 | 12:50 | 2024-08-02 | 13:48 | 0.0012704 | 2.2072e-05 | 8 | 460 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: 1198 No. Fuses: 2 Fuse Amp Size: 8 And 1 X Candle TIME CLOSED: 13-47 Cause: Wind Weather (wind/rain): Win d Follow up required (select advisory)? | .
3522 |  | JE24027259 | TE KIRI | Western | TE KIRI | 2024-08-02 | 22:45 | 2024-08-03 | 1:48 | 0.041801 | 0.00075044 | 272 | 15151 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV, CB TA9 Protection flags (nil where none): E/F CAUSE: Line Down Location: 715528 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Yes / Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Line down due to corrosion at mid span twist joint SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3523 |  | JE24024601 | 634 HALL BLOCK ROAD BALLANCE PAHIATUA | Western | MANGATAINOKA | 2024-08-01 | 9:45 | 2024-08-01 | 12:50 | 0.0035729 | 1.9313e-05 | 7 | 1295 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace burnt off larch pole P18288 after temp repairs | .
3524 |  | JE24024604 | 330 EVERETT ROAD EVERETT PARK INGLEWOOD | Western | WAITARA RD | 2024-08-01 | 9:15 | 2024-08-01 | 14:16 | 0.042252 | 0.00014071 | 51 | 15314 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 742610 and TX 874 with new 50kva. | .
3525 |  | JE24024623 | 1009 OKOKI ROAD OKOKI URENUI | Western | MAIN RD MOTONUI | 2024-08-01 | 9:46 | 2024-08-01 | 12:56 | 0.0020996 | 1.1036e-05 | 4 | 761 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Safety isolation of Tx 4779T to carry out works on pole 763807 | .
3526 |  | JE24024632 | 195 KARERE ROAD LONGBURN PALMERSTON NORTH | Western | LINTON | 2024-08-01 | 9:09 | 2024-08-01 | 13:34 | 0.019704 | 7.4492e-05 | 27 | 7142 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace transformer & all hardware at pole P43510. Replace pole P31839. Rebind conductors at 590322 | .
3527 |  | JE24024817 | 37 DENBIGH ROAD MIDHIRST STRATFORD | Western | CLOTON RD NORTH | 2024-08-01 | 9:10 | 2024-08-01 | 16:26 | 0.061331 | 0.00014071 | 51 | 22230 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install new Entec structure at 741548, Remove Fused ABS 5539 and install xarms at 741543 Commissioning of Sec 12731/2 to be done Monday 5th August | .
3528 |  | JE24024865 | 9 DURIE VALE ROAD DURIE HILL WANGANUI | Western | BASTIA HILL | 2024-08-01 | 9:11 | 2024-08-01 | 15:31 | 0.03144 | 8.2769e-05 | 30 | 11396 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace TX Pole 767763 - 1580W | .
3529 |  | JE24024866 | 336 MARATOTO ROAD KOMATA PAEROA | Eastern | BENNETT ST | 2024-08-01 | 9:08 | 2024-08-01 | 14:47 | 0.039735 | 0.00029245 | 106 | 14402 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | AP-01 Replace 11kV Xarms at poles N12884 & N12942. AP-02 Replace 11kV & 400V Xarms at poles N2481, N2486 & N2491. AP-03 Replace 11kV & 400V Xarms at Poles N2447 & N12932. | .
3530 |  | JE24024878 | 6170 STATE HIGHWAY 1 WAIOURU MILITARY AREA WAIOURU | Western | RUAPEHU | 2024-08-01 | 8:56 | 2024-08-01 | 14:24 | 0.0070969 | 2.2072e-05 | 8 | 2572 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Fused ABS 1265 at pole 778518. DNO 2405018 | .
3531 |  | JE24024881 | 190 FLAT POINT ROAD FLAT POINT MASTERTON | Western | WESTMERE GLADSTONE | 2024-08-01 | 9:31 | 2024-08-01 | 13:16 | 0.023624 | 0.00010484 | 38 | 8563 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Isolation for Vegetation cutting between poles 449065 to 832436 | .
3532 |  | JE24024887 | 23 LINLEY TERRACE JUDEA TAURANGA | Eastern | BROOKFIELD TCE | 2024-08-01 | 9:15 | 2024-08-01 | 15:40 | 0.2271 | 0.0028831 | 570 | 82313 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV poles and hardware at sites - 206136, 206138, 206140, 206145 | .
3533 |  | JE24024889 | 7557 STATE HIGHWAY 26 KOMATA PAEROA | Eastern | BENNETT ST | 2024-08-01 | 9:30 | 2024-08-01 | 13:37 | 0.00068018 | 2.759e-06 | 1 | 247 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV B2*/T2 Xarm at pole N2632 | .
3534 |  | JE24024958 | 414 CHELTENHAM HUNTERVILLE ROAD WAITUNA WEST REWA, | Western | COLYTON | 2024-08-01 | 8:38 | 2024-08-01 | 16:07 | 0.10031 | 0.00022348 | 81 | 36358 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Vegetation outage for Asplundh to work between three pole areas, P08044-458494 - 141 Cheltenham Hunterville Rd P08028-P08037 - 46 Mangapipi Rd, P08804-P26923 - 753 Cheltenham Hunterville Rd | .
3535 |  | JE24024965 | 2 DREGHORN PLACE TOKOROA TOKOROA | Eastern | DALMENY ST | 2024-08-01 | 23:30 | 2024-08-02 | 1:56 | 0.034196 | 0.00023451 | 85 | 12394 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - IC1531-FC5033-IC1506 | .
3536 |  | JE24026803 | 204 HIKUNUI ROAD KAHUTARA FEATHERSTON | Western | DAIRY FACTORY | 2024-08-01 | 10:33 | 2024-08-01 | 12:56 | 0.011007 | 7.7251e-05 | 28 | 3990 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace cracked 11KV Insulator at pole 812808 determine condition of remaining insulators, change if required | .
3537 |  | JE24026985 | POHANGINA | Western | POHANGINA | 2024-08-01 | 1:00 | 2024-08-01 | 13:20 | 0.045735 | 0.00054076 | 134 | 16577 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: REC F26 Protection flags (nil where none): 3 phase OC EF CAUSE: Tree through the lines and lines down Location: Pole P14146 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): windy LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Links at Pole need a label Additional fault restoration comments: | .
3538 |  | JE24027042 | DAIRYFACT | Western | DAIRYFACT | 2024-08-01 | 10:46 | 2024-08-01 | 11:47 | 0.01219 | 0.00019865 | 72 | 4418 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 11klV Binder broken at Pole P03475. Isolated at ABS H127 & H129 to allow rebind.rebind all 3 Insulators | .
3539 |  | JE24027060 | MAKINO | Western | MAKINO | 2024-08-01 | 11:37 | 2024-08-01 | 14:33 | 0.34571 | 0.0038681 | 1402 | 125306 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11KV CB22 Protection flags (nil where none): A B C Phase O/C CAUSE: Glass Strain Fault also Blown 1 Lightning Arrestor and replaced 2 Deadends at same pole P18364 Location: Pole P18364 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Light Rain & Wind LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: | .
3540 |  | JE24027061 | recloser_573 | Western | RANGIKURA | 2024-08-01 | 11:39 | 2024-08-02 | 15:15 | 0.10998 | 0.00035867 | 123 | 39864 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | REGULATORY INFORMATION Voltage & Device ID: 11KV Rec RS573 Protection flags (nil where none): A Phase E/F CAUSE: Line Down Location: Pole 781466 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Rain & Wind LFI (Y/N + Comments): Yes But Did not work Follow up Required (select advisory)? Additional fault restoration comments: Transformers past Pole 371125 will be off over night due to Huge Valley, line down, Need more Gear Maybe Chopper | .
3541 |  | JE24024181 | 16 CAMPBELL STREET TOKOROA TOKOROA | Eastern | CAMPBELL ST | 2024-07-31 | 23:30 | 2024-08-01 | 2:23 | 0.00047592 | 2.759e-06 | 1 | 173 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - IC1820-FC5043-IC1843 | .
3542 |  | JE24024406 | 153B SCHRIEBER ROAD PUKEHINA TE PUKE | Eastern | OTAMARAKAU | 2024-07-31 | 9:46 | 2024-07-31 | 15:21 | 0.00092545 | 2.759e-06 | 1 | 335 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Cut terees in 11kv line between poles 481824 & 486846 | .
3543 |  | JE24024551 | 201 HIKUAI SETTLEMENT ROAD DUCK CREEK HIKUAI | Eastern | HIKUAI | 2024-07-31 | 9:00 | 2024-07-31 | 16:56 | 0.21515 | 0.00045247 | 164 | 77982 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install fibre between poles 383157 & U0453 | .
3544 |  | JE24024600 | 48 WAIPARUPARU ROAD TAIHAPE TAIHAPE | Western | MOAWHANGO | 2024-07-31 | 9:16 | 2024-07-31 | 11:22 | 0.0090802 | 7.1733e-05 | 26 | 3291 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | SHUT 5 Repair & Resag conductor at pole 788471. | .
3545 |  | JE24024826 | 88 MURICATA AVENUE MOUNT MAUNGANUI TAURANGA | Eastern | CENTRAL PARADE | 2024-07-31 | 8:56 | 2024-07-31 | 10:05 | 0.018214 | 0.00026486 | 96 | 6602 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace blown surge arrestors at pole 213873 | .
3546 |  | JE24026855 | IHAIA RD | Western | IHAIA RD | 2024-07-31 | 6:56 | 2024-07-31 | 7:44 | 0.0016179 | 3.3108e-05 | 12 | 586 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: 11kV Fuses TA189 Pole: 715 128 CAUSE: Strong winds/deterioration. Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Strong wind/light rain. Follow up required (select advisory)? No Additional fault restoration comments: HV Insulator has come off the cross-arm at Pole 715 128 Repairs being made under AP 6855-01 Full Power restored at 07:44 | .
3547 |  | JE24026867 | TUTAENUI | Western | TUTAENUI | 2024-07-31 | 9:00 | 2024-07-31 | 11:23 | 0.0011788 | 8.2769e-06 | 3 | 427 | Unplanned | VEGETATION - OUTSIDE ZONE | Isolation: 11kV Fuses 868 Poles: 794368 - 370906 CAUSE: Tree branch went through HV Line Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Light Rain Follow up required (select advisory)? No Additional fault restoration comments: HV Fuses 868 did not operate - I confirmed with the Field Switcher. HV Lines down (on the ground) between Poles 794368 - 370906 due to a tree that went through the Lines. Repairs completed under AP 6867-01 Full Power restored at 11:22 | .
3548 |  | JE24026893 | 118 OHAWE ROAD, HAWERA, 4671 | Western | KETEMARAE RD | 2024-07-31 | 10:43 | 2024-07-31 | 12:16 | 0.034527 | 0.00037246 | 135 | 12515 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: 11kV Fuses 6533 Pole: 721 939 CAUSE: Deterioration Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Rain Follow up required (select advisory)? No Additional fault restoration comments: HV Line came off the pin-insulator at Pole 721 939. Repairs completed & Full Power restored at 12:15 | .
3549 |  | JE24026910 | Fuses SD4-136 | Eastern | OROPI RD | 2024-07-31 | 11:43 | 2024-08-01 | 15:45 | 0.15324 | 0.0023368 | 715 | 55542 | Unplanned | THIRD PARTY INTERFERENCE - DIG IN | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 9517 Protection flags (nil where none): E/F CAUSE: Cable strike by digger Location: Hilltop Rd Temp generation (state details when used): Yes PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F3, not patrolled Weather (wind/rain): Rain LFI (Y/N + Comments): Yes, activated Follow up Required (select advisory)? NDR to follow Additional fault restoration comments: Cable strike on Hilltop Rd by digger NDR 2R -Generator has been installed Crews returning in morning to repair the cable, Jumper has been put on E-map as transformer is been fed from a generator. HV cable repaired and generator removed 1 x 35mm² single cable repair kit 2 x zip repair sleeves | .
3550 |  | JE24026949 | recloser_14727:2 | Eastern | BRUCE RD | 2024-07-31 | 15:45 | 2024-08-01 | 10:35 | 0.21272 | 0.001167 | 392 | 77103 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 14727 Protection flags (nil where none): E/F CAUSE: Car V Pole Location: Pole 319252 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4, Yes, Either side of the crash site Weather (wind/rain): wind LFI (Y/N + Comments): No Follow up Required (select advisory)? NDR to follow Additional fault restoration comments: ETA - 15MINS - Fire Comms notified Lines were isolated at Links 14722, IP119 & 9876/6 and at ABS's 9876/1, SD4-372 & SD5-001 to replace pole. Crew required to return in morning to phase out cable at Links 14731 after pole replacement. Cable tested Ok reading 6 GΩ Cable was livened, phased out & the network restored 1 x 11m pole 1 x HV cross arm assembly 1 x LV cross arm assembly | .
3551 |  | JE24026953 | DYERVILLE | Western | DYERVILLE | 2024-07-31 | 18:42 | 2024-07-31 | 19:26 | 0.00024021 | 5.5179e-06 | 2 | 87 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faultman found burnt off lead to fuse holder at transformer T2505, line was isolated at Fuses 7359 and all 3 DDO's were replaced. | .
3552 |  | JE24026973 | CHURCH ST | Western | CHURCH ST | 2024-07-31 | 20:54 | 2024-08-01 | 2:15 | 0.042202 | 0.0010125 | 194 | 15296 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11KV REC C279/2 Protection flags (nil where none): A Ph O/C & E/F CAUSE: Damaged cable terminations & blown lightning arrestors Location: Pole 446702 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: Cursory Weather (wind/rain): windy LFI (Y/N + Comments): N Follow up Required (select advisory)? N Additional fault restoration comments: Line was isolated at Fuses 7122 to joint & reterminate cables & replace blown lightning arrestors. | .
3553 |  | JE24026974 | LANGDALE | Western | LANGDALE | 2024-07-31 | 21:14 | 2024-08-01 | 10:40 | 0.031135 | 3.8625e-05 | 14 | 11285 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faultman found blown fuses at Fuses 7889, line was patrolled but most of the line could not be seen in the rain and fog as most goes cross country. Crew will return in morning the patrol at day light. Line Patrolled & broken binder at Pole 360416. Crossarm replaced & conductors rebound. Power restored. | .
3554 |  | JE24026978 | WILLOUGHBY ST | Eastern | WILLOUGHBY ST | 2024-07-31 | 22:00 | 2024-07-31 | 22:57 | 0.011613 | 0.00020416 | 74 | 4209 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Electric shocks reported at 64A Belmont Road, Paeroa - Faultman attended 30/07/2024 Electrical inspector and electrician attended and found the High voltage readings on the LV . No one was electrocuted. This is an empty Kiosk. Safety disconnection A38562 - Further investigation on on 31st in connection with customers electrician Initial report was LV only, HV outage to make repairs Part of U6826 - Repair Neutral in Transformer TC2826 Stewart Simpson advised returned 01/08/2024 and completed loop impendance tests. Tidied everything up. Network restored. | .
3555 |  | JE24020114 | RETA CRESCENT off KEREPEHI TOWN ROAD KEREPEHI | Eastern | MANGATARATA | 2024-07-30 | 8:45 | 2024-07-30 | 14:41 | 0.0088269 | 2.4831e-05 | 9 | 3199 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Kerepehi New Feeder - Installation of Links 14764 at Pole 269983 on KPE CB5. Install Links on KPE CB5 to allow future KPE bus outage with no SAIDI. | .
3556 |  | JE24024026 | 103 SWETMAN ROAD WAIKINO WAIHI | Eastern | OLD TAURANGA RD | 2024-07-30 | 10:00 | 2024-07-30 | 12:11 | 0.0054048 | 4.1384e-05 | 15 | 1959 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Arms at Poles P13346 & P2121 | .
3557 |  | JE24024176 | 1 KELSO STREET TOKOROA TOKOROA | Eastern | LOMOND AVE | 2024-07-30 | 23:30 | 2024-07-31 | 4:06 | 0.055397 | 0.0002014 | 73 | 20079 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - IC3037-IC3026-IC3035-IC3033 | .
3558 |  | JE24024327 | 190 MILL ROAD, PAEROA | Eastern | RAILWAY ST | 2024-07-30 | 9:03 | 2024-07-30 | 15:10 | 0.0065682 | 1.9313e-05 | 7 | 2381 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv Poles N13246,876685,876684,N1277,N1278 and 876682 | .
3559 |  | JE24024390 | 47 CORNWALL STREET MASTERTON MASTERTON | Western | CORNWALL ST | 2024-07-30 | 8:32 | 2024-07-30 | 13:07 | 0.29318 | 0.001065 | 386 | 106266 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles 822808 and 822786 | .
3560 |  | JE24024412 | 51 ACKWORTH ROAD LEPPERTON NEW PLYMOUTH | Western | WAITARA RD | 2024-07-30 | 9:00 | 2024-07-30 | 13:13 | 0.032109 | 0.00012691 | 46 | 11638 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace transformer 1332 with new 50kva and pole 745006. | .
3561 |  | JE24024437 | 190 ORCHARD EAST ROAD TURUA THAMES | Eastern | HAURAKI RD | 2024-07-30 | 9:13 | 2024-07-30 | 15:09 | 0.037311 | 0.00010484 | 38 | 13524 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole O12854 | .
3562 |  | JE24024565 | 40 WINGS LINE MARTON MARTON | Western | NGATAWA | 2024-07-30 | 9:24 | 2024-07-30 | 15:00 | 0.0027835 | 8.2769e-06 | 3 | 1009 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install line break at pole 801491, replace X arms on poles 801496 (X2062) 801495, 801494, 801492, Close line break at pole 801491. | .
3563 |  | JE24026273 | 6 STOKES ROAD MAUNGATAUTARI CAMBRIDGE | Eastern | TOTMANS RD | 2024-07-30 | 10:00 | 2024-07-30 | 15:44 | 0.26196 | 0.00076147 | 276 | 94949 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | DEFECT. GLASS INSULATOR HAS COME AWAY FROM XARM 875867. XARMS ALL NEED REPLACING FITTED OUT WITH NEW HARDWARE | .
3564 |  | JE24026667 | 227 MANAIA ROAD MANAIA HAWERA | Western | OTAKEHO | 2024-07-30 | 8:40 | 2024-07-30 | 12:58 | 0.033466 | 0.00012967 | 47 | 12130 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace DNO abs MA121 & pole 718296 | .
3565 |  | JE24026708 | MAIN RD MOTONUI | Western | MAIN RD MOTONUI | 2024-07-30 | 6:44 | 2024-07-30 | 8:55 | 0.000721 | 5.5179e-06 | 2 | 261 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Transformer 2695T No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 08:54 Cause: Lightning Weather (wind/rain): Drizzle Follow up required (select advisory)? NIL | .
3566 |  | JE24026709 | KAIMAI DRIVE | Eastern | KAIMAI DRIVE | 2024-07-30 | 6:52 | 2024-07-30 | 7:32 | 0.00055474 | 1.3795e-05 | 5 | 201 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses S6025 No. Fuses: 2 Fuse Amp Size: 25A TIME CLOSED: :07:31 Cause: Bird Strike Weather (wind/rain): Drizzle Follow up required (select advisory)? NIL | .
3567 |  | JE24026712 | PORTLAND QUAY | Western | PORTLAND QUAY | 2024-07-30 | 7:29 | 2024-07-30 | 18:56 | 0.36714 | 0.0008939 | 324 | 133071 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV LIV CB LI6 Protection flags (nil where none): E/F CAUSE: Neutral termination faulted. (HV Pole burnt/was on fire) Location: Pole 842 664 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: ETA - 30min as per Downer Hub - Fire comms advised First reported by Jerome who was passing by - NOC put in an emergency job and dispatched field crew. Shortly after this job was put in, LIV CB LI6 tripped at 07:29 on E/F Field Switcher was not able to identify the location, ie: Pole number & could not open his SCADA tile on his device. After identifying the correct location in the field, field switcher carried out the Isolation points. LIV CBLI6 was closed in at 08:49 & open point was closed at ABS LI615 at 09:14. Work site was then safety tested and Issuer Earths applied. Wooden Pole is being replaced under AP 6712-01 SAFETY MANAGER - Medical dependant person was not doing well as per Jasmyn Telfer . | .
3568 |  | JE24026769 | TIKORANGI | Western | TIKORANGI | 2024-07-30 | 11:42 | 2024-07-30 | 13:25 | 0.0014132 | 1.3795e-05 | 5 | 512 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 5241 No. Fuses: 2 Fuse Amp Size: 10Amp TIME CLOSED: 13:24 Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)? NIL | .
3569 |  | JE24026846 | WAIHI NORTH | Eastern | WAIHI NORTH | 2024-07-30 | 20:22 | 2024-07-31 | 4:23 | 0.051267 | 0.00022899 | 83 | 18582 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV Sec 13777 Protection flags (nil where none): E/F CAUSE: Tree through Lines Location: Pole 496624 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Curse Weather (wind/rain): Light Winds LFI (Y/N + Comments): no Follow up Required (select advisory)? Additional fault restoration comments: 3rd time in 2 years Faultsman reports the trees have been through the lines at this site !!! SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3570 |  | JE24027090 | MANAIA | Western | MANAIA | 2024-07-30 | 17:00 | 2024-07-30 | 18:08 | 0.03353 | 0.00049661 | 180 | 12153 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace rotten Crossarms at pole 719367 E00143 30/07/24 1700-1900 | .
3571 |  | JE24023724 | 671 SPRINGHILL ROAD BIDEFORD TINUI | Western | ANNEDALE | 2024-07-29 | 9:30 | 2024-07-29 | 15:16 | 0.0019076 | 5.5179e-06 | 2 | 691 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Isolation for Vegetation cutting at multiple sites between poles 462337 and 462344 | .
3572 |  | JE24024626 | 1227 HIKUAI SETTLEMENT ROAD PAUANUI HIKUAI | Eastern | PAUANUI | 2024-07-29 | 9:18 | 2024-07-29 | 12:30 | 0.032806 | 0.00017106 | 62 | 11891 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Change Faulty SF6 Gas Gauge on Switchgear 9770, TC3231 will be off, SAIDI Approved. | .
3573 |  | JE24025257 | 69 BURGON ROAD OKAIAWA HAWERA | Western | OKAIAWA | 2024-07-29 | 9:01 | 2024-07-29 | 11:03 | 0.00033636 | 2.759e-06 | 1 | 122 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace hv pin arm and replace deteriorated hv sleeve at pole 721219 | .
3574 |  | JE24025981 | 7 ALEXANDRA AVENUE MORRINSVILLE MORRINSVILLE | Eastern | NZDC A | 2024-07-29 | 8:00 | 2024-08-15 | 10:35 | 0.01053 | 0.00015174 | 28 | 3816 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Morrinsville Protection Upgrade Stage 3 Install/reinstate cable break at TC3822/A - CB1 Isolation point. Isolate 11kV bus and cables and complete protection upgrade and CT replacements. Disconnect cable from TEP027/3 & connect to CB2. Restore Fonterra from Mobile Sub to CB2 - Break/Make -Open MSX1122 , open SW/Gear 2099 , phase rotation to be confirmed at TP224 before closing CB2 . Remove MSX , SW/G 14914 , TEMP027 & TEMP019 metering unit from Network . | .
3575 |  | JE24026265 | 99 HARPER STREET GONVILLE WANGANUI | Western | PURIRI ST | 2024-07-29 | 9:16 | 2024-07-29 | 13:10 | 0.099836 | 0.00043868 | 159 | 36186 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Pole 765788 that has been hit by a car | .
3576 |  | JE24026339 | 23 DUNTON DRIVE WELCOME BAY TAURANGA | Eastern | WELCOME BAY | 2024-07-29 | 9:47 | 2024-07-29 | 13:59 | 0.093192 | 0.00037246 | 135 | 33778 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove generator from TD4-537 Connect new 11kv cable to supply TD4-537 from SW/Gear 14849/2 & permanently remove cable from fuses SD4-135 Upgrade Fuses 14849/2 - ( Safelink SW/Gear .) Remove DNO2407016 | .
3577 |  | JE24026558 | LEPPERTON | Western | LEPPERTON | 2024-07-29 | 3:30 | 2024-07-29 | 5:16 | 0.0011642 | 1.1036e-05 | 4 | 422 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 8153 No. Fuses: 2 Fuse Amp Size: 6 Amp TIME CLOSED: 05:15 Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)? N | .
3578 |  | JE24026195 | 6 HULL ROAD MOUNT MAUNGANUI TAURANGA | Eastern | HULL RD | 2024-07-28 | 8:00 | 2024-07-28 | 8:54 | 0.0025179 | 4.6902e-05 | 17 | 913 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Reconnect jumpers at pole 213812 Check phasing of new cable at Switchgear 14816 | .
3579 |  | JE24026481 | WAIRERE RD | Eastern | WAIRERE RD | 2024-07-28 | 18:59 | 2024-07-28 | 21:06 | 0.011551 | 9.1046e-05 | 33 | 4187 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Auto-recloses on WLN CB 1 Walton CB 1 sectionalised to identify persistent AB & C phase fault INVT Line patrol during daylight hours 26/07/24 did not find anything , has been multiple trips since. 28/07/2024: Customer at 83 Given Road has advised: : Hi there, our property and neighbours have been experiencing several outages this week. Fortunately, these only last for under a minute but is now concerning as they are frequently happening in the night and my baby’s heater is turning off making her room cold. CG. Customer advised she has power - it is just flicking on and off SMC Advised FM to contact Control Found ffault to be pole 493268 line clashing in wind & Cows also hitting stay wire, farmer has blocked cows from stay wires 3 metre cross arm installed to give additional conductor spacing. Isolation for repairs made between ABS 1068, IC730 & 1191 | .
3580 |  | JE24026499 | BLACK STUMP | Eastern | BLACK STUMP | 2024-07-28 | 7:55 | 2024-07-28 | 10:00 | 0.036341 | 0.00094357 | 342 | 13172 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 3 Protection flags (nil where none): A,B,C, O/C Inverse Time CAUSE: Pukeko Tangled in lines on Sw/Gear 13625/1 Section Location: Sw/Gear 13625/1 Section Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: curse/opp Weather (wind/rain): Slight Wind LFI (Y/N + Comments): yes 13625/2 & 1 Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3581 |  | JE24026506 | pole_801538 - 366 STATE HIGHWAY 3, BULLS, 4894 | Western | BULLS | 2024-07-28 | 11:13 | 2024-07-28 | 12:33 | 0.019142 | 0.00024003 | 87 | 6938 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Replace king bolt in 11kV cross arm at Pole 801538 | .
3582 |  | JE24026529 | ATHENREE | Eastern | ATHENREE | 2024-07-28 | 13:07 | 2024-07-28 | 21:16 | 0.025608 | 0.0013988 | 507 | 9282 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | ETA advised to Fire comms 10 to 15 min Vehicle contact with Pole 207362 Isolation from IP631 to SA2-003 to replace pole Restoration of network to normal Recloser 9404 opened ABS SA2-003 closed within a minute to avoid phase shift issue | .
3583 |  | JE24025384 | 7 ALEXANDRA AVENUE MORRINSVILLE MORRINSVILLE | Eastern | NZDC A | 2024-07-27 | 8:01 | 2024-07-27 | 8:41 | 0.00010976 | 2.759e-06 | 1 | 40 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Morrinsville Protection Stage 2 Switch Fonterra off CB 2 Morrinsville Substation, and onto Temporary Mobile Substation and liven. Connect SW/Gear TEMP027/1 to 14914/2 - Remove cable from CB2 & connect to TEMP027/3 . Northpower to repair oil leak on transformer 4306 . Confirm Phase rotation at TP224 before restoring supply from the Mobile Sub . Emails re Fonterra outage in switch pack . | .
3584 |  | JE24026209 | 59 STATION ROAD TE PUKE TE PUKE | Eastern | JELLICOE ST | 2024-07-27 | 8:01 | 2024-07-27 | 9:05 | 0.00053454 | 8.2769e-06 | 3 | 194 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | reistste jumpers at pole# 267898 | .
3585 |  | JE24026440 | TE PUNINGA | Eastern | TE PUNINGA | 2024-07-27 | 2:25 | 2024-07-27 | 5:06 | 0.011073 | 6.8974e-05 | 25 | 4013 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 3 Protection flags (nil where none): Nil CAUSE: Boat V pole Location: Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4, cursory patrolled either side of the crash site. Weather (wind/rain): Dense fog LFI (Y/N + Comments): Yes installed, no activation Follow up Required (select advisory)? NDR to follow Additional fault restoration comments: Boat came off trailer and hit pole K2046 Pole replaced 1 x 11m Pole HV pin arm complete assembly LV pin arm complete assembly SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3586 |  | JE24026442 | SHERWOOD ST | Eastern | SHERWOOD ST | 2024-07-27 | 5:16 | 2024-07-27 | 10:11 | 0.19647 | 0.0025631 | 840 | 71212 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: CB 3242 33kv & 11kV CB 5 Protection flags (nil where none): O/C E/F & T6 Tripped on Diff CAUSE: Lightning Strike Suspected Location: Pole 852797 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Curse Weather (wind/rain): Fine LFI (Y/N + Comments): Nil Follow up Required (select advisory)? Additional fault restoration comments: also removed Old Dead Cat off T6 Transformer ( it's been there a while ) 3 x 33kv L/A's Replaced also 3 x 11kV L/A's replaced SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3587 |  | JE24026471 | BENNETT ST | Eastern | BENNETT ST | 2024-07-27 | 15:26 | 2024-07-27 | 17:29 | 0.00067537 | 5.5179e-06 | 2 | 245 | Unplanned | WILDLIFE - BIRD | Fuses Location: FC2300 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 17:28 Cause: Duck strike Weather (wind/rain): Calm Follow up required (select advisory)? | .
3588 |  | JE24026474 | MANGAMAIRE | Western | MANGAMAIRE | 2024-07-27 | 18:47 | 2024-07-27 | 19:03 | 8.4148e-05 | 5.5179e-06 | 2 | 31 | Unplanned | WILDLIFE - BIRD | Fuses Location: R49 No. Fuses: 1 Fuse Amp Size: 6 TIME CLOSED: 19-02 Cause: Birds Nest Weather (wind/rain): Fine Follow up required (select advisory)? Removed all 3 fuses to Remove The Birds Nest safety ONLY 1 FUSE BLOWN | .
3589 |  | JE24026477 | KAIMAI DRIVE | Eastern | KAIMAI DRIVE | 2024-07-27 | 17:52 | 2024-07-27 | 19:10 | 0.081052 | 0.0017519 | 635 | 29378 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV TGA CB11 Protection flags (nil where none): TGA CB 11 OC INV T REC9275 A Phase OC gas/sw 13363 B & C phase OC CAUSE: no fault found Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Telemetered LFI at one of ABS SE3-001 SE3--04 or SE3-016 will signiciantly reduce patrol & saidi SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3590 |  | JE24021365 | 94 PLUMMER ROAD WHAKAMARAMA | Eastern | BARRETT RD | 2024-07-26 | 9:00 | 2024-07-26 | 14:52 | 0.00097138 | 2.759e-06 | 1 | 352 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace TX pole 209257 "pole top photography" | .
3591 |  | JE24024121 | 1268 ROBERTS LINE BUNNYTHORPE PALMERSTON NORTH | Western | TE ARAKURA | 2024-07-26 | 8:46 | 2024-07-26 | 14:02 | 0.079357 | 0.00025107 | 91 | 28763 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | HV Reconductor from P19819 - P39198 | .
3592 |  | JE24024138 | 4 SURREY STREET HAWERA HAWERA | Western | ARGYLE ST | 2024-07-26 | 9:00 | 2024-07-26 | 10:51 | 0.047079 | 0.00042764 | 155 | 17064 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove 11kv line breaks form poles 703731 and 846455 | .
3593 |  | JE24024306 | 150 STATE HIGHWAY 53 SOUTH FEATHERSTON FEATHERSTON | Western | DAIRY FACTORY | 2024-07-26 | 8:32 | 2024-07-26 | 15:19 | 0.044923 | 0.00011036 | 40 | 16283 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace existing 11kv take off pole 799760 and replace existing 11kv cross arms on pole 799738 | .
3594 |  | JE24025858 | 854 WHITE ROCK ROAD RUAKOKOPUTUNA MARTINBOROUGH | Western | HAU NUI 33KV | 2024-07-26 | 11:01 | 2024-07-26 | 12:39 | 0.051721 | 0.00052696 | 191 | 18747 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace cracked 33kv insulator at pole 811210 | .
3595 |  | JE24026324 | WESTMERE GLADSTONE | Western | WESTMERE GLADSTONE | 2024-07-26 | 9:28 | 2024-07-26 | 10:20 | 0.0038959 | 7.4492e-05 | 27 | 1412 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Floating Conductor at Pole 832310 Isolated at Fuses 7850 Floater repaired | .
3596 |  | JE24026329 | BELVEDERE | Western | BELVEDERE | 2024-07-26 | 7:59 | 2024-07-26 | 11:32 | 0.001761 | 8.2769e-06 | 3 | 638 | Unplanned | WILDLIFE - BIRD | Fuses Location: 7569 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 11:31 Cause: Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? N | .
3597 |  | JE24026387 | DYERVILLE | Western | DYERVILLE | 2024-07-26 | 13:09 | 2024-07-26 | 13:23 | 0.00019497 | 1.3795e-05 | 5 | 71 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | High Voltage at Transformer 247, 250, 247 Transformer isolated, tapped down Power off 13:08 Power on 13:22 Voltages now 236, 238, 235 | .
3598 |  | JE24026397 | dtx_5380E | Western | OTAKEHO | 2024-07-26 | 14:15 | 2024-07-26 | 14:24 | 2.5061e-05 | 2.759e-06 | 1 | 9 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Lower Transformer 1 Tap at TX 5380E - Contact Control 105 Rowan Rd - Manaia Transformer 5380E was tapped down 1 tap to tap 2, as ABS MA208 was closed to equalize voltages better. | .
3599 |  | JE24027083 | NGATAWA | Western | NGATAWA | 2024-07-26 | 13:30 | 2024-07-26 | 14:31 | 0.0071695 | 0.00011864 | 43 | 2599 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 200kVA Transformer X762, Oil Leak E00142 outage 26/07/2024 1330-1600 | .
3600 |  | JE24024044 | 1 O'SULLIVAN DRIVE TOKOROA TOKOROA | Eastern | CAMPBELL ST | 2024-07-25 | 23:31 | 2024-07-26 | 1:18 | 0.0091586 | 8.5528e-05 | 31 | 3320 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU oil maintenance - IC1888-TC1156-IC1521 | .
3601 |  | JE24024066 | 130 ARGYLE STREET HAWERA HAWERA | Western | ARGYLE ST | 2024-07-25 | 8:45 | 2024-07-25 | 13:47 | 0.078299 | 0.00025934 | 94 | 28380 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace hv poles 703725 , 703727 , 703728 | .
3602 |  | JE24024071 | 246 SH53 Featherston | Western | DAIRY FACTORY | 2024-07-25 | 8:30 | 2024-07-25 | 15:41 | 0.04757 | 0.00011036 | 40 | 17242 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Transformer structure T2103 | .
3603 |  | JE24024074 | 72 MATAROA ROAD TAIHAPE TAIHAPE | Western | MATAROA A | 2024-07-25 | 9:45 | 2024-07-25 | 12:18 | 0.0021127 | 1.3795e-05 | 5 | 766 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Shut 3 Lines to be resagged at pole 459494. | .
3604 |  | JE24024081 | 1271 ROBERTS LINE BUNNYTHORPE PALMERSTON NORTH | Western | TE ARAKURA | 2024-07-25 | 9:01 | 2024-07-25 | 14:12 | 0.014629 | 4.6902e-05 | 17 | 5302 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | HV reconductoring 18 spans from P02238 - P19818. | .
3605 |  | JE24024082 | 80 OPARIA ROAD TURUA THAMES | Eastern | HAURAKI RD | 2024-07-25 | 8:46 | 2024-07-25 | 10:14 | 0.00096803 | 1.1036e-05 | 4 | 351 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace HV pin arm on Pole O13107 and O2493 | .
3606 |  | JE24024140 | 120 MILL ROAD PAEROA | Eastern | TIROHIA-KARANGAHAKE | 2024-07-25 | 9:16 | 2024-07-25 | 14:56 | 0.013119 | 3.8625e-05 | 14 | 4755 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE 11KV POLE'S N1268,N1269,N13243,N13244,N13245 AND N1272 | .
3607 |  | JE24024459 | 1 CORINTH GROVE PAPAMOA BEACH TAURANGA | Eastern | GRAVATT RD | 2024-07-25 | 9:00 | 2024-07-25 | 17:06 | 0.22801 | 0.00065387 | 237 | 82642 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Disconnect cable from 13846/3 and terminate new 3c 185mm cable from new CFC 14916/3. Disconnect all cables from 9022 remove switch and install new CFCC 14905 in same location. Disconnect 3c x 25mm cable from TD5 252 and terminate new 3c x 35mm. Terminate new 3c x 185mm cable at 14905/1 and complete through joint towards 9033/1. Terminate new cable onto 14905/3, new cable onto 14905/2 and 14905/4 and complete connections. Liven 14905 & 14916 and check phasing at 14905/3 & /4 Phasing correction required at end of job which caused time over run. Power was restored to HV of TD5-253 via 14905/2 16:04 , LV restored via LV fuses of TD5-253 @ 16:10 This was done to determine which cable on 14905 needed to have phasing corrected without exposing TD5-253 customers to incorrect phase rotation. | .
3608 |  | JE24024972 | 92 WORKSOP ROAD MASTERTON MASTERTON | Western | COLOMBO RD | 2024-07-25 | 10:00 | 2024-07-25 | 11:25 | 0.017652 | 0.00020968 | 76 | 6398 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv cross arm at pole 833328 | .
3609 |  | JE24026210 | recloser_12556:2 | Western | BRISTOL RD | 2024-07-25 | 9:29 | 2024-07-25 | 10:42 | 0.012936 | 0.00021244 | 77 | 4689 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11KV REC 12556/2 Protection flags (nil where none): A & B ph O/C & E/F CAUSE: Suspect Magpies Location: PastREC 12556/2 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: Cursory Weather (wind/rain): calm LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Area full of Magpies on the lines. | .
3610 |  | JE24026279 | PATETONGA | Eastern | PATETONGA | 2024-07-25 | 14:23 | 2024-07-25 | 18:46 | 0.0014529 | 5.5179e-06 | 2 | 527 | Unplanned | WILDLIFE - BIRD | Fuses Location: FC4221 No. Fuses: 2 Fuse Amp Size: 20A TIME CLOSED: 18:45 Cause: Bird strike Weather (wind/rain): Calm Follow up required (select advisory)? No | .
3611 |  | JE24026295 | TAWHITI RD | Western | TAWHITI RD | 2024-07-25 | 16:23 | 2024-07-25 | 17:59 | 0.0013137 | 1.3795e-05 | 5 | 476 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: CA465 No. Fuses: 2 Fuse Amp Size: 8 TIME CLOSED: 17:58 Cause: Suspect line clash Weather (wind/rain): calm Follow up required (select advisory)? Y - job would not move to the Fuses keep saying transformer was de-energized | .
3612 |  | JE24019360 | 255 WOODLAND ROAD TAHAWAI | Eastern | LINDERMANN RD | 2024-07-24 | 8:45 | 2024-07-24 | 17:28 | 0.064945 | 0.00012415 | 45 | 23540 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Reconductor 11kV between Poles 380368 & 263964. Isolation SB1-025. Job over run the restore time. Kenny Douglas said they ran into issues with running the new conductor due to there being too many angles to contend with, this was hampered by correcting the sagging. | .
3613 |  | JE24023408 | 4 WAIHIRERE DRIVE TUATEAWA COROMANDEL | Eastern | KAPANGA ROAD | 2024-07-24 | 9:32 | 2024-07-24 | 13:52 | 0.039428 | 0.00015174 | 55 | 14291 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Disconnect and cut existing 11kV cable to TX TC5709 at TX TC5029. Install new 11kV U/G cable and connect at fuse switch 14890 /4 and thru joint at cable end TC5079. Replace 11kV fuses FC4025 with solid links. | .
3614 |  | JE24023745 | 1678 HINEKURA ROAD HINAKURA MARTINBOROUGH | Western | COLOGNE ST | 2024-07-24 | 9:16 | 2024-07-24 | 15:17 | 0.087868 | 0.00024279 | 88 | 31848 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Isolation for Vegetation cutting and FFT repairs, poles 816688 - 816687, 816717, 816694 - 816695, 841962 - 483050, 851790 - 851799, 816981 - 816983, 816989 - 848678,848686 - 851785, 816675-816677, 816685-816686, 816751-816757, 372299-816720 | .
3615 |  | JE24023754 | 356 NO 1 ROAD WAITOA WAITOA | Eastern | TATUANUI | 2024-07-24 | 8:30 | 2024-07-24 | 14:36 | 0.069671 | 0.00019037 | 69 | 25253 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace pole and ABS 669, replace arm on Poles C2250, C14255, C2153, C2185 and C2198 | .
3616 |  | JE24023793 | 100 VICTORIA STREET HAWERA HAWERA | Western | CAMBRIA ST | 2024-07-24 | 8:46 | 2024-07-24 | 13:53 | 0.024584 | 8.001e-05 | 29 | 8911 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace hv poles 703605 , 703606 , 703608 , 703609 | .
3617 |  | JE24023990 | 78 CHAMBERS STREET TOKOROA TOKOROA | Eastern | CAMPBELL ST | 2024-07-24 | 23:30 | 2024-07-25 | 3:35 | 0.0047281 | 1.9313e-05 | 7 | 1714 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - IC1959-IC1967-IC1962-FC5041 | .
3618 |  | JE24024016 | 996 RUATANGATA ROAD WHANGAEHU WANGANUI | Western | FORDELL | 2024-07-24 | 9:11 | 2024-07-24 | 15:10 | 0.027761 | 7.7251e-05 | 28 | 10062 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace X arms poles 792726, 792724, 792697, 792677 | .
3619 |  | JE24024024 | 59 KURIPUNI STREET KURIPUNI MASTERTON | Western | COLOMBO RD | 2024-07-24 | 8:45 | 2024-07-24 | 13:51 | 0.10703 | 0.00035039 | 127 | 38792 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles and repair defects | .
3620 |  | JE24024072 | 409 TAIRUA ROAD WHANGAMATA WHANGAMATA | Eastern | OPOUTERE | 2024-07-24 | 9:24 | 2024-07-24 | 18:34 | 0.64368 | 0.0013712 | 497 | 233306 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install fiber between poles 263631 & R0775 On livening the network on closing Sw/Gear IC1487 CB 3 tripped on A Ø E/F O/C, OMS JE24026143. Sw/Gear IC1487 was opened and CB 3 closed and the rest of the network was backfed via TAI3. Only 3 transformers were left off beyond fuses FC805. | .
3621 |  | JE24026049 | KATERE 5 | Western | KATERE 5 | 2024-07-24 | 3:37 | 2024-07-24 | 5:41 | 0.02449 | 0.00019865 | 72 | 8876 | Unplanned | WILDLIFE - BIRD | Fuses Location: 8163 No. Fuses: 2 Fuse Amp Size: 30A TIME CLOSED: 0540 Cause: bird strike Weather (wind/rain): fine Follow up required (select advisory)? | .
3622 |  | JE24026051 | PIONEER RD | Western | PIONEER RD | 2024-07-24 | 3:56 | 2024-07-24 | 6:35 | 0.0074463 | 4.6902e-05 | 17 | 2699 | Unplanned | WILDLIFE - BIRD | Fuses Location: 'Fuses 6466 No. Fuses: 2 Fuse Amp Size: 8 TIME CLOSED: 06:35 Cause: Bird Strike Weather (wind/rain): calm Follow up required (select advisory)?n | .
3623 |  | JE24026054 | KAKARIKI | Western | KAKARIKI | 2024-07-24 | 7:20 | 2024-07-24 | 9:49 | 0.015717 | 0.00021244 | 77 | 5697 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11KV Rec 10300 Protection flags (nil where none): E/F CAUSE: Conductor Down Due to Copper To Ali Joint faulty Location: Pole P01921 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Yes And not Working No Comms Follow up Required (select advisory)? Additional fault restoration comments: Back Feed in At ABS M72 | .
3624 |  | JE24026074 | MANGOREWA | Eastern | MANGOREWA | 2024-07-24 | 13:20 | 2024-07-24 | 15:34 | 0.0018547 | 1.3795e-05 | 5 | 672 | Unplanned | WILDLIFE - OTHER | REGULATORY INFORMATION Voltage & Device ID: 11kV Sw/Gear SE6-173 Protection flags (nil where none): Nil CAUSE: Rat between HV bushings Location: Link box SE6-159 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: yes F4 Weather (wind/rain): Calm LFI (Y/N + Comments): yes no activation Follow up Required (select advisory)? No Additional fault restoration comments: Possible cable fault. Rat shorted out the two fuse link bushings inside link box SE6-159 causing two HV 16A fuses to blow. The link box was inspected and the HV fuses replaced. Power restored at 15:34 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3625 |  | JE24026111 | 416 PUKE PUKE ROAD, FOXTON | Western | OROUA DOWNS | 2024-07-24 | 13:35 | 2024-07-24 | 13:46 | 2.8509e-05 | 2.759e-06 | 1 | 10 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Tapped Down Transformer T1/541 Was Getting 255V On All Phases Isolated at L81 Tapped down 1 Tap Now Got 243V On All Phases | .
3626 |  | JE24026140 | OTAKEHO | Western | OTAKEHO | 2024-07-24 | 19:45 | 2024-07-24 | 19:52 | 1.9911e-05 | 2.759e-06 | 1 | 7 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: Low Voltage What was replaced? Nil replaced. Tap Setting Raised from Tap 2 to Tap 3. Where was it replaced (pole/TX/pillar box)? Tx 5380E Is 2R required? Y 2R Y - What is the timeframe for repairs? Complete Additional Info: Voltage & Loop Impedance tested. All connections tested. Voltage was too low for voltage sensitive equipment in the cowshed to work correctly. Once voltage raised at Txfmr cowshed now operating correctly. 2nd job created 26/07 to lower transformer tap at TX5380E once feeder configuration back to normal - linked as related to | .
3627 |  | JE24026143 | OPOUTERE | Eastern | OPOUTERE | 2024-07-24 | 16:36 | 2024-07-25 | 16:41 | 0.014276 | 0.00076975 | 279 | 5174 | Unplanned | HUMAN ERROR - POTENTIAL WORKMANSHIP | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 3 Protection flags (nil where none): E/F O/C A phase CAUSE: Screw anchor into 11kV cable Location: Pole 263631 Tairua Road Temp generation (state details when used): Nil PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Fine LFI (Y/N + Comments): Nil Follow up Required (select advisory)? No Additional fault restoration comments: Screw anchor install under NAPA 112634 as part of project Hauraki. 11kV cable was isolated as part of planned shut, faulted on restoration. Temp line break cut to restore three transformers. Northpower to repair & close temp break tomorrow Napa 112364 crew has struck HV cable with screw anchor 25/07/24 request for flag resets under 2R WGM CB 3 | .
3628 |  | JE24026181 | PUNGAREHU | Western | PUNGAREHU | 2024-07-24 | 23:31 | 2024-07-25 | 10:46 | 0.013025 | 1.9313e-05 | 7 | 4721 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: Tx 5144E Fuses CAUSE: Faulty Transformer Temp generation (stage details when used): n PERFORMANCE DETAIL DNO (number or state no): n Circuit patrolled & type: cursory Weather (wind/rain): calm Follow up required (select advisory)? Additional fault restoration comments: Transformer 5144E requires replacement. Crew returning at first light to replace Transformer 5144E was replaced. | .
3629 |  | JE24023529 | 502 MOAWHANGO VALLEY ROAD MOAWHANGO TAIHAPE | Western | PAPAKAI | 2024-07-23 | 9:30 | 2024-07-23 | 12:05 | 0.0051256 | 3.3108e-05 | 12 | 1858 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Shut2 8 Spans to be resagged between poles 787235 - 787241. | .
3630 |  | JE24023632 | 569 HUIHUITAHA ROAD WAOTU PUTARURU | Eastern | HORAHORA | 2024-07-23 | 8:30 | 2024-07-23 | 15:29 | 0.073895 | 0.00017657 | 64 | 26784 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace arm on Poles M12866, M0437, M0441, M0456, M0454, M0415, M0413 | .
3631 |  | JE24023637 | 39 BLACK ROAD PAENGAROA TE PUKE | Eastern | ROYDEN DOWNS RD | 2024-07-23 | 8:51 | 2024-07-23 | 14:43 | 0.059327 | 0.0001683 | 61 | 21504 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv/400vt poles,221695,221697,221698, 221700: Replace 11kv/400vt cross arms @ poles 221694 & 221696.Isolation point @ ABS .Issuer earths @ pole 221694(221693 side) | .
3632 |  | JE24023640 | 1293A ROBERTS LINE BUNNYTHORPE PALMERSTON NORTH | Western | TE ARAKURA | 2024-07-23 | 8:31 | 2024-07-23 | 14:02 | 0.015514 | 4.6902e-05 | 17 | 5623 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Change crossarms and reconductor HV on P49674, P49670 and P02238. | .
3633 |  | JE24023645 | 71 FERGUSSON STREET TOKOROA TOKOROA | Eastern | THOMPSON DR | 2024-07-23 | 23:00 | 2024-07-24 | 1:36 | 0.026209 | 0.0001683 | 61 | 9500 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - IP140-FP453-IP122 | .
3634 |  | JE24023697 | 4 SMITHS ROAD MARTON | Western | PUTORINO | 2024-07-23 | 9:41 | 2024-07-23 | 15:30 | 0.061763 | 0.00017657 | 64 | 22386 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Transformer and X arms at X2782, X1002, X1001, X1003, X1010, replace Pin arm on pole 805809 | .
3635 |  | JE24023709 | 148 ARGYLE STREET HAWERA HAWERA | Western | ARGYLE ST | 2024-07-23 | 8:47 | 2024-07-23 | 13:03 | 0.066504 | 0.00025934 | 94 | 24105 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace hv poles 703719 , 703721 , 703723 | .
3636 |  | JE24025653 | 924 POHANGINA VALLEY EAST ROAD, POHANGINA, ASHHURST, 4884 | Western | POHANGINA | 2024-07-23 | 8:30 | 2024-07-23 | 10:36 | 0.00034699 | 2.759e-06 | 1 | 126 | Unplanned | VEGETATION - OUTSIDE ZONE | Insulated lines in tree, safe at the moment. Tree trimming company required to clear tree FM to arrange urgent work request 2R left open Tree cutting carried out on 23/07/24 under urgent NAPA | .
3637 |  | JE24025795 | 387 MORRINSVILLE-TAHUNA ROAD, MORRINSVILLE, 3373 | Eastern | HORRELLS RD | 2024-07-23 | 9:40 | 2024-07-23 | 11:16 | 0.0010644 | 1.1036e-05 | 4 | 386 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Nearest ICP Used Broken 3m LV cross arm broken. TC5983 isolated and cross arm replaced. | .
3638 |  | JE24025854 | TAURIKURA DR | Eastern | TAURIKURA DR | 2024-07-23 | 10:19 | 2024-07-26 | 14:24 | 0.00019635 | 5.5179e-06 | 1 | 71 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Suspect Cable fault to transformer TP3122. Single ICP. Like a food processing plant currently not running. Customer happy for Downer to come in the morning and hook a generator on 23/07/24. 2R left open for all further work to come Repairs made 26/07/24 Generation on 23/07/24 11:13 Generation off 26/07/24 14:07 Restored via network 26/07/24 14:34 | .
3639 |  | JE24025901 | MAIN RD MOTONUI | Western | MAIN RD MOTONUI | 2024-07-23 | 1:43 | 2024-07-23 | 11:46 | 0.12971 | 0.0002152 | 78 | 47014 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 5196 No. Fuses: 2 Fuse Amp Size: 20 Amp TIME CLOSED: 11:46 Cause: Unknown Weather (wind/rain): Clear Follow up required (select advisory)? Yes Check Fuses 5196 07:09 - Rang SMC, Seth on stand down, Supervisor to get day FM to go 09:43 - Rang SMC, no one else available, Caleb on feeder fault Mangorei 5 No fault found Downer had no Field Staff available at the time to attend this fault - ICP's were left without Power for several hours. | .
3640 |  | JE24025903 | TIKORANGI | Western | TIKORANGI | 2024-07-23 | 2:02 | 2024-07-23 | 6:06 | 0.10502 | 0.00088011 | 319 | 38064 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: REC 6224 Protection flags (nil where none): C phase EF CAUSE: line down Location: between Pole 945387 & 346518 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: cursory Weather (wind/rain): fine LFI (Y/N + Comments): Failed to indicate correctly Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3641 |  | JE24025917 | JUNCTION RD | Western | JUNCTION RD | 2024-07-23 | 7:49 | 2024-07-23 | 10:20 | 0.093298 | 0.0015312 | 555 | 33816 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV MAN CB 6777/5 Protection flags (nil where none): B, C Ø HLT Trip CAUSE: Seagulls made contact with HV Lines Location: Transformer 1826N Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Clear LFI (Y/N + Comments): No, none operated on SCADA Follow up Required (select advisory)? No Additional fault restoration comments: Feeder fault while HLT was applied for CACL 112 925-01 (Field Applied) No LFI's operated at Sw/Gear 12026 - NOC opened Sw/Gear 12026/2 Back feed put in via BBK8 - NOC closed in SEC 12247/2 Field switcher instructed to remove HLT at Mangorei Line Patrol from S/S to ABS 224 - No fault was found. During the Line Patrol Field Switcher found HV Fuses blown at 6731 From ABS 224 to ABS 231 - No Fault Found From ABS 231 to Recloser 12453/2 to Sw/Gear 12026/2 to ABS 580 - No Fault Found From ABS 580 nothing abnormal was found. Finally Fuses 6731 were reloaded and closed at 10:20. All Power was restored and the Network was returned to the normal configuration. | .
3642 |  | JE24025933 | SOUTH RD CHAPEL | Western | SOUTH RD CHAPEL | 2024-07-23 | 8:30 | 2024-07-23 | 12:49 | 0.00071361 | 2.759e-06 | 1 | 259 | Unplanned | OTHER | Cause: Planned shut What was replaced? NA Where was it replaced (pole/TX/pillar box)? NA Is 2R required? N 2R Y - What is the timeframe for repairs? NA Additional Info: FM confirmed customer affected by NAPA 103962 they are fed from T1997 but not advertised, NI admin emailed | .
3643 |  | JE24025948 | MANGAWEKA | Western | MANGAWEKA | 2024-07-23 | 9:19 | 2024-07-23 | 12:50 | 0.013412 | 6.3456e-05 | 23 | 4861 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 2813 No. Fuses: 2 + 1 Barrel Fuse Amp Size: 10 Amp TIME CLOSED: 12:50 Cause: Unknown (Line Patrolled) Weather (wind/rain): Clear Follow up required (select advisory)? No Line Patrolled - No fault found. | .
3644 |  | JE24025952 | TAIRUA NORTH | Eastern | TAIRUA NORTH | 2024-07-23 | 11:20 | 2024-07-23 | 11:25 | 4.0281e-05 | 8.2769e-06 | 3 | 15 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Actual issue was high voltage due to voltage sensitive equipment, which came from transformer TC5379 Before tapping (tap 3) R Ø - 243V B Ø - 244V After tapping (tap 2) R Ø - 236V B Ø - 235V | .
3645 |  | JE24025953 | SOUTH RD NGARIKI | Western | SOUTH RD NGARIKI | 2024-07-23 | 10:55 | 2024-07-23 | 15:55 | 0.069511 | 0.00056559 | 205 | 25194 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV ABS 6768 & ABS NG341 Protection flags (nil where none): Nil CAUSE: Car vs Pole Location: Pole 712 397 (Fused Pole NG375) Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Clear LFI (Y/N + Comments): No Follow up Required (select advisory)? Yes Additional fault restoration comments: ETA 40-45 Minutes, Fire service informed Car vs Pole at Pole 712 397 - HV Lines were hanging low but did not touch the ground, for safety reasons Isolation was first carried out at ABS 6768 & ABS NG341 immediately. Once Isolation & Earthing were carried out the back feed was put in via NGA 4 by Field Switcher closing ABS NG326 Repairs are being carried out under AP 5953-01 Repairs complete and full Power restored at 15:54 SAFETY MANAGER | .
3646 |  | JE24026005 | CHURCH ST | Western | CHURCH ST | 2024-07-23 | 13:58 | 2024-07-23 | 14:30 | 0.001883 | 5.7938e-05 | 21 | 683 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: King Bolt came out of Crossarm What was replaced? Existing King Bolt refitted Where was it replaced (pole/TX/pillar box)? Pole 829385 Is 2R required? N 2R Y - What is the timeframe for repairs? Completed Additional Info: | .
3647 |  | JE24026024 | OTAKEHO | Western | OTAKEHO | 2024-07-23 | 16:19 | 2024-07-23 | 19:16 | 0.00048856 | 2.759e-06 | 1 | 177 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: Fuses 6926 No. Fuses: 3 Fuse Amp Size: 6A and 1 x barrel TIME CLOSED: 1916 Cause: age Weather (wind/rain): light rain Follow up required (select advisory)? | .
3648 |  | JE24026030 | TAWHITI RD | Western | TAWHITI RD | 2024-07-23 | 14:50 | 2024-07-23 | 17:08 | 0.0019035 | 1.3795e-05 | 5 | 690 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: CA445 No. Fuses: 2 Fuse Amp Size: 10 Amp TIME CLOSED: 17:08 Cause: Unknown Weather (wind/rain): Clear Follow up required (select advisory)? No | .
3649 |  | JE24023285 | 1353 TAIHAPE-NAPIER ROAD MOAWHANGO TAIHAPE | Western | MOAWHANGO | 2024-07-22 | 10:00 | 2024-07-22 | 14:23 | 0.001449 | 5.5179e-06 | 2 | 525 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Shut1 FFT Resag clashing conductors at poles 786642, 786648 & 786635. | .
3650 |  | JE24023297 | 172 MOERAKI ROAD HINAKURA MARTINBOROUGH | Western | COLOGNE ST | 2024-07-22 | 9:24 | 2024-07-22 | 14:30 | 0.016092 | 5.242e-05 | 19 | 5833 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Isolation for Vegetation cutting between poles 360440-816804, 816832-816833, 816824-816826 | .
3651 |  | JE24023321 | 239 TURAKINA VALLEY ROAD TURAKINA WANGANUI | Western | TURAKINA | 2024-07-22 | 9:40 | 2024-07-22 | 10:41 | 0.00066325 | 1.1036e-05 | 4 | 240 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Disconnect fuses 550, replace fuses 550 on tap off pole 794194, reconnect fuses 550 | .
3652 |  | JE24023382 | 689 RUATANGATA ROAD WHANGAEHU WANGANUI | Western | FORDELL | 2024-07-22 | 9:00 | 2024-07-22 | 14:21 | 0.016789 | 5.242e-05 | 19 | 6085 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace X arms on poles 794066, 794070, 478661 (794184) | .
3653 |  | JE24023446 | 195 PARTON ROAD PAPAMOA BEACH TE PUKE | Eastern | BLACK STUMP | 2024-07-22 | 8:30 | 2024-07-25 | 11:00 | 0.019034 | 0.00012139 | 22 | 6899 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Create 11Kv cable-break at pole 215944. Replace rusted SD switchgear 9048 base-units & coupling, also re-level pad. Reinstate 11Kv cable-break at pole 215944. | .
3654 |  | JE24023464 | 4 SURREY STREET HAWERA HAWERA | Western | ARGYLE ST | 2024-07-22 | 9:00 | 2024-07-22 | 10:59 | 0.047475 | 0.00042764 | 155 | 17207 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | install two 11kv line breaks at poles 703731 and 846455 | .
3655 |  | JE24023625 | 434 TAIRUA ROAD WHANGAMATA WHANGAMATA | Eastern | HIKUAI | 2024-07-22 | 8:45 | 2024-07-22 | 14:09 | 0.051368 | 0.00016554 | 60 | 18619 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install draw rope with drone between poles R12937 and 877108 and poles 862068 and R0761. | .
3656 |  | JE24025713 | OKOROIRE | Eastern | OKOROIRE | 2024-07-22 | 6:02 | 2024-07-22 | 19:00 | 0.073095 | 0.0001683 | 54 | 26494 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Multiple Faults/Outages caused due to Lightning in the area. Fuses Location: TC3066 No. Fuses: 1 Fuse Amp Size: 6 Amp TIME CLOSED: 07:45 Cause: Lightning Weather (wind/rain): Clear Follow up required (select advisory)? No Fuses Location: TC1578 No. Fuses: 2 Fuse Amp Size: 2 Amp TIME CLOSED: 08:04 Cause: Lightning Weather (wind/rain): Clear Follow up required (select advisory)? No Fuses Location: TC5263 No. Fuses: 2 Fuse Amp Size: 2 Amp TIME CLOSED: 08:20 Cause: Lightning Weather (wind/rain): Clear Follow up required (select advisory)? No Fuses Location: FP1538 No. Fuses: 2 Fuse Amp Size: 10 Amp TIME CLOSED: 08:44 Cause: Lightning Weather (wind/rain): Clear Follow up required (select advisory)? No Fuses Location: TC3592 No. Fuses: 2 Fuse Amp Size: 3 Amp TIME CLOSED: 09:26 Cause: Lightning Weather (wind/rain): Clear Follow up required (select advisory)? No Fuses Location: TC2519 No. Fuses: 2 Fuse Amp Size: 2 Amp TIME CLOSED: 09:50 Cause: Lightning Weather (wind/rain): Clear Follow up required (select advisory)? No Fuses Location: TC5574 No. Fuses: 3 Fuse Amp Size: 3 Amp TIME CLOSED: Closed in at 08:30 & FAILED Cause: Lightning Weather (wind/rain): Clear Follow up required (select advisory)? No Fuses Location: TC1027 No. Fuses: 3 Fuse Amp Size: 3 Amp TIME CLOSED: Closed in at 08:10 & FAILED Cause: Lightning | .
3657 |  | JE24025725 | GORDON | Eastern | GORDON | 2024-07-22 | 8:29 | 2024-07-22 | 11:15 | 0.0013735 | 8.2769e-06 | 3 | 498 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Fuses FC1109 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 11:15 Cause: Lightning Weather (wind/rain): Yes Follow up required (select advisory)?No | .
3658 |  | JE24025734 | OKOROIRE | Eastern | OKOROIRE | 2024-07-22 | 8:51 | 2024-07-22 | 11:22 | 0.0020757 | 1.3795e-05 | 5 | 752 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Transformer TC4706 No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 11:21 Cause: lightning Weather (wind/rain): lightning Follow up required (select advisory)?No | .
3659 |  | JE24025774 | HURFORD RD | Western | HURFORD RD | 2024-07-22 | 10:38 | 2024-07-22 | 12:43 | 0.052576 | 0.00045247 | 164 | 19056 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 12000/2 Protection flags (nil where none): A , C Ø E/F CAUSE: Tree fell on HV Lines Location: Pole 752 869 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Clear LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Recloser tripped at 10:37 - NOC advised CACL 112 846-02 to stand down until the Power is restored safely. Tree fell over and brought down HV Line at Pole 752 869 Repairs carried out under AP 5774-01 Full Power restored at 12:43. NOC advised CACL 112 846-02 to resume tree work as per normal at 12:59 | .
3660 |  | JE24025783 | LEPPERTON | Western | LEPPERTON | 2024-07-22 | 11:02 | 2024-07-22 | 13:31 | 0.0024634 | 1.6554e-05 | 6 | 893 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses 8160 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 13:30 Cause: Birdstrike Weather (wind/rain): Calm Follow up required (select advisory)? No | .
3661 |  | JE24025823 | OTAKEHO | Western | OTAKEHO | 2024-07-22 | 12:56 | 2024-07-22 | 14:36 | 0.0013783 | 1.3795e-05 | 5 | 500 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: Fuses TA806 CAUSE: Low hanging HV conductors Location: Pole 357 004 Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Clear Follow up required (select advisory)? Additional fault restoration comments: Low hanging HV Conductors are being re-tensioned under AP 5781-01 Repairs completed and Power restored at 14:35 | .
3662 |  | JE24025853 | PAPANUI ST | Eastern | PAPANUI ST | 2024-07-22 | 17:16 | 2024-07-22 | 22:23 | 0.00084631 | 2.759e-06 | 1 | 307 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: Fuses FC4197 Pole P0372 CAUSE:Cracked Insulator burnt end of crossarm off Location: Pole B0372 Temp generation (stage details when used): No PERFORMANCE DETAIL High Low Contact Suspected Houses Inspected. DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Rain Follow up required (select advisory)? No Additional fault restoration comments: Cracked Insulator burnt end of crossarm off dropping onto 400V Circuit, Houses Inspected all OK Broken cross-arm at Pole B0372 Awaiting crew to finish on JE2402 5713 TIR CB9 fault first and then they will come and assist on this job. Toma to organize material to get to site. Complete 22:22 | .
3663 |  | JE24025900 | UNION LINE | Western | UNION LINE | 2024-07-22 | 23:06 | 2024-07-22 | 23:58 | 0.00028538 | 5.5179e-06 | 2 | 103 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 1421 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 2357 Cause: Unknown Weather (wind/rain): fine Follow up required (select advisory)? | .
3664 |  | JE24023310 | 52 MAKOMAKO ROAD KELVIN GROVE PALMERSTON NORTH | Western | KEITH ST 14 | 2024-07-21 | 8:00 | 2024-07-21 | 11:34 | 0.002945 | 1.3795e-05 | 5 | 1067 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | CHECK HV CABLE TERMINATION AND APPLY POSSIBLE REMEDY FOR TRACKING IN THE SWITCH. (Switch gear 10026/1/2/3) | .
3665 |  | JE24025663 | NGAERE | Western | NGAERE | 2024-07-21 | 7:18 | 2024-07-21 | 8:44 | 0.0052648 | 6.0697e-05 | 22 | 1908 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 4980 No. Fuses: 2 Fuse Amp Size: 15A TIME CLOSED: 0844 Cause: Unknown Weather (wind/rain): fine Follow up required (select advisory)? | .
3666 |  | JE24024937 | SMITH ST | Eastern | SMITH ST | 2024-07-20 | 11:08 | 2024-07-20 | 12:46 | 0.018783 | 0.00019037 | 69 | 6808 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | LAK Sub - 33kV CB 3152 - B Ø Earth Fault - Line Patrol Needed - Contact Control REGULATORY INFORMATION Voltage & Device ID: LAK 3152, BRN 3062 Protection flags (nil where none): EF Line Diff B Phase CAUSE: Cable Fault Location: Between CB 3152 and Pole 339752 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): 2407012 Circuit patrolled and type: Cursory Weather (wind/rain): Rain LFI (Y/N + Comments): No Follow up Required (select advisory)? Yes Additional fault restoration comments: Cable Fault location to start 18/07/24-Mathew McCullock 11kV Isolation required on BRN CB 3 on 20/07 for repairs SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3667 |  | JE24025599 | 174 PATEA ROAD, PATEA, PATEA, 4597 | Western | OTAUTU | 2024-07-20 | 9:01 | 2024-07-20 | 11:32 | 0.0062628 | 4.1384e-05 | 15 | 2270 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Nothing tripped, so NC isolated from Gas/sw 12230-2 for the pole replacement Car V Pole ETA Please Event Number P059397479 Replace Pole 727834 NDR to follow | .
3668 |  | JE24025600 | WHARAWHARA ROAD | Eastern | WHARAWHARA ROAD | 2024-07-20 | 6:57 | 2024-07-20 | 10:17 | 0.0011057 | 5.5179e-06 | 2 | 401 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: TB1-093 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 10:17 Cause: unknown Weather (wind/rain): rain Follow up required (select advisory)? | .
3669 |  | JE24025622 | ROTOEHU | Eastern | ROTOEHU | 2024-07-20 | 11:19 | 2024-07-20 | 16:36 | 0.071443 | 0.0004304 | 156 | 25895 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 9556 Protection flags (nil where none): A,B,C O/C CAUSE: Old Dead Tree fell through Lines @ Pole 229070 Location: Pole 229070 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Curse Weather (wind/rain): Rain LFI (Y/N + Comments): Nil Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3670 |  | JE24025627 | WHARAWHARA ROAD | Eastern | WHARAWHARA ROAD | 2024-07-20 | 14:30 | 2024-07-20 | 18:46 | 0.016322 | 0.00034487 | 125 | 5916 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: CAUSE: DTX TB1-093 Failed Temp generation (stage details when used): no PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: Weather (wind/rain): Follow up required (select advisory)? Additional fault restoration comments: Failed Transformer, then saw top arms on pole where trying to fall off with old clamp style attachment 2nd outage to rectify problem then Transformer changed out | .
3671 |  | JE24025646 | HUNTERVILLE 22KV | Western | HUNTERVILLE 22KV | 2024-07-20 | 18:10 | 2024-07-20 | 19:29 | 0.15604 | 0.001992 | 722 | 56557 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: CB 4138 Protection flags (nil where none): B phase EF CAUSE: Tree contact Location: Pole 804701 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): raining LFI (Y/N + Comments): N no active LFI's on feeder Follow up Required (select advisory)? Additional fault restoration comments: No back feed was possible due to comms fail at REC 4137, OMS JE24025647 created to check batteries Unable to open recloser 4137 to be able to install back feed Branch Cleared SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3672 |  | JE24022477 | 10 JULIET STREET STRATFORD STRATFORD | Western | CLOTON RD NORTH | 2024-07-19 | 9:00 | 2024-07-19 | 14:30 | 0.17086 | 0.00051869 | 188 | 61930 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace DNO ABS 5720 structure. Replace 11KV poles 734537, 734542, 734544, 734550 and 734552. 23 Juliet Street, Stratford - Tag A42027 and 24 Juliet Street, Stratford - Tag A42026. Left off, could not do testing. Added into safety tag reg. Will reconnect under the NAPA tonight. | .
3673 |  | JE24023216 | 406 DEVON STREET WEST LYNMOUTH NEW PLYMOUTH | Western | WHITELEY ST | 2024-07-19 | 8:37 | 2024-07-19 | 14:24 | 0.063801 | 0.00071457 | 162 | 23125 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | DNO 2406002. Replace faulty cablebetween SW 83/3 and Magnefix 306/1. Staged outage work over 2 days. Day 1, disconnect and remove faulty cable from SW 83/3. Then install and connect new cable at SW 83/3. Day 2, remove Magnefix 306. Install new switchgear 12780 . Install, joint/terminate and connect new HV cables as per new configuration. Then test cables, liven to phase and restore network. No outage today 18/07/24 | .
3674 |  | JE24023256 | 1226 ROBERTS LINE BUNNYTHORPE PALMERSTON NORTH | Western | TE ARAKURA | 2024-07-19 | 8:30 | 2024-07-19 | 12:08 | 0.010219 | 4.6902e-05 | 17 | 3704 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Change Xarms from P06511 to P49671 and reconductor LV on P06501 and P06504 | .
3675 |  | JE24023277 | 53 PUKEOKAHU ROAD TAOROA JUNCTION TAIHAPE | Western | PAPAKAI | 2024-07-19 | 9:45 | 2024-07-19 | 11:22 | 0.0021251 | 2.2072e-05 | 8 | 770 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace TX X670 with a 50KVa | .
3676 |  | JE24023436 | 2405 MOUNTAIN ROAD TARIKI INGLEWOOD | Western | CLOTON RD SOUTH | 2024-07-19 | 9:37 | 2024-07-19 | 14:17 | 0.0046411 | 1.6554e-05 | 6 | 1682 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 757807, Re-sag spurline between poles 757802 and 757803 - 757806 and 757805 | .
3677 |  | JE24024441 | 21 BLACK ROAD PAENGAROA TE PUKE | Eastern | ROYDEN DOWNS RD | 2024-07-19 | 9:30 | 2024-07-19 | 14:19 | 0.045399 | 0.00015726 | 57 | 16455 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv/400vt poles, 221733,221691,221692,221693: isolation and issuer earths @ ABS 14861 | .
3678 |  | JE24024834 | 2 SUNVALE PLACE GATE PA TAURANGA | Eastern | GATE PA | 2024-07-19 | 8:45 | 2024-07-19 | 16:34 | 0.19315 | 0.002003 | 398 | 70008 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install cable break at pole 481967 Replace 11kV RMU 13223, damaged by vehicle. Close cable break at pole 481967 | .
3679 |  | JE24025421 | PUTORINO | Western | PUTORINO | 2024-07-19 | 7:06 | 2024-07-19 | 14:30 | 0.034797 | 0.0009077 | 131 | 12612 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faultman found ABS 4087 at the Sub was arcing badly, CB 1488 was opened and ABS 4087 opened ABS 4066 closed to restore supply. Line was isolated at ABS's 4002, 2512 & 2570 & 2856 to replace ABS 4087 and make repairs to ABS 4066. | .
3680 |  | JE24025445 | MOWBRAY RD | Eastern | MOWBRAY RD | 2024-07-19 | 9:10 | 2024-07-19 | 10:56 | 0.0037848 | 3.5867e-05 | 13 | 1372 | Unplanned | WILDLIFE - BIRD | Fuses Location: FC2150 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 10:45 Fuses Location: FP58 No. Fuses: 1 Fuse Amp Size:10 TIME CLOSED: 10:55 Cause: Bird strike Weather (wind/rain): FINE Follow up required (select advisory)?NA | .
3681 |  | JE24025465 | TE PUKE NORTH | Eastern | TE PUKE NORTH | 2024-07-19 | 13:21 | 2024-07-23 | 18:53 | 0.0026046 | 4.1384e-05 | 11 | 944 | Unplanned | THIRD PARTY INTERFERENCE - DIG IN | Generation connected to 400V of transformer TE5-224 @ 15:40, 11kV Cable hit with Digger Blew 1 11kV fuse inside Fuse Sw 9383/2 , SW/G 9383/2 intrenal Mech was Jammed & Fuse sw 9383/2 never opened when striker hit leaving the Cable alive on 2 Phases. Both 9383 & 9382 where marked as SDAF Series 1 so safety isolation procedures used. then the SCADA Tile changed while I was Operating ( Refer Printed Tile for changes) RMU Sw/Gear 9383/ Completely isolated to allow to change Sw/Gear out Sw/Gear replaced 23/07/24 Gen removed 18:39, Power restored 18:53 | .
3682 |  | JE24025578 | 55A PAUL ROAD, TAIRUA | Eastern | TAIRUA NORTH | 2024-07-19 | 21:21 | 2024-07-20 | 0:46 | 0.00056793 | 2.759e-06 | 1 | 206 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | lightning arrestor failed at Fused ABS IP195 1 fuse found blown on arrival, became 3 phase when FABS IP195 opened 21:20 Lightning arrestor replaced | .
3683 |  | JE24028583 | 2 SUNVALE PLACE GATE PA TAURANGA | Eastern | GATE PA | 2024-07-19 | 8:46 | 2024-07-19 | 8:48 | 4.1201e-05 | 1.9313e-05 | 7 | 15 | Unplanned | HUMAN ERROR - POTENTIAL SWITCHING ERROR | Customers on tx TP2528 were affected by planned outage after notification sent to retailers advising they would not be affected. Switching sheet not corrected after amended notification sent to retailers. Power isolated at 08:45 restored at 08:47. Related as non planned outage | .
3684 |  | JE24022484 | 23 HEREFORD STREET MARTON MARTON | Western | MARTON | 2024-07-18 | 10:01 | 2024-07-18 | 11:28 | 0.00096012 | 1.1036e-05 | 4 | 348 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace MDI meters for transformer 3247W | .
3685 |  | JE24022749 | 505 NO 3 LINE OKOIA WANGANUI | Western | NO 3 LINE | 2024-07-18 | 9:04 | 2024-07-18 | 14:47 | 0.021765 | 6.3456e-05 | 23 | 7889 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace defected 11KV poles & X-Arms between 790939 & 790985 | .
3686 |  | JE24022772 | 48 BELT ROAD MOTUROA NEW PLYMOUTH | Western | CITY 9 | 2024-07-18 | 8:45 | 2024-07-18 | 16:25 | 0.13072 | 0.00028417 | 103 | 47380 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Transformer 980 with a 500kVA Ground Mounted Transformer 2525N Replace OH with UG cable between poles 843250 & 700414. Cable join to existing UG at pole 843250 | .
3687 |  | JE24023085 | 3000 TAIRUA ROAD PUKEPOTO HIKUAI | Eastern | HIKUAI | 2024-07-18 | 8:46 | 2024-07-18 | 18:15 | 0.036081 | 8.001e-05 | 29 | 13078 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install fibre between poles 383157 & U12632 Pole 383159 found to be cracked to point of being required to change. Outage shorted down after original permit to recloser 9643 links & ABS to ABS IC352 so pole can be replaced. | .
3688 |  | JE24023088 | 204 COLOMBO ROAD KURIPUNI MASTERTON | Western | COLOMBO RD | 2024-07-18 | 8:52 | 2024-07-18 | 15:15 | 0.36131 | 0.00094357 | 342 | 130958 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv pole 833039 | .
3689 |  | JE24023097 | 91 MILL ROAD PAEROA | Eastern | TIROHIA-KARANGAHAKE | 2024-07-18 | 9:00 | 2024-07-18 | 15:40 | 0.01545 | 3.8625e-05 | 14 | 5600 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv pole's N13242,N1263,876686,N1266 and N1267 | .
3690 |  | JE24023120 | 221 ROSEBERY STREET TOKOROA TOKOROA | Eastern | CAMPBELL ST | 2024-07-18 | 23:30 | 2024-07-19 | 1:24 | 0.016601 | 0.00014623 | 53 | 6017 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kV oil maintenance - IC1896-TC3182-IC1891 | .
3691 |  | JE24023122 | 997 KAHUTARA ROAD KAHUTARA FEATHERSTON | Western | KUMENGA | 2024-07-18 | 9:45 | 2024-07-18 | 16:42 | 0.050561 | 0.00012139 | 44 | 18326 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Removal of trees at pole site 378128 | .
3692 |  | JE24023131 | 747 PUTORINO ROAD HUNTERVILLE MARTON | Western | PUTORINO | 2024-07-18 | 8:30 | 2024-07-18 | 14:27 | 0.017729 | 4.9661e-05 | 18 | 6426 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace all crossarms on pole 805975 and replace service pole 805976. | .
3693 |  | JE24023134 | 278 MANGAMAHOE CENTRAL ROAD EKETAHUNA MASTERTON | Western | MAURICEVILLE | 2024-07-18 | 9:32 | 2024-07-18 | 14:17 | 0.016512 | 5.7938e-05 | 21 | 5985 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace red tag pole P15762 , 11kv xarms at P15755, P15774,P15724,P15773,P15709 | .
3694 |  | JE24023135 | 152 BLAIRLOGIE-LANGDALE ROAD BLAIRLOGIE MASTERTON | Western | MANGAPAKEHA | 2024-07-18 | 9:16 | 2024-07-18 | 14:35 | 0.038435 | 0.0001545 | 56 | 13931 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Structure maintenance | .
3695 |  | JE24023229 | 238 SANDON BLOCK ROAD-MANGAMAKO RD-ORANGIPONGO RD OHINGAITI HUNTERVILLE | Western | RANGIWAHIA | 2024-07-18 | 8:30 | 2024-07-18 | 14:00 | 0.066416 | 0.0002014 | 73 | 24073 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles, crossarms at P07092, P07094, P07099, P10002, P26475, P08415 and P10043 and repair conductor at P23653, install arm brace: P09709, P09618, P08416. | .
3696 |  | JE24025252 | MANGATOKI | Western | MANGATOKI | 2024-07-18 | 2:30 | 2024-07-18 | 3:40 | 0.00058332 | 8.2769e-06 | 3 | 211 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 5264 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 03:40 hrs Cause: Unk / Suspect Bird Strike Weather (wind/rain): Light Rain Follow up required (select advisory)? | .
3697 |  | JE24025273 | SOUTH RD CHAPEL | Western | SOUTH RD CHAPEL | 2024-07-18 | 8:52 | 2024-07-18 | 15:14 | 0.0010539 | 2.759e-06 | 1 | 382 | Unplanned | OTHER | Cause: HV Planned outage - IS 2R required? N Additional Info: Planned HV outage 111616. Customer feeds off TX T306 NI Admin e-mailed | .
3698 |  | JE24025282 | MARAETAI ROAD 33kV | Eastern | MARAETAI ROAD 33kV | 2024-07-18 | 9:21 | 2024-07-18 | 12:48 | 0.62927 | 0.019426 | 7041 | 228083 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 33KV CB 2242 (KIN GXP) & CB 42 (BRD Sub) Protection flags (nil where none): Neutral Time O/C CAUSE: Magpie on line at pole KINBRD086 & Fualt Suspect 33kv Cable fault Location: 33KV Pole KINBRD 086 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: n Weather (wind/rain): foggy LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Fault 1: 33KV fault on pole KINBRD 086 caused 400v cables to be blown off pole and the fault went back through the 400V cables and blow the leads off transformer TC2420, Tfr TC2420 was isolated to carry out repairs on LV network, 2 customers have been safety disconnected until meter board and service cable replaced. 213 Baird Rd, Tokoroa - A39474 - Meter board to be replaced 237 Baird Rd, Tokoroa - A39473 - Service cable to be replaced. 223 Baird Rd, Tokoroa - A39472 - Service Cable to be repaired. Safety tag reg has been updated and all retailers have been emailed and notified by the team onsite about faults and meter replacements. Fault 2: Suspect 33KV Cable between KIN GXP CB 2242 & ABS 44 at ripple plant to be tested 19/07/24 33kV Cable Fault was found and repaired under AP. Cable was then tested and the results prov | .
3699 |  | JE24025324 | RAHOTU | Western | RAHOTU | 2024-07-18 | 11:40 | 2024-07-18 | 15:24 | 0.00061833 | 2.759e-06 | 1 | 224 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 6769 No. Fuses: 2 Fuse Amp Size:6 TIME CLOSED: 15:24 Cause: suspected Bird Strike Weather (wind/rain): Drizzle Follow up required (select advisory)?NA Original job logged to the wrong TX should have been 5287E | .
3700 |  | JE24025335 | KAIHERE | Eastern | KAIHERE | 2024-07-18 | 12:22 | 2024-07-18 | 15:34 | 0.002655 | 1.3795e-05 | 5 | 962 | Unplanned | WILDLIFE - BIRD | Fuses Location: FC 762 No. Fuses: 2 Fuse Amp Size: 25 TIME CLOSED: 15:34 Cause: bird strike Weather (wind/rain): Follow up required (select advisory)? Yes Locations identified by faultman & with information provided from local farmer. Bird reflectors would be of use between poles O187-0179. These are locations where the faultman has repaired lines down and where the farmer has found dead swans in his fields. In Dec 2023 to Feb 2024 there were 3 or 4 outages on the feeder due to swans through the lines past ABS 1245 and LFI's were added to the spur line at the ABS and between FC762 & FP109, swans continue to be a problem. | .
3701 |  | JE24025363 | SOUTH RD CHAPEL | Western | SOUTH RD CHAPEL | 2024-07-18 | 8:52 | 2024-07-18 | 15:14 | 0.0010539 | 2.759e-06 | 1 | 382 | Unplanned | OTHER | Please get information from Faultman about which Transformer customer is fed from on closure. Was part of NAPA 111616 but not advertised FM confirmed correct transformer T306. Customer has power restored as part of NAPA AI team and Network connections advised | .
3702 |  | JE24025394 | CHURCH ST | Western | CHURCH ST | 2024-07-18 | 17:31 | 2024-07-18 | 19:37 | 0.043137 | 0.00053524 | 194 | 15635 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV Reclosure C279/2 Protection flags (nil where none): C Ph O/C, E/F CAUSE: Wildlife (Goose) Location: Pole 829 494 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Clear LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Yes Additional fault restoration comments: After Recloser C279/2 tripped. Field Switcher started with a Line Patrol and sectionalizing up to ABS S95 & then ABS S74 A dead bird & HV Line down was found at Pole 829 494 Repairs being carried out under AP 5394 Full Power restored at 19:37 | .
3703 |  | JE24019357 | 286 WOODLAND ROAD TAHAWAI | Eastern | LINDERMANN RD | 2024-07-17 | 9:12 | 2024-07-17 | 15:58 | 0.043412 | 0.00012415 | 45 | 15735 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Reconductor 11kV between Poles 204422 & 204430. Isolation SB1-025. Transformer TB1-001 was left isolated at end of switching for safety will crew completed LV reconductoring supply restored at 15:58. | .
3704 |  | JE24022628 | 14740 ROUTE 52 ALFREDTON EKETAHUNA | Western | BROOKLANDS | 2024-07-17 | 9:34 | 2024-07-17 | 14:10 | 0.015228 | 5.5179e-05 | 20 | 5519 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace red tag pole P08283 resag 11kv conductor at P08280 & 469601 | .
3705 |  | JE24022638 | 1752 WAIHI VALLEY ROAD, PONGOROA | Western | HOROEKA | 2024-07-17 | 8:30 | 2024-07-17 | 16:50 | 0.15036 | 0.00030073 | 109 | 54500 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Perform ABS Maintenance at V15 & V7, recloser maintenance at V5, Remove TEMP119 at pole P04875 Notes on SIS - Late restoration due to weather | .
3706 |  | JE24022640 | 91 ASHWORTH STREET TOKOROA TOKOROA | Eastern | ASHWORTH ST | 2024-07-17 | 23:31 | 2024-07-18 | 2:26 | 0.00048415 | 2.759e-06 | 1 | 175 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - IC3217-FC5053-IC3082 | .
3707 |  | JE24022686 | 88 TUTAENUI ROAD MARTON MARTON | Western | TUTAENUI | 2024-07-17 | 9:28 | 2024-07-17 | 11:55 | 0.017845 | 0.00012139 | 44 | 6468 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace faulty MDI meters for 1095W | .
3708 |  | JE24022759 | 6 ALEXANDER PLACE PAPAMOA BEACH TAURANGA | Eastern | GRAVATT RD | 2024-07-17 | 9:00 | 2024-07-17 | 13:45 | 0.10567 | 0.00078355 | 284 | 38300 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 381348 with B11 pole and terminate new 3c 185mm cable onto the crucifix . Remove old 3c 25mm cable cut and abandon. Access and disconnect existing cable at switch 13846/1 cut and abandon. Terminate new 3c 185mm cable and liven Phasing check across switch 13846/1 | .
3709 |  | JE24023043 | 4 RANGATAUA STREET WELCOME BAY TAURANGA | Eastern | WELCOME BAY | 2024-07-17 | 9:35 | 2024-07-17 | 16:38 | 0.13421 | 0.00031728 | 115 | 48645 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install automation retrofit kit on the existing ABB Safelink 13037. Job had an over run due to motor problems with Sw/Gear 13037/3 | .
3710 |  | JE24023048 | 23 KIATERE STREET RATANA WANGANUI | Western | TURAKINA | 2024-07-17 | 8:40 | 2024-07-17 | 15:16 | 0.021826 | 5.5179e-05 | 20 | 7911 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install line break at pole 794865, replace Transformer pole 794867, remove line break | .
3711 |  | JE24023412 | 48 WAHITAPU LANE OPOUTERE WHANGAMATA | Eastern | OPOUTERE | 2024-07-17 | 9:50 | 2024-07-17 | 10:16 | 6.9526e-05 | 2.759e-06 | 1 | 25 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Tap down TP4290 one Tap | .
3712 |  | JE24025042 | 2294 STATE HIGHWAY 25, WHANGAMATA | Eastern | WHIRITOA | 2024-07-17 | 12:53 | 2024-07-17 | 13:26 | 0.0061093 | 0.00018485 | 67 | 2214 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Broken binder on Pole WHIWGN147 No immediate risk involved, it is secure as per Field Switcher. Emergency shut will be arranged for 17/07/2024. Line was isolated at ABS IC251 & Links 13079/4 to rebind in jumper at transformer TC2445. | .
3713 |  | JE24025113 | PUTORINO | Western | PUTORINO | 2024-07-17 | 6:03 | 2024-07-17 | 13:50 | 0.05866 | 0.0002621 | 52 | 21262 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: Recloser 4246 Protection flags (nil where none): EF, Ph A,C OC CAUSE: Arcing ABS (found 19/07) Location: ABS 4087 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: Operational Weather (wind/rain): Calm LFI (N + Comments): Follow up Required (select advisory)? No Additional fault restoration comments: While patrolling also installing bird deterrents at Transformers Z67 & 4300W under access permits Crew also cutting trees between Transformers Z166 & Z171 Backfeed via ABS 089 left in place until 19/07 REF : JE24025421- Fault found at RAT Sub on 11KV ABS 4087. | .
3714 |  | JE24025114 | WELCOME BAY | Eastern | WELCOME BAY | 2024-07-17 | 8:31 | 2024-07-17 | 10:46 | 0.025318 | 0.00018761 | 68 | 9177 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Cable fault feeding tx TD4-537. Isolated fuses SD4-135 to install generator. Generator installed 17/07 1045am to tx TD4-537. 23/07/24 DNO 2407016 Created to be completed under a planned NAPA. | .
3715 |  | JE24025127 | WAITOTARA | Western | WAITOTARA | 2024-07-17 | 7:48 | 2024-07-17 | 10:52 | 0.016241 | 8.8287e-05 | 32 | 5887 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 2719 No. Fuses: 2 Fuse Amp Size: 30a TIME CLOSED: 10:52 Cause: Suspected bird strike Weather (wind/rain): Calm over cast Follow up required (select advisory)? NA | .
3716 |  | JE24025174 | TE MATAI RD | Eastern | TE MATAI RD | 2024-07-17 | 12:40 | 2024-07-17 | 13:51 | 0.00078355 | 1.1036e-05 | 4 | 284 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Repair broken jumper on Tfr TE6-120, Tfr TE6-120 was isolated to repair the jumper due to deteriation. | .
3717 |  | JE24025180 | MOROA | Western | MOROA | 2024-07-17 | 11:06 | 2024-07-17 | 15:23 | 0.082407 | 0.00072561 | 263 | 29869 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11KV CB C956 Protection flags (nil where none): A & B & C Phase O/C Invt CAUSE: Conductor down Location: Pole 816280 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Told by owner of house Weather (wind/rain): Fine LFI (Y/N + Comments): Yes and worked well Follow up Required (select advisory)? Additional fault restoration comments: 11KV /400v Clash Inspector has been and everything is OK | .
3718 |  | JE24025181 | KAKARIKI | Western | KAKARIKI | 2024-07-17 | 11:05 | 2024-07-17 | 12:51 | 0.00058439 | 5.5179e-06 | 2 | 212 | Unplanned | WILDLIFE - BIRD | Fuses Location: M86 No. Fuses: 2 Fuse Amp Size:3 TIME CLOSED: 12:50 Cause: Wild life - Line Crosses a Dam Weather (wind/rain): Calm /overcast Follow up required (select advisory)?NA | .
3719 |  | JE24025235 | 604 BRUNSKILL ROAD, TE MIRO, CAMBRIDGE, 3496 | Eastern | TE MIRO RD | 2024-07-17 | 18:47 | 2024-07-17 | 19:43 | 0.00030818 | 5.5179e-06 | 2 | 112 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: TX TC2833 Fuses (Safety Isolation) Location: TX TC2833 CAUSE: Deterioration Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Rain Follow up required (select advisory)?No Additional fault restoration comments: Create safety panel to carry out repairs to burnt termination on LV O/H at Transformer TC2833 Full Power restored at 19:42 Three different jobs involved which were all linked - Main Transformer Switched off was TC2833. Please see linked Jobs. | .
3720 |  | JE24025239 | BLAIRLOGIE | Western | BLAIRLOGIE | 2024-07-17 | 18:45 | 2024-07-17 | 21:25 | 0.00044086 | 2.759e-06 | 1 | 160 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses 8164 No. Fuses: 2 Fuse Amp Size: 10 Amp TIME CLOSED: 21:25 Cause: Bird strike Weather (wind/rain): Rain Follow up required (select advisory)? No | .
3721 |  | JE24020769 | 31 PITT STREET WHANGANUI WANGANUI | Western | PITT ST | 2024-07-16 | 11:45 | 2024-07-16 | 11:46 | 0.00023451 | 0.00023451 | 85 | 85 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Preform screen tests on 33kv cable at pole 706045 and CB2142 Hatricks Wharf Sub . | .
3722 |  | JE24022329 | 997 KAHUTARA ROAD KAHUTARA FEATHERSTON | Western | KUMENGA | 2024-07-16 | 8:30 | 2024-07-16 | 15:16 | 0.04928 | 0.00012139 | 44 | 17862 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Removal of trees at pole site 378128 | .
3723 |  | JE24022450 | 119 CENTRAL MANGAONE ROAD EKETAHUNA EKETAHUNA | Western | EKETAHUNA | 2024-07-16 | 9:00 | 2024-07-16 | 15:10 | 0.021437 | 5.7938e-05 | 21 | 7770 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Change 11kv poles & arms from T8/41 to end of line | .
3724 |  | JE24022455 | 96 OXFORD ROAD OKATO OKATO | Western | INLAND COAST | 2024-07-16 | 9:30 | 2024-07-16 | 15:10 | 0.10131 | 0.00029797 | 108 | 36720 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 755788 and install new Entec/Links/TX/ABS structure & Remove fuses 8418 from pole 757684 | .
3725 |  | JE24022456 | 16 LOGAN STREET TOKOROA TOKOROA | Eastern | CAMPBELL ST | 2024-07-16 | 23:30 | 2024-07-17 | 2:31 | 0.00050034 | 2.759e-06 | 1 | 181 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9191-1/2/3 | .
3726 |  | JE24022466 | 107 BUICK CRESCENT AWAPUNI PALMERSTON NORTH | Western | PIONEER | 2024-07-16 | 9:45 | 2024-07-16 | 11:05 | 0.072395 | 0.00090494 | 328 | 26240 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Perform 11kv magnefix maintenance at MS13 | .
3727 |  | JE24022491 | 1470 PAREWANUI ROAD PAREWANUI BULLS | Western | PAREWANUI | 2024-07-16 | 8:48 | 2024-07-16 | 13:18 | 0.0022348 | 8.2769e-06 | 3 | 810 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 809511 and 809503 including transformer X2177. | .
3728 |  | JE24022511 | 81 DENNY HULME DRIVE MOUNT MAUNGANUI TAURANGA | Eastern | EVERSHAM RD | 2024-07-16 | 8:31 | 2024-07-16 | 15:08 | 0.20933 | 0.00052696 | 191 | 75872 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace rusted out SD switchgear base-unit at SD5-230>233 | .
3729 |  | JE24022558 | 5 BLACK ROAD PAENGAROA TE PUKE | Eastern | ROYDEN DOWNS RD | 2024-07-16 | 9:12 | 2024-07-16 | 16:26 | 0.14967 | 0.00034487 | 125 | 54250 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv/400vt poles 221654,221659, 221654,221660,221690: replace 11kv/400vt cross arms @ pole 221688: Install new ABS # 14861 @ pole 221689. Replace Hv conductor with New 3W Squirrel between poles 221654 & 221690 | .
3730 |  | JE24022592 | 22 MANGATI ROAD BELL BLOCK NEW PLYMOUTH | Western | KATERE 12 | 2024-07-16 | 8:30 | 2024-07-17 | 14:17 | 0.12823 | 0.00061801 | 167 | 46479 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | ELE020758 TAR GM Switchgear - Magnefix. Systematic/staged 4 day replacement of Magnefix 322 with new Safelink unit. Due to SAIDI requirements, DAY 1 & 2 shuts was done on NAPA 110739. Then min 5 day gap was left before Day 3 & 4 shuts. This NAPA is for Day 3 & 4 shuts. | .
3731 |  | JE24022599 | 295 DALEFIELD ROAD DALEFIELD CARTERTON | Western | BELVEDERE | 2024-07-16 | 8:45 | 2024-07-16 | 13:54 | 0.028133 | 9.1046e-05 | 33 | 10197 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replacement of tx structure T741 and hardware at T2366 | .
3732 |  | JE24023118 | 460 YOUNGSON ROAD WHAKAMARAMA | Eastern | WHAKAMARAMA | 2024-07-16 | 9:06 | 2024-07-16 | 15:08 | 0.034956 | 9.6564e-05 | 35 | 12670 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Upgrade TX structure TD2-069 | .
3733 |  | JE24024951 | sub_PGA | Eastern | ROYDEN DOWNS RD | 2024-07-16 | 7:25 | 2024-07-16 | 9:08 | 0.037555 | 0.00074768 | 271 | 13612 | Unplanned | WILDLIFE - POSSUM | REGULATORY INFORMATION Voltage & Device ID: 11kV PGA CB5 Protection flags (nil where none): B Ø E/F CAUSE: Wildlife - Possum Location: Pole 231 074 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Calm LFI (Y/N + Comments): None operated. Follow up Required (select advisory)? Yes Additional fault restoration comments: This feeder tripped during the night and no fault was found as per Warren Ngata Planned switching on this Feeder NAPA 111 080 was put on hold to carry out fault-finding. 1st Back feed was put in via PKW4 - Sw/Gear 14407/3 NOC Opened & REC 9463/2 NOC Closed in at 07:30 ABS SE6-047 was opened and NOC Closed in PGA CB5 at 07:53 Line Patrol down past Old Coach Rd Field Switcher then found a dead possum at Pole 231 074 Isolation and Earthed work area between ABS SF6-013 & ABS SE6-047 Remaining Network was restored via closing Sw/Gear 14407/3 at 08:36 & then REC 9987/2 NOC Closed in at 08:37 Two cracked insulators were changed under AP 4951-01 After repairs were made Power restored via closing ABS SF6-013 at 09:07 Planned NAPA 111 080 was then started at approx. 09:11 | .
3734 |  | JE24024973 | PARIHAKA | Western | PARIHAKA | 2024-07-16 | 11:28 | 2024-07-16 | 12:29 | 0.0050489 | 8.2769e-05 | 30 | 1830 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Replaced king bolt at Pole 709971 | .
3735 |  | JE24024996 | dtx_2111T | Western | TE ROTI | 2024-07-16 | 10:08 | 2024-07-16 | 10:56 | 0.00025999 | 5.5179e-06 | 2 | 94 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Repair stay at Transformer 2111T, Hanging loose and too close to live conductors Replaced stay wire and stay insulator, but pole to defected . Structural Defect because the Transformer is on the wrong side | .
3736 |  | JE24025001 | 1529 RANGITATAU EAST ROAD, KAI IWI, WANGANUI, 4578 | Western | WATERWORKS RD | 2024-07-16 | 10:21 | 2024-07-16 | 14:20 | 0.0019826 | 8.2769e-06 | 3 | 719 | Unplanned | VEGETATION - OUTSIDE ZONE | Cause: Hit by a tree What was replaced? Spragged conductor at pole 481146 Where was it replaced (pole/TX/pillar box)? Isolation from Fuses 16077 Is 2R required? YES 2R Y - What is the timeframe for repairs? Tomorrow Additional Info: 2R to be used for a emergency outage tomorrow to replace the span of conductor. Traffic management needed. Emergency Outage E00140 advertised 15/07 ~15:00, outage is unplanned. | .
3737 |  | JE24025018 | RANGITANUKU RD | Eastern | RANGITANUKU RD | 2024-07-16 | 12:10 | 2024-07-16 | 14:00 | 0.0012226 | 1.1036e-05 | 4 | 443 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: Fuses FC912 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 14:00 Cause: Wind Weather (wind/rain): Yes Follow up required (select advisory)? No | .
3738 |  | JE24025027 | TAVERNER ST | Western | TAVERNER ST | 2024-07-16 | 13:20 | 2024-07-16 | 13:27 | 0.0090999 | 0.0013215 | 479 | 3298 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11KV Rec 11141 Protection flags (nil where none): A & C Phase O/C E/F CAUSE: Bird in lines Location: Transformer T1024 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: None Faultman was 2 Poles away Weather (wind/rain): Fine LFI (Y/N + Comments): No Follow up Required (select advisory)? Additional fault restoration comments: | .
3739 |  | JE24025035 | 109 TE TUHI ROAD, OKAUIA, MATAMATA, 3471 | Eastern | GORDON | 2024-07-16 | 15:09 | 2024-07-17 | 14:48 | 0.00072009 | 1.6554e-05 | 3 | 261 | Unplanned | THIRD PARTY INTERFERENCE - OTHER | Removed bailing from conductors and cut away stay wire touching lines Isolation at Fuses FC1469 Coming back 17/07/24 to replace stay wire-no access due to wet ground, need 4 x 4 truck. 2R left open to replace stay 17/07/17 13:50 to 14:48 | .
3740 |  | JE24025044 | 105 TE MAIRE ROAD, FEATHERSTON | Western | DAIRY FACTORY | 2024-07-16 | 17:42 | 2024-07-16 | 20:33 | 0.044957 | 0.00026762 | 97 | 16295 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV C917 Protection flags (nil where none): None CAUSE: Rebind at 2 poles reported by Poletech Location: 799439 & 799440 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Fine LFI (Y/N + Comments): Nil Follow up Required (select advisory)? No Additional fault restoration comments: Initial fault was to Rebind at 2 poles reported by Poletech. During fault switching, the bypass ABS 11235/1 was closed when the regulators weren't in Neutral Tap. This blew the tails off ABS 11235/1. Additional isolations were used to Rebind the pole & repair the ABS. Next day regulator set was tested & returned to service, no damage | .
3741 |  | JE24025077 | PAREWANUI | Western | PAREWANUI | 2024-07-16 | 20:22 | 2024-07-17 | 1:14 | 0.015375 | 0.0013657 | 297 | 5573 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV, Rec 717 Auto Reclosed Protection flags (nil where none): O/C B-C phase CAUSE: Blown Jumper due to corrosion Location: Pole 458397 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Yes/ Operational Weather (wind/rain): Calm LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Rec 717 Auto Reclosed. This was followed shortly after by multiple part powers. Break Make backfeed installed via VS912. Fault located and Isolated at Rec 717 for repairs. Another break before make required to remove VS912 backfeed. | .
3742 |  | JE24025091 | PIRINOA | Western | PIRINOA | 2024-07-16 | 20:55 | 2024-07-17 | 0:10 | 0.001614 | 8.2769e-06 | 3 | 585 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: T1063 Fuses CAUSE: Internal failure Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): N/A Circuit patrolled & type: N/A Weather (wind/rain): Calm / misty Follow up required (select advisory)? No Additional fault restoration comments: 1 x 15kVA 1 Ø transformer replaced. | .
3743 |  | JE24025107 | PUTORINO | Western | PUTORINO | 2024-07-16 | 23:51 | 2024-07-17 | 2:56 | 0.026554 | 0.00014347 | 52 | 9625 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV, Rec 4246/2 Protection flags (nil where none): E/F A phase CAUSE: ABS 4087 burning up, Found on 19/0724 JE24025421 Location: Unk Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes / Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: | .
3744 |  | JE24022286 | 194 JUNCTION ROAD NORTH KIMBOLTON FEILDING | Western | RANGIWAHIA | 2024-07-15 | 8:31 | 2024-07-15 | 12:08 | 0.0059929 | 2.759e-05 | 10 | 2172 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace crossarms at P05550 and P26616. And base fill at P05566 to cover exposed earth. | .
3745 |  | JE24022312 | 1954 LAKE FERRY ROAD PIRINOA FEATHERSTON | Western | BURNSIDE | 2024-07-15 | 9:31 | 2024-07-15 | 11:47 | 0.00072552 | 5.5179e-06 | 2 | 263 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Create line break live line, replace cross arm at pole 810904 and re instate line break | .
3746 |  | JE24022326 | 304 KIRI ROAD TE KIRI OPUNAKE | Western | IHAIA RD | 2024-07-15 | 9:22 | 2024-07-15 | 16:51 | 0.030938 | 6.8974e-05 | 25 | 11214 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace DNO ABS TA108 at pole 715661 | .
3747 |  | JE24022391 | 225 KAUANGAROA ROAD FORDELL WANGANUI | Western | FORDELL | 2024-07-15 | 9:15 | 2024-07-15 | 14:16 | 0.011196 | 0.00092977 | 171 | 4058 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace X arms on pole number 791378 | .
3748 |  | JE24022445 | 1172 ROBERTS LINE BUNNYTHORPE PALMERSTON NORTH | Western | TE ARAKURA | 2024-07-15 | 8:53 | 2024-07-15 | 13:24 | 0.012747 | 4.6902e-05 | 17 | 4620 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Change crossarms between and including P19820 and P19816 plus reconductor LV on 872841,P19817,P19816 | .
3749 |  | JE24022494 | 743 LICHFIELD ROAD LICHFIELD PUTARURU | Eastern | LICHFIELD | 2024-07-15 | 9:06 | 2024-07-15 | 14:45 | 0.032775 | 9.6564e-05 | 35 | 11880 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | PQR - To upgrade TC3669 to 50kVA 3 phase and install new TP4425 30kVA 3 phase on Pole M1027 | .
3750 |  | JE24023580 | 173 PAHAUTEA ROAD KAHUTARA FEATHERSTON | Western | DAIRY FACTORY | 2024-07-15 | 10:15 | 2024-07-15 | 12:15 | 0.029078 | 0.00024279 | 88 | 10539 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove damaged wrap locks and fit armour rods and binder at poles 812833 & 812840 | .
3751 |  | JE24024853 | RANGITANUKU RD | Eastern | RANGITANUKU RD | 2024-07-15 | 12:37 | 2024-07-15 | 15:02 | 0.0019983 | 1.3795e-05 | 5 | 724 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: Fuses FC4155 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 15:02 Cause: wInd Weather (wind/rain): windy Follow up required (select advisory)? No | .
3752 |  | JE24024874 | CROWN | Western | CROWN | 2024-07-15 | 14:07 | 2024-07-15 | 15:51 | 0.0089326 | 0.0001545 | 56 | 3238 | Unplanned | HUMAN ERROR - POTENTIAL WORKMANSHIP | REGULATORY INFORMATION Voltage & Device ID: 11kV, CB 15 Protection flags (nil where none): O/C A-B-C phase CAUSE: Live Cable Spiked whilst Identification of redundant cables was taking place. Location: Sw/Gear 10446/1 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: N/A Weather (wind/rain): N/A LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Live 11kV Cable spiked when Omexom were overseeing the earthworks at a new development. Omexom carried out repairs to the privately owned cable that was affected. Omexom and Downer were involved in restoration switching to restore power. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3753 |  | JE24024880 | HAURAKI RD | Eastern | HAURAKI RD | 2024-07-15 | 14:39 | 2024-07-15 | 21:20 | 0.0027652 | 1.9313e-05 | 4 | 1002 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: FP767 No. Fuses: 2 Fuse Amp Size: 10 Amp TIME CLOSED: 15:50 Cause: TX TC4839 faulted internally (downstream) Weather (wind/rain): Rain Follow up required (select advisory)? No Isolation: TX TC4839 Fuses Location: Pole O13107 CAUSE: Internal Fault (Customer's heard a loud bang) Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Rain Follow up required (select advisory)? No Additional fault restoration comments: Steve Hooper Isolated faulty Transformer TC4839 Awaiting standby crew to arrive with a new Transformer. 15kVA transformer replaced | .
3754 |  | JE24024909 | LINTON | Western | LINTON | 2024-07-15 | 17:22 | 2024-07-15 | 19:21 | 0.078684 | 0.0018513 | 671 | 28520 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: CB 8 Protection flags (nil where none): EF CAUSE: line down - unknown why Location: Pole P03950 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): light rain, windy LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: | .
3755 |  | JE24024923 | CROWN | Western | CROWN | 2024-07-15 | 18:40 | 2024-07-15 | 19:43 | 0.00052311 | 8.2769e-06 | 3 | 190 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Blown jumper at ABS J86, suspect it is a secondary fault from feeder fault under JE24024874. Repair broken HV jumper at ABS J86 | .
3756 |  | JE24024943 | sub_PGA | Eastern | ROYDEN DOWNS RD | 2024-07-15 | 22:17 | 2024-07-16 | 0:27 | 0.062746 | 0.00074768 | 271 | 22743 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 5 Protection flags (nil where none): B Ø E/F CAUSE: No fault found Location: Unknown Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4, cursory patrolled Weather (wind/rain): Wind and rain LFI (Y/N + Comments): Installed none operated Follow up Required (select advisory)? No Additional fault restoration comments: Line patrolled and sectionalized, no fault cause could be found SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3757 |  | JE24024946 | PUTORINO | Western | PUTORINO | 2024-07-15 | 22:51 | 2024-07-16 | 0:56 | 0.016844 | 0.00028693 | 52 | 6105 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: REC 4246 Protection flags (nil where none): A & C phase OC CAUSE: Unknown/ 19/07/24 ABS 4087 burning up causing out of balance tripping Recloser 4246 on E/F Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): fine LFI (Y/N + Comments): N Follow up Required (select advisory)? This is the 4th time this week the recloser has tripped. Could we follow up during daylight for an operational patrol, possibly using a drone? Additional fault restoration comments: | .
3758 |  | JE24022327 | 31 MAHINUI STREET FEILDING FEILDING | Western | CROWN | 2024-07-13 | 8:16 | 2024-07-13 | 16:25 | 0.0013495 | 2.759e-06 | 1 | 489 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE TRANSFORMER T3/218 | .
3759 |  | JE24024682 | TAIRUA NORTH | Eastern | TAIRUA NORTH | 2024-07-13 | 4:03 | 2024-07-13 | 15:07 | 0.4134 | 0.0015974 | 579 | 149840 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 9848/2 Protection flags (nil where none): C Ø O/C CAUSE: Car vs Pole Location: Pole U0066 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? Yes Additional fault restoration comments: Car vs Pole at U0066 Multiple calls from Fire Comms and Police asking about the Traffic management on site, Field Switcher advised NOC Traffic management arrived on site around 08:30 Pole was replaced and HV Conductors repaired on site under AP 4682 Just to put on the record, field staff seem as if they are running on an empty tank and wellbeing should take first priority as I can hear they are tired and short of staff. Minor challenge where REC 9848/2 RTU was offline and NOC could not close via remote, Field Switcher was then given instruction to close REC 9848/2 and on arrival the control panel was blank. Decision was taken to restore supply via ABS 2664 which was closed in at 15:07. With Power being restored REC 9848/2 RTU came online and NOC restored the network to it's normal configuration. | .
3760 |  | JE24024695 | KONINI | Western | KONINI | 2024-07-13 | 11:27 | 2024-07-13 | 13:43 | 0.0026166 | 1.9313e-05 | 7 | 948 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Replace DTX T7/230 | .
3761 |  | JE24024718 | MATAROA A | Western | MATAROA A | 2024-07-13 | 11:53 | 2024-07-13 | 14:26 | 0.0084068 | 5.5179e-05 | 20 | 3047 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuse 2621 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 1425 Cause: Unknown Weather (wind/rain): fine Follow up required (select advisory)? | .
3762 |  | JE24024720 | PUTORINO | Western | PUTORINO | 2024-07-13 | 13:49 | 2024-07-13 | 16:00 | 0.015379 | 0.00014347 | 52 | 5574 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: REC 4246 Protection flags (nil where none): A / C phase EF CAUSE: bird strike Location: Pole 806976 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): fine LFI (Y/N + Comments): N/A Follow up Required (select advisory)? There is a lot of bird activity in the area Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3763 |  | JE24024743 | OKAIAWA | Western | OKAIAWA | 2024-07-13 | 22:33 | 2024-07-13 | 23:05 | 0.00099796 | 3.0349e-05 | 11 | 362 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolated at Fuses MA443 Replaced broken Insulator and Fuses carriers Cause age | .
3764 |  | JE24022248 | 81677 STATE HIGHWAY 2 PAHIATUA PAHIATUA | Western | RUAWHATA | 2024-07-12 | 9:46 | 2024-07-12 | 13:47 | 0.0033257 | 1.3795e-05 | 5 | 1205 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace LV conductor and cut trees at TX T7/460 | .
3765 |  | JE24022254 | 301 NEAVESVILLE ROAD PURIRI THAMES | Eastern | PURIRI | 2024-07-12 | 9:01 | 2024-07-12 | 11:10 | 0.0067788 | 5.242e-05 | 19 | 2457 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace 11kv & 400v Xarms on poles S12793, S12792, S12790. | .
3766 |  | JE24022272 | 3442 NGAHAPE ROAD NGAHAPE MASTERTON | Western | WERAITI | 2024-07-12 | 9:30 | 2024-07-12 | 13:46 | 0.013435 | 5.242e-05 | 19 | 4870 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Repair 11kv sags and remove incorrect joint at multiple sites past links 7113 | .
3767 |  | JE24022278 | 1935 PAREWANUI ROAD PAREWANUI BULLS | Western | PAREWANUI | 2024-07-12 | 9:01 | 2024-07-12 | 13:49 | 0.059676 | 0.00020692 | 75 | 21630 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 809369 including all hardware and transformer X2184. | .
3768 |  | JE24022283 | 2454 STATE HIGHWAY 4 WAIMARINO WANGANUI | Western | MAKIRIKIRI | 2024-07-12 | 9:31 | 2024-07-12 | 14:50 | 0.016365 | 0.00023727 | 57 | 5931 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace truck pole 783761 & digger pole 783787. | .
3769 |  | JE24022302 | 790 TAUMATA ROAD OMANAWA TAURANGA | Eastern | PYES PA | 2024-07-12 | 9:42 | 2024-07-12 | 15:06 | 0.065252 | 0.0002014 | 73 | 23651 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV overhead conductors between Poles 217036 & 384144 with 3W Ferret.Replace 11kV overhead conductors between 2W Ferret between poles 216961 & 216968. Remove temp ABS 022 | .
3770 |  | JE24022304 | 1729 SOUTH ROAD TATARAIMAKA NEW PLYMOUTH | Western | INLAND COAST | 2024-07-12 | 10:00 | 2024-07-12 | 11:18 | 0.00021548 | 2.759e-06 | 1 | 78 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace faulty set of lightning arrestors on ABS 6869 | .
3771 |  | JE24024214 | WILSON RD | Eastern | WILSON RD | 2024-07-12 | 9:31 | 2024-07-12 | 12:49 | 0.039878 | 0.0002014 | 73 | 14454 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Red Defect - CAE24030395 - Secure HV cable and Replace LV x-arm at pole Q12382 | .
3772 |  | JE24024581 | pole_772922 | Western | RANGIKURA | 2024-07-12 | 10:39 | 2024-07-12 | 11:11 | 0.008139 | 0.00025934 | 94 | 2950 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Repair jumper at Pole 772922 | .
3773 |  | JE24024588 | MAIN RD MOTONUI | Western | MAIN RD MOTONUI | 2024-07-12 | 10:26 | 2024-07-12 | 12:30 | 0.00034239 | 2.759e-06 | 1 | 124 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 6554 No. Fuses: 3 Fuse Amp Size: 15 TIME CLOSED: 12:30 Cause: Unknown, Suspect Digger contact at Quarry. Weather (wind/rain): Windy Follow up required (select advisory)? Voltage & Device ID: 11KV REC 6286-2 Protection flags (nil where none): A ph O/C & E/F Weather (wind/rain): windy Follow up required (select advisory): Y LFI Activation: Y Replace 3 x 15 amp fuses Fault crew was requested to patrol lines from Recloser 6286/2 to Recloser 12131/2 as line had been auto reclosing, Faultman found blown fuses at Fuses 6554 that feeds down to the quarry, suspect loader has hit lines, a Faultman will go out to the quarry in the week and advise then that they will need a CAC to work under the lines and the dangers of coming into contact with the lines. | .
3774 |  | JE24024618 | DAIRY FACTORY | Western | DAIRY FACTORY | 2024-07-12 | 12:58 | 2024-07-12 | 13:03 | 0.030518 | 0.0064643 | 2343 | 11061 | Unplanned | HUMAN ERROR - LOAD SHEDDING - NETWORK LOAD | During planned switching restoration under SIS 111 110 REC 11352 tripped on O/L | .
3775 |  | JE24024642 | MAKIRIKIRI | Western | MAKIRIKIRI | 2024-07-12 | 16:32 | 2024-07-12 | 19:07 | 0.0072536 | 4.6902e-05 | 17 | 2629 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Please Check JE24024643, JE24024652, JE24024656, JE24024663 and JE24024657 (To confirm which Tx this one is fed off too please) on closure Fuses Location: 1252 No. Fuses: 2 Fuse Amp Size: 20 Amp TIME CLOSED: 19:06 Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)? N | .
3776 |  | JE24024671 | TETLEY ROAD | Eastern | TETLEY ROAD | 2024-07-12 | 21:28 | 2024-07-14 | 13:18 | 0.023394 | 0.00015174 | 39 | 8479 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: TX TB2-024 Fuses CAUSE: Transformer TB2-024 DDO's failed. Temp generation (stage details when used): Yes, Generator connected at 12:40 on 13/07/2024 Generator removed at 13:01 on 14/07/2024 PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Calm Follow up required (select advisory)? Yes Additional fault restoration comments: Due to car vs pole emergency JE2402468 crew diverted Will be attended by AM crew 13/07/2024 Generator connected for ICP's at TB2-024 by Warren Ngata at 12:40 Short of staff to replace faulty transformer, will follow up on Monday 15/07/2024 14/07/2024 Field Switcher came to NOC to replace defective DDO's at Transformer TB2-024 Isolation point: Fuses SB2-037 & Earthed at Pole 201 578 Issued AP 4671-01 at 12:09 to carry out the repairs. At first the Transformer was suspected to be faulty, hence the Generator being connected. Upon repairs carried out today and testing on the Transformer it points to the fault being the DDO's that only failed and were then replaced. Fuses SB2-037 closed in at 12:31 Full Power restored to Transformer TB2-024 at 13:17 Job complete | .
3777 |  | JE24024678 | PORTSIDE | Eastern | PORTSIDE | 2024-07-12 | 23:30 | 2024-07-13 | 5:06 | 0.035363 | 0.00043316 | 157 | 12817 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV TRI CB10 Protection flags (nil where none): - CAUSE: Car vs Pole Location: Pole 213812 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): 2407009 Circuit patrolled and type: Yes Weather (wind/rain): Unknown LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Corner newton Street & hull road .Event P059330998 Car vs Pole - New Pole installed. Cable disconnected at Pole , left earthed at switchgear needs to be tested before being connected to service on new pole. See DNO 2407009 | .
3778 |  | JE24018128 | MARAETAI ROAD 33kV | Eastern | MARAETAI ROAD 33kV | 2024-07-11 | 8:36 | 2024-07-11 | 15:14 | 0.11074 | 0.00035039 | 126 | 40138 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACING POLE A12649 / KINMAR094 FOR FUTURE UG 33KV CABLE | .
3779 |  | JE24019352 | 286 WOODLAND ROAD TAHAWAI | Eastern | LINDERMANN RD | 2024-07-11 | 9:11 | 2024-07-11 | 14:47 | 0.041724 | 0.00012415 | 45 | 15123 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Reconductor 11kV between Poles 262461 & 204412. Isolation SB1-025. | .
3780 |  | JE24021951 | 5 CANTEEN STREET MARTON MARTON | Western | CROFTON | 2024-07-11 | 9:18 | 2024-07-11 | 12:16 | 0.026417 | 0.00014898 | 54 | 9575 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Swing 400V and 11kv lines over to new pole with fuses 16143 to supply new 200kva pad mount tx X274 | .
3781 |  | JE24021989 | 198 COLLEGE STREET WEST END PALMERSTON NORTH | Western | FERGUSON ST WEST | 2024-07-11 | 23:00 | 2024-07-12 | 2:31 | 0.29407 | 0.0013988 | 507 | 106588 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Perform magnefix maintenance at G46, G104 & G195 | .
3782 |  | JE24021995 | 14 BABERTON STREET TOKOROA TOKOROA | Eastern | DALMENY ST | 2024-07-11 | 8:30 | 2024-07-11 | 14:52 | 0.12829 | 0.00033659 | 122 | 46500 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove 2 pole structure A12364/5 and Transformer TC1607. Replace with new pole and Fuses 14902. Connect new 300KVA ground mount transformer to replace TC1607 (Id retained). | .
3783 |  | JE24022000 | 78 BOYDFIELD STREET WHANGANUI EAST WANGANUI | Western | WANGANUI EAST | 2024-07-11 | 9:00 | 2024-07-11 | 12:28 | 0.14991 | 0.00072285 | 262 | 54337 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace X arms on poles 768788 and 768643 | .
3784 |  | JE24022223 | 98 IKITARA ROAD BASTIA HILL WANGANUI | Western | IKITARA RD | 2024-07-11 | 9:30 | 2024-07-11 | 12:24 | 0.026804 | 0.0001545 | 56 | 9715 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install line break at p[ole 767200, replace tap-off X arms on pole 767200, remove line break | .
3785 |  | JE24022225 | 91 PAUL ROAD PUMPKIN HILL WHITIANGA | Eastern | COROGLEN | 2024-07-11 | 9:52 | 2024-07-11 | 15:13 | 0.0035418 | 1.1036e-05 | 4 | 1284 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install new 11kV pole, Paul Rd Rd Whitianga | .
3786 |  | JE24022234 | 138 WARAHOE ROAD MATATOKI THAMES | Eastern | KOPU | 2024-07-11 | 9:50 | 2024-07-11 | 11:49 | 0.0035948 | 3.0349e-05 | 11 | 1303 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To re-secure loose DDO fuses to crossarm at 11kV Pole S12545 (TC5758). | .
3787 |  | JE24022238 | 76 WINGS LINE MARTON MARTON | Western | NGATAWA | 2024-07-11 | 9:20 | 2024-07-11 | 15:16 | 0.0049015 | 1.3795e-05 | 5 | 1777 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace low Voltage transformer X arms on pole 801478, TX X275 | .
3788 |  | JE24022243 | 1268 ROBERTS LINE BUNNYTHORPE PALMERSTON NORTH | Western | TE ARAKURA | 2024-07-11 | 9:17 | 2024-07-11 | 14:24 | 0.077047 | 0.00025107 | 91 | 27926 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Pole upgrades from and including poles P39162 - P39295. Reconductor LV from P39162 - P39172. | .
3789 |  | JE24022244 | 68 FAIRFIELD ROAD HAWERA HAWERA | Western | GLOVER RD EAST | 2024-07-11 | 9:16 | 2024-07-11 | 12:26 | 0.035705 | 0.00018761 | 68 | 12942 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace TX 5450E and fuses 8532 | .
3790 |  | JE24022245 | 43 STANLEY AVENUE TE AROHA TE AROHA | Eastern | STANLEY AVE | 2024-07-11 | 8:30 | 2024-07-11 | 11:10 | 0.021165 | 0.00013243 | 48 | 7671 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9279-1/2/3 | .
3791 |  | JE24022339 | 416 MAIN ROAD TAIRUA TAIRUA | Eastern | COROGLEN | 2024-07-11 | 9:15 | 2024-07-11 | 11:47 | 0.020911 | 0.00013795 | 50 | 7579 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV poles U12466 & 383445/383446 Main Rd Tairua | .
3792 |  | JE24023569 | 320 BENNETT ROAD TE MATA THAMES | Eastern | MANAIA COROMANDEL | 2024-07-11 | 10:19 | 2024-07-11 | 14:55 | 0.00076244 | 2.759e-06 | 1 | 276 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Red Defect. Hanger arm TC5891 urgently needs replacing due to rot. | .
3793 |  | JE24024400 | CLOTON RD INDUSTRIAL | Western | CLOTON RD INDUSTRIAL | 2024-07-11 | 9:23 | 2024-07-11 | 9:45 | 0.00012572 | 5.5179e-06 | 2 | 46 | Unplanned | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | Voltage & Device ID: 11kV REC 6942/2 Protection flags (nil where none): A, B ph O/C & E/F Weather (wind/rain): calm Follow up required (select advisory): n Unknown reason for tripping, Suspect tripping when cheal was shutting down machine 33kV CB 2782 also tripped | .
3794 |  | JE24024429 | TOTMANS RD | Eastern | TOTMANS RD | 2024-07-11 | 10:34 | 2024-07-11 | 17:43 | 0.091158 | 0.0011891 | 431 | 33041 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11KV REC 13260/2 Protection flags (nil where none): n CAUSE: Car vs pole Location: E1275 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: n Weather (wind/rain): calm LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: ETA 30 min. MDP Control advised pole and lines on car, Controller opened Recloser 13260/2 for safety. Faultman found car vs Pole E1275, line was isolated at ABS's 1154 & 2625. | .
3795 |  | JE24024467 | 14 SECOND AVENUE TAURANGA TAURANGA | Eastern | 5TH AVE | 2024-07-11 | 13:35 | 2024-07-11 | 14:11 | 0.029557 | 0.00082217 | 298 | 10713 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2 faults, 1 Overload - Circulating current between Waihi Road- Hamilton caused overload on CB3 2 CB3 unable to close - Mechanical issue on HST CB3 Sticking mech CRC | .
3796 |  | JE24024486 | HEADS RD | Western | HEADS RD | 2024-07-11 | 18:43 | 2024-07-11 | 19:00 | 0.013741 | 0.00081389 | 295 | 4981 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | DDO for Transformer 2207W found to be fault Isolated at ABS's 1356, 1351, & 1491. Replaced 1X DDO will defect the rest | .
3797 |  | JE24024518 | KAIHERE | Eastern | KAIHERE | 2024-07-11 | 19:21 | 2024-07-11 | 21:21 | 0.0013253 | 1.1036e-05 | 4 | 480 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 11KV Fuses IP621 No. Fuses: 2 Fuse Amp Size: 25 TIME CLOSED: 21:21 Cause: unknown Weather (wind/rain): Follow up required (select advisory)? IP621 are fuses not solid links as drawn on SCADA there has been some over sight as IP621 were drawn on scada before sectionaliser 14565 was installed last year | .
3798 |  | JE24025123 | OLD CAMBRIDGE RD | Eastern | OLD CAMBRIDGE RD | 2024-07-11 | 9:30 | 2024-07-11 | 11:31 | 0.07578 | 0.00062628 | 227 | 27467 | Unplanned | HUMAN ERROR - POTENTIAL SWITCHING ERROR | Unplanned outage associated with NAPA 111031 11kv backfeed missed in switching steps, ICP's were not advertised, Isolation at ABS 997 | .
3799 |  | JE24020958 | 153 CAPTAIN COOK ROAD NETHERTON PAEROA | Eastern | HAURAKI RD | 2024-07-10 | 9:31 | 2024-07-10 | 11:31 | 0.0013261 | 1.1036e-05 | 4 | 481 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Repair Stay Wire at TC3993 | .
3800 |  | JE24021498 | 449 WILTSDOWN ROAD WILTSDOWN PUTARURU | Eastern | PAPANUI ST | 2024-07-10 | 9:16 | 2024-07-10 | 13:04 | 0.0075447 | 3.3108e-05 | 12 | 2735 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | AT POLE B12384 REPLACE ALL CROSSARMS FITTED WITH NEW HARDWARE | .
3801 |  | JE24021832 | 1099 OLD TAUPO ROAD LICHFIELD PUTARURU | Eastern | WAOTU | 2024-07-10 | 9:45 | 2024-07-10 | 13:59 | 0.00069986 | 2.759e-06 | 1 | 254 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Assess oil leak at TC5462. Remove LV frame for full investigation. | .
3802 |  | JE24021833 | 148 COOK STREET WEST END PALMERSTON NORTH | Western | WEST END | 2024-07-10 | 23:00 | 2024-07-11 | 3:16 | 0.23895 | 0.00093253 | 338 | 86607 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Perform magnefix maintenance at G173, G83 & G134 | .
3803 |  | JE24021933 | 97 MILL ROAD PAEROA PAEROA | Eastern | TIROHIA-KARANGAHAKE | 2024-07-10 | 9:15 | 2024-07-10 | 14:50 | 0.012931 | 3.8625e-05 | 14 | 4687 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles N1250,N1251,876690,N1253,N1254,N1262 and 876687 | .
3804 |  | JE24021936 | 14 COBDEN ROAD CARRINGTON CARTERTON | Western | BELVEDERE | 2024-07-10 | 8:46 | 2024-07-10 | 14:36 | 0.10446 | 0.00029797 | 108 | 37863 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace OYT Recloser C416 | .
3805 |  | JE24021939 | 662 RANGITATAU EAST ROAD KAI IWI WANGANUI | Western | WATERWORKS RD | 2024-07-10 | 9:22 | 2024-07-10 | 10:45 | 0.025659 | 0.000309 | 112 | 9300 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Defected 11KV X-Arm on pole 781977 | .
3806 |  | JE24021978 | 32 RANGINUI ROAD WELCOME BAY TAURANGA | Eastern | WELCOME BAY | 2024-07-10 | 8:34 | 2024-07-10 | 16:08 | 0.09268 | 0.00020416 | 74 | 33592 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install and commission new 11kv recloser # 14877 with source side links and bypass ABS on pole 215410 Isolation point @ SD4-076,issuer earths @ pole 215410( 215490 side) | .
3807 |  | JE24021985 | 67 ARAWA CRESCENT TOKOROA TOKOROA | Eastern | LOMOND AVE | 2024-07-10 | 9:15 | 2024-07-10 | 13:05 | 0.054008 | 0.00023451 | 85 | 19576 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - IC1450-FC2743-IC1463-FC2720 | .
3808 |  | JE24023468 | 91 OLD WEST ROAD LINTON | Western | LINTON | 2024-07-10 | 8:51 | 2024-07-10 | 11:38 | 0.021655 | 0.00012967 | 47 | 7849 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11KV Xarm install Temp links Temp087 at Pole P00510. | .
3809 |  | JE24024245 | PUTORINO | Western | PUTORINO | 2024-07-10 | 0:55 | 2024-07-10 | 3:42 | 0.017837 | 0.00014347 | 52 | 6465 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 4246/2 Protection flags (nil where none): A & C ph O/C & E/F CAUSE: Magpies Location: Tfr 4350W Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: Operational Weather (wind/rain): calm LFI (Y/N + Comments): n Follow up Required (select advisory)? 2R - To remain open to complete line patrol when daylight breaks Additional fault restoration comments: Faultman found dead Magpies at transformer 4350W, on transformer and on the ground underneath., Magpie removed with line sticks. | .
3810 |  | JE24024247 | OHAKEA | Western | OHAKEA | 2024-07-10 | 2:27 | 2024-07-10 | 10:26 | 0.11076 | 0.0012608 | 457 | 40147 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV Recloser 10748/2 Protection flags (nil where none): B Ph, E/F CAUSE: Car V Pole Location: Pole P20283 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Isolated at ABS's 10620/1 & L77/1 and Links 10620/6 & L77/6 Back feed installed Pole Replaced SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3811 |  | JE24024253 | WAIONE | Western | WAIONE | 2024-07-10 | 6:36 | 2024-07-10 | 8:24 | 0.0029945 | 2.759e-05 | 10 | 1085 | Unplanned | WILDLIFE - BIRD | Fuses Location: V44 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 08:24 Cause: Bird strike Weather (wind/rain): Fine Follow up required (select advisory)? N | .
3812 |  | JE24024255 | KETEMARAE RD | Western | KETEMARAE RD | 2024-07-10 | 7:03 | 2024-07-10 | 8:37 | 0.0025805 | 2.759e-05 | 10 | 935 | Unplanned | WILDLIFE - BIRD | Fuses Location: WH 831 No. Fuses: 3 + 1 x holder Fuse Amp Size: 15 TIME CLOSED: 08:36 Cause: Bird Strike - Swan Weather (wind/rain): calm Follow up required (select advisory)?n | .
3813 |  | JE24024259 | LANGDALE | Western | LANGDALE | 2024-07-10 | 7:35 | 2024-07-10 | 9:55 | 0.00038804 | 2.759e-06 | 1 | 141 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: 7867 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 09:55 Cause: UNKNOWN - PATROLLED Weather (wind/rain): FINE Follow up required (select advisory)? N | .
3814 |  | JE24024300 | recloser_11169:2 | Western | KUMENGA | 2024-07-10 | 10:57 | 2024-07-10 | 15:16 | 0.063056 | 0.00024279 | 88 | 22855 | Unplanned | THIRD PARTY INTERFERENCE - OVERHEAD CONTACT | REGULATORY INFORMATION Voltage & Device ID: Recloser 11169 Protection flags (nil where none): B, Ph EF CAUSE: Digger through lines Location: Pole 812985 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): None Follow up Required (select advisory)? No Additional fault restoration comments: Isolated at ABS 11169/1 & Links 11169/6 FM to supply NDR Lines repaired SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3815 |  | JE24019350 | 225 WOODLAND ROAD TAHAWAI | Eastern | LINDERMANN RD | 2024-07-09 | 9:03 | 2024-07-09 | 16:10 | 0.052972 | 0.00012415 | 45 | 19200 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Reconductor 11kV between Poles 204393 & 204399. Isolation SB1-025. Time over run cause: access issues | .
3816 |  | JE24021664 | 359 MAIN ROAD TAIRUA TAIRUA | Eastern | TAIRUA NORTH | 2024-07-09 | 9:30 | 2024-07-09 | 12:08 | 0.062244 | 0.00039453 | 143 | 22561 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV poles 264013, 264014 & 264016 Main Rd Tairua | .
3817 |  | JE24021666 | 709 INGAHAPE ROAD OHANGAI HAWERA | Western | WHAKAMARA | 2024-07-09 | 8:32 | 2024-07-10 | 16:00 | 0.046609 | 9.9323e-05 | 18 | 16894 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | asplundh to clear vegatation from lines between poles 729702 & 729719 | .
3818 |  | JE24021676 | 62 KOWHAI STREET MANGAMAHU WANGANUI | Western | FORDELL | 2024-07-09 | 9:18 | 2024-07-09 | 12:42 | 0.0084528 | 4.1384e-05 | 15 | 3064 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace X arms on pole 783897 | .
3819 |  | JE24021680 | 3 TAWA STREET TOKOROA TOKORA | Eastern | RATA ST BAIRD ROAD | 2024-07-09 | 9:45 | 2024-07-09 | 13:35 | 0.020924 | 9.1046e-05 | 33 | 7584 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - FC5028 | .
3820 |  | JE24021693 | 60 ESDAILE ROAD WHAKAMARAMA | Eastern | APATA | 2024-07-09 | 9:16 | 2024-07-09 | 11:24 | 0.032808 | 0.00025658 | 93 | 11892 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace HV arm on Pole 209510 and 209293 | .
3821 |  | JE24021701 | 19 DOVER ROAD OKATO NEW PLYMOUTH | Western | INLAND COAST | 2024-07-09 | 9:30 | 2024-07-09 | 13:00 | 0.015626 | 7.4492e-05 | 27 | 5664 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install new Entec / Links / TX structure on existing pole 453956. Entec ID 12710 | .
3822 |  | JE24021704 | 28 FRONT MIRANDA ROAD WAITAKARURU THAMES | Eastern | MANGATARATA | 2024-07-09 | 9:45 | 2024-07-09 | 12:35 | 0.049524 | 0.00029245 | 106 | 17950 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To straighten pole 269577 and reinstate ground stay. | .
3823 |  | JE24021710 | 1268 ROBERTS LINE BUNNYTHORPE PALMERSTON NORTH | Western | TE ARAKURA | 2024-07-09 | 9:31 | 2024-07-09 | 13:55 | 0.066236 | 0.00025107 | 91 | 24008 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Pole upgrades from and including poles P39161 to P39295. Reconductor LV from P39161 - P39156. Replace TX T2/244 with a 50kVA TX (number to remain) | .
3824 |  | JE24021800 | 120 GLOVER ROAD HAWERA HAWERA | Western | ARGYLE ST | 2024-07-09 | 9:00 | 2024-07-09 | 10:37 | 0.024462 | 0.00025382 | 92 | 8866 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | remove hv & lv line break at pole 441163 and remove lv backfeed at pole 359616 | .
3825 |  | JE24021812 | 684 PIONEER HIGHWAY HIGHBURY PALMERSTON NORTH | Western | PASCAL ST 9 | 2024-07-09 | 23:25 | 2024-07-10 | 4:34 | 0.22762 | 0.00073664 | 267 | 82503 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Perform magnefix maintenance at G151, G206, G153 & G183 | .
3826 |  | JE24021841 | 14 SECOND AVENUE TAURANGA TAURANGA | Eastern | 5TH AVE | 2024-07-09 | 8:31 | 2024-07-09 | 15:20 | 0.010162 | 2.4831e-05 | 9 | 3683 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Switchgear 9114 with two fully Automated CFCC Switchgear 14898 and CCCC Switchgear 14895. Power restored to customers 09/07/24 15:20 via (additional) LV back feeds , restoration to transformer performed later in the evening. | .
3827 |  | JE24023302 | 170 YORK ROAD MIDHIRST STRATFORD | Western | CLOTON RD NORTH | 2024-07-09 | 10:17 | 2024-07-09 | 11:19 | 0.0086934 | 0.00014071 | 51 | 3151 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Resag conductors at pole 456308 | .
3828 |  | JE24023317 | 518 DENBIGH ROAD MIDHIRST STRATFORD | Western | CLOTON RD NORTH | 2024-07-09 | 14:01 | 2024-07-09 | 14:41 | 0.0049266 | 0.00012139 | 44 | 1786 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Repair or replace jumper at pole 459245, check polymer and replace as required.Â | .
3829 |  | JE24024158 | recloser_11169:2 | Western | KUMENGA | 2024-07-09 | 10:36 | 2024-07-09 | 12:58 | 0.026312 | 0.00024279 | 88 | 9537 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kv Rec11169 Protection flags (nil where none): A Phase E/F CAUSE: Unknown Location: Unknown Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory patrol Weather (wind/rain): Fine LFI (Y/N + Comments): No Follow up Required (select advisory)? Additional fault restoration comments: | .
3830 |  | JE24024221 | PUTORINO | Western | PUTORINO | 2024-07-09 | 17:08 | 2024-07-09 | 19:24 | 0.018307 | 0.00014347 | 52 | 6636 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV, Rec 4246/2 Protection flags (nil where none): E/F, O/C A-C phase CAUSE: Unk Location: Unk Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Yes / Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3831 |  | JE24021478 | 152 Church St & 52 West St PLM & 96 Lyndhurst St PLM | Western | FERGUSON ST WEST | 2024-07-08 | 23:01 | 2024-07-09 | 5:24 | 0.16209 | 0.00086907 | 315 | 58750 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Perform 11kV Magnefix maintenance at G11 & G92 & G56 | .
3832 |  | JE24021485 | 103 GLENCAIRN ROAD TURAKINA MARTON | Western | TURAKINA | 2024-07-08 | 8:45 | 2024-07-08 | 10:05 | 0.0026541 | 3.3108e-05 | 12 | 962 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Isolation for vegetation cutting at pole 802448 Job was not completed as tree contractor did not show up, they forgot to book the tree work in, Scanpower will reapply for new outage | .
3833 |  | JE24021495 | 540 OHAUTI RD TAURANGA | Eastern | OHAUITI RD | 2024-07-08 | 9:05 | 2024-07-08 | 11:08 | 0.027691 | 0.00022623 | 82 | 10037 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace lightening arrestors on Pole 212477 | .
3834 |  | JE24021505 | 6 ARCUS ROAD DALEFIELD CARTERTON | Western | BELVEDERE | 2024-07-08 | 9:15 | 2024-07-08 | 11:25 | 0.0032193 | 2.4831e-05 | 9 | 1167 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | repair, replace defective hardware T3118 | .
3835 |  | JE24021647 | 2759 WAIHI WHANGAMATA ROAD WHANGAMATA WHANGAMATA | Eastern | HETHERINGTON RD | 2024-07-08 | 10:00 | 2024-07-08 | 10:07 | 7.7435e-05 | 1.1036e-05 | 4 | 28 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | On Transformer TP3518 change Tap from 3 to 2 and check voltages, at present too high | .
3836 |  | JE24021652 | 550 TRIG ROAD NORTH WAIHI WAIHI | Eastern | WAIHI NORTH | 2024-07-08 | 9:30 | 2024-07-08 | 13:32 | 0.0066932 | 2.759e-05 | 10 | 2426 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace LV Transformer Xarm at pole P13536 | .
3837 |  | JE24021678 | 22 MANGATI ROAD BELL BLOCK NEW PLYMOUTH | Western | KATERE 12 | 2024-07-08 | 9:00 | 2024-07-09 | 12:10 | 0.06589 | 0.001534 | 278 | 23882 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | ELE020758 TAR GM Switchgear - Magnefix. Systematic/staged 4 day replacement of Magnefix 322 with new Safelink unit. Due to SAIDI requirements, DAY 1 & 2 shuts will be done on this NAPA. Then min 5 day gap before Day 3 & 4 shuts. Day 3 & 4 shuts will follow the week after on NAPA 110742. | .
3838 |  | JE24023907 | 833 TURAKINA VALLEY RD, TURAKINA, WANGANUI, 4581 | Western | TUTAENUI | 2024-07-08 | 13:30 | 2024-07-08 | 14:04 | 0.0079157 | 0.00023175 | 84 | 2869 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Jeremy Hill to fix this within the next two days under Urgent NAPA. Application to be submitted today. Cause: King bolt had come off What was replaced? Bolt on king bolt Where was it replaced (pole/TX/pillar box)? 793487 Is 2R required? Y 2R Y - What is the timeframe for repairs? 09/07/24 Additional Info: Line was isolated at Links 4237/6 & ABS 4237/1 to make repair. | .
3839 |  | JE24024043 | RATAPIKO | Western | RATAPIKO | 2024-07-08 | 12:16 | 2024-07-08 | 14:09 | 0.017718 | 0.00015726 | 57 | 6422 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 5400 No. Fuses: 2 Fuse Amp Size: 30 TIME CLOSED: 14:09 Cause: Suspect bird strike Weather (wind/rain): calm Follow up required (select advisory)?n | .
3840 |  | JE24024064 | PIHAMA | Western | PIHAMA | 2024-07-08 | 13:49 | 2024-07-08 | 14:35 | 0.00012613 | 2.759e-06 | 1 | 46 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Faultman found broken jumpers at Fuses 6579 while driving past, line was isolated at Fuses 6579 to repair the jumpers. | .
3841 |  | JE24024109 | HORAHORA | Eastern | HORAHORA | 2024-07-08 | 23:43 | 2024-07-09 | 4:59 | 0.013991 | 4.4143e-05 | 16 | 5071 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: Fuses FP660 Protection flags (nil where none): Nil CAUSE: Line down Location: Pole M0201 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4, cursory patrolled. Weather (wind/rain): calm LFI (Y/N + Comments): no LFI's Follow up Required (select advisory)? No Additional fault restoration comments: Bimetal joint failure on outside phase this caused the line to fall down. This caused other damage due to shock loading. 1 x HV pin arm complete assembly 1 x HV termination cross arm complete assembly 3 x Bimetal joints SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3842 |  | JE24021466 | 14 KENSINGTON ROAD MARTON MARTON | Western | CROFTON | 2024-07-07 | 9:00 | 2024-07-07 | 10:33 | 0.053993 | 0.00066767 | 242 | 19570 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install 11kv Fuses 16156 at pole 464039 to supply spur line with X274 | .
3843 |  | JE24021549 | 24 KEREPEHI TOWN ROAD KEREPEHI PAEROA | Eastern | COUNTY WATER | 2024-07-07 | 8:32 | 2024-07-07 | 13:24 | 0.0016124 | 5.5179e-06 | 2 | 584 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To carry out oil repair works on GMT TC5340 | .
3844 |  | JE24021640 | 2 VICKERS ROAD WAIWHAKAIHO NEW PLYMOUTH | Western | KATERE 11 | 2024-07-07 | 6:18 | 2024-07-07 | 10:26 | 0.0061572 | 2.4831e-05 | 9 | 2232 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | DNO 2403009. HV cable failed last testing while connected to old ABS 447. AP-01: Replace ABS 447 and do 10 Yearly 11kV metering unit 1086 calibration. TP-02: Re-test HV between ABS 447 and SW 563/3. SW-03: If HV cable fails testing, leave isolated and restore supply to customers. If cable testing OK, restore supply to phase at sw 563/3 and restore network. | .
3845 |  | JE24023898 | MOUNT BRUCE | Western | MOUNT BRUCE | 2024-07-07 | 2:28 | 2024-07-07 | 9:36 | 0.085645 | 0.0023617 | 743 | 31042 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB C816 Protection flags (nil where none): A B C Ø O/C & E/F CAUSE: Car vs Pole Location: Pole 419467 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Calm LFI (Y/N + Comments): Yes, did not operate. Follow up Required (select advisory)? No Additional fault restoration comments: 1st Fault Car vs Pole at Pole 419 467 - Repairs were made and a new Pole was installed. No back feed option was available. 2nd Fault Field Switcher found a dead-end failed at Links TEMP145 and the conductor was hanging on just by the jumper including lines were low. Repairs were completed under a second AP 3898-02 with multiple Isolation points and back feeding two sections. Full Power restored at 09:35 | .
3846 |  | JE24023905 | TAINUI | Eastern | TAINUI | 2024-07-07 | 8:03 | 2024-07-07 | 10:36 | 0.00084055 | 5.5179e-06 | 2 | 305 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses SE7-030 No. Fuses: 2 Fuse Amp Size: 6 Amp TIME CLOSED: 10:35 Cause: Suspect bird strike Weather (wind/rain): Calm Follow up required (select advisory)? No | .
3847 |  | JE24023919 | COROGLEN | Eastern | COROGLEN | 2024-07-07 | 9:43 | 2024-07-07 | 11:55 | 0.01242 | 9.3805e-05 | 34 | 4502 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 13588/2 Protection flags (nil where none): B Ø O/C & E/F CAUSE: HV Line down across the road - Deterioration. Location: Pole W1257 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Calm LFI (Y/N + Comments): Yes one in the field. (No SCADA) Follow up Required (select advisory)? No Additional fault restoration comments: Feeder fault and crew dispatched to site. Found HV Lines down across the road at Pole W1257 Repairs carried out under AP 3919-01 Full Power restored at 11:55 | .
3848 |  | JE24023922 | WAITARA RD | Western | WAITARA RD | 2024-07-07 | 8:53 | 2024-07-07 | 10:22 | 0.0053858 | 6.0697e-05 | 22 | 1952 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 8267 No. Fuses: 2 Fuse Amp Size: 15 Amp TIME CLOSED: 10:21 hrs Cause: Suspect Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? No | .
3849 |  | JE24023952 | KAIPI RD | Western | KAIPI RD | 2024-07-07 | 15:43 | 2024-07-11 | 11:01 | 0.049408 | 1.1036e-05 | 4 | 17908 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | HV cable fault between ABS 527 & Sw/Gear 405/3. Crew will return first light to locate fault. Generator in service on Tfr 405-P at 16:16 - 08/07/24 Cable fault was repaired between Fuses 8151 & Sw/Gear 405/3 | .
3850 |  | JE24021624 | 95 NGATI MARU HIGHWAY KOPU THAMES | Eastern | KOPU | 2024-07-06 | 9:01 | 2024-07-06 | 15:01 | 0.016493 | 4.6902e-05 | 17 | 5978 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole S0536 | .
3851 |  | JE24023836 | CENTRAL PARADE | Eastern | CENTRAL PARADE | 2024-07-06 | 4:01 | 2024-07-06 | 5:48 | 0.14381 | 0.0024224 | 878 | 52126 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 13393 Protection flags (nil where none): A, O/C & E/F CAUSE: Unknown Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Curse Weather (wind/rain): Light Winds LFI (Y/N + Comments): Yes 13608/1 Follow up Required (select advisory)? Additional fault restoration comments: Found 1 x Failed Lightning arrestor, Will replace with 2R | .
3852 |  | JE24023842 | WAITOTARA | Western | WAITOTARA | 2024-07-06 | 7:42 | 2024-07-06 | 9:31 | 0.0039089 | 3.5867e-05 | 13 | 1417 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 684 No. Fuses: 2 Fuse Amp Size: 10 Amp TIME CLOSED: 09:31hrs Cause: Unk, Suspect Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? | .
3853 |  | JE24023847 | MARTON | Western | MARTON | 2024-07-06 | 7:05 | 2024-07-06 | 8:31 | 0.015254 | 0.00017657 | 64 | 5529 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 2550 No. Fuses: 2 Fuse Amp Size: 20 Amp TIME CLOSED: 08:31 hrs Cause: Unk, suspect bird Weather (wind/rain): Calm Follow up required (select advisory)? | .
3854 |  | JE24023850 | JE24023841 | Western | HUNTERVILLE 22KV | 2024-07-06 | 9:11 | 2024-07-06 | 10:40 | 0.012245 | 0.00013795 | 50 | 4438 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: HV Line Down Location: Pole 804809-804810 Isolation: ABS 1049 Back Feeds: N/A LFI Indication: N/A What was replaced? Conductor, 2x cond joints, and 1x binder Weather: Calm Additional Info: | .
3855 |  | JE24023852 | TOTARA ST | Western | TOTARA ST | 2024-07-06 | 8:56 | 2024-07-06 | 11:08 | 0.0021943 | 1.6554e-05 | 6 | 795 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: Fuses 7750 No. Fuses: 2x Fuse Amp Size: 8A TIME CLOSED: 11:08 Cause: Found twisted lines over a pond - suspect bird strike Weather (wind/rain): Calm Follow up required (select advisory)? No | .
3856 |  | JE24023880 | SHAW AVE | Eastern | SHAW AVE | 2024-07-06 | 16:27 | 2024-07-07 | 15:00 | 0.14168 | 0.0010732 | 361 | 51354 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV POA CB4 Protection flags (nil where none): A B C Ø O/C CAUSE: Unknown (First test permit indicated HV Cable fault) Location: Unknown - Suspected between ABS IP 751 towards Sw/Gear 13495/1 Temp generation (state details when used): Yes, LV Generator connected to Transformer TP3436 at 02:12 on 07/07/2024 LV Generator removed from TP3436 at 14:51 on 07/07/2024 PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Calm LFI (Y/N + Comments): Yes, LFI's at Sw/Gear 13535/1 were flashing & LFI's past ABS IC2678 operated. Follow up Required (select advisory)? No Additional fault restoration comments: Feeder fault which was then Line Patrolled and sectionalized between Sw/Gear & HV Cables. First Test Permit indicated that we had a HV Cable fault. Later on during the course of the day a second Test Permit was taken and the results were all good, well above the standard values. HV Cable was then re-livened from ABS IP751 at 14:41 Fuse/Sw 13495/4 was closed in at 14:47 towards TX TC4410 (Race course) Access Permit was taken to remove the Generator and close the LV Cable break. Fuse/Sw 13495/2 was closed in at 15:00 After all the testing and fault-finding involved, no actual permanent fault was found. Full Power restore | .
3857 |  | JE24018283 | 1022 TAUMATA ROAD OMANAWA TAURANGA | Eastern | PYES PA | 2024-07-05 | 9:13 | 2024-07-05 | 14:13 | 0.033994 | 0.00011312 | 41 | 12321 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV overhead conductors between Poles 216961 & 217089 with 3W ferret. | .
3858 |  | JE24020608 | 469 RAETIHI OHAKUNE ROAD RAETIHI OHAKUNE | Western | RAETIHI | 2024-07-05 | 9:11 | 2024-07-05 | 12:53 | 0.0067338 | 3.0349e-05 | 11 | 2441 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 776871 using digger. | .
3859 |  | JE24021313 | 85 MOSSTON ROAD CASTLECLIFF WANGANUI | Western | HEADS RD | 2024-07-05 | 9:16 | 2024-07-05 | 14:30 | 0.0026053 | 8.2769e-06 | 3 | 944 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Transformer X484 | .
3860 |  | JE24021350 | 38 FRENCH STREET MARTON MARTON | Western | NGATAWA | 2024-07-05 | 10:48 | 2024-07-05 | 14:28 | 0.026169 | 0.00011864 | 43 | 9485 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Disconnect old transformer X762, connect new transformer and remove old pole 801436 | .
3861 |  | JE24021356 | 20 BRADSHAW ROAD KOMATA PAEROA | Eastern | BENNETT ST | 2024-07-05 | 9:16 | 2024-07-05 | 10:53 | 0.0039943 | 4.1384e-05 | 15 | 1448 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REMOVE 11KV RECLOSURE 9901/2 (FOR SERVICING) THEN INSTALL BACK INTO SERVICE. | .
3862 |  | JE24021367 | 4711 STATE HIGHWAY 4 KAKATAHI WANGANUI | Western | PARAPARA | 2024-07-05 | 10:00 | 2024-07-05 | 12:59 | 0.0057803 | 0.00012415 | 29 | 2095 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | ReSag conductor between pole 783658 - 783659 | .
3863 |  | JE24021383 | 1644 ANNEDALE ROAD TINUI TINUI | Western | ANNEDALE | 2024-07-05 | 9:00 | 2024-07-05 | 14:03 | 0.03585 | 0.00011864 | 43 | 12994 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Isolation for vegetation cutting between poles 838475 and 838476 | .
3864 |  | JE24021398 | 275 HILDRETH ROAD ARAPUNI PUTARURU | Eastern | HORAHORA | 2024-07-05 | 9:15 | 2024-07-05 | 11:40 | 0.0099794 | 6.8974e-05 | 25 | 3617 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | EXTENSION OF OH HV TO NEW 50KVA TX | .
3865 |  | JE24021491 | 372 GOLDEN VALLEY ROAD WAIHI WAIHI | Eastern | WAIHI NORTH | 2024-07-05 | 9:17 | 2024-07-05 | 13:38 | 0.058868 | 0.00022623 | 82 | 21337 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv Xarms at Pole P1727,P13678,876605,P1648 | .
3866 |  | JE24023690 | PONATAHI | Western | PONATAHI | 2024-07-05 | 7:07 | 2024-07-05 | 11:11 | 0.00067245 | 2.759e-06 | 1 | 244 | Unplanned | WILDLIFE - POSSUM | Fuses Location: Fuses 7401 No. Fuses: 2 Fuse Amp Size: 65A TIME CLOSED: 1110 Cause: Possum Weather (wind/rain): Fine Follow up required (select advisory)? | .
3867 |  | JE24023691 | WAIOURU 33KV | Western | WAIOURU 33KV | 2024-07-05 | 7:11 | 2024-07-05 | 8:06 | 0.061145 | 0.0016719 | 606 | 22162 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 33 KV CB 3094 & 11kv CB 1 Protection flags (nil where none): 33kV TFR T1 H/V E/F CB 3094 C Phase O/C CAUSE: Unknown Location: Sub Temp generation (state details when used): PERFORMANCE DETAILCB DNO (number or state No): Circuit patrolled and type: Checked all of the sub and looked at all relays could not see anything Weather (wind/rain): Fine & Frosty LFI (Y/N + Comments): Nil Follow up Required (select advisory)? protection team Additional fault restoration comments: LOS to Waiouru Sub | .
3868 |  | JE24023749 | MOWBRAY RD | Eastern | MOWBRAY RD | 2024-07-05 | 11:33 | 2024-07-05 | 13:06 | 0.00025493 | 2.759e-06 | 1 | 92 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: FC929 No. Fuses: 2 Fuse Amp Size: 6amp TIME CLOSED: 13:05 Cause: Unknown Weather (wind/rain): Windy Follow up required (select advisory)? | .
3869 |  | JE24023751 | HEADS RD | Western | HEADS RD | 2024-07-05 | 11:49 | 2024-07-05 | 14:31 | 0.14433 | 0.0041633 | 1509 | 52314 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: CB 5 Protection flags (nil where none): 3 phase OC CAUSE: Car V Pole Location: Pole 765313 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: N/A Weather (wind/rain): fine LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Replace cross arm only | .
3870 |  | JE24023769 | TOTMANS RD | Eastern | TOTMANS RD | 2024-07-05 | 14:03 | 2024-07-05 | 15:10 | 0.0037448 | 5.5179e-05 | 20 | 1357 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Repair Jumper at Transformer TC 4525 Isolated at ABS 1154 & ABS 2625 Backfeed in at Sec 9790 | .
3871 |  | JE24023812 | MANGATARATA | Eastern | MANGATARATA | 2024-07-05 | 17:41 | 2024-07-05 | 20:34 | 0.0067015 | 3.8625e-05 | 14 | 2429 | Unplanned | THIRD PARTY INTERFERENCE - TREES | REGULATORY INFORMATION Voltage & Device ID: 11kV Fuses FP1166 Protection flags (nil when none): A/R upstream at REC RC24 (A Ø O/C) CAUSE: Customer cut down a tree which fell on the HV Lines. Location: Pole O13938 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Calm Follow up required (select advisory)? No Additional fault restoration comments: Member of public was cutting down a tree when it fell over and hit the HV Lines, which caused two HV Lines to break and hit the ground near Pole O13938. Field Switcher carried out emergency switching on arrival and Isolated the Fuses FP1166 Repairs carried out under AP 3810-01 Safety Manager ID 1395898 | .
3872 |  | JE24023827 | MANGOREWA | Eastern | MANGOREWA | 2024-07-05 | 18:51 | 2024-07-05 | 20:46 | 0.0003162 | 2.759e-06 | 1 | 115 | Unplanned | WILDLIFE - BIRD | Fuses Location: SF6-024 No. Fuses: 2 Fuse Amp Size: 3amp TIME CLOSED: 2045 Cause: Birdstrike Weather (wind/rain): Follow up required (select advisory)? | .
3873 |  | JE24024307 | OKAIAWA | Western | OKAIAWA | 2024-07-05 | 9:50 | 2024-07-05 | 14:21 | 0.0014928 | 5.5179e-06 | 2 | 541 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Blown Transformer 5194E after 1x 10amp fuse replaced at 6568 Weather (wind/rain): Fine Follow up required (select advisory)? Replaced transformer 5194E ( Powerworks ) | .
3874 |  | JE24024447 | SPRINGVALE | Western | SPRINGVALE | 2024-07-05 | 12:56 | 2024-07-05 | 14:15 | 0.0065636 | 8.2769e-05 | 30 | 2379 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Repairs to cable at bottom of Transformer X3041 Fuses Crews are on linked related job - original parent cancelled so had to recreate for regulatory reporting. | .
3875 |  | JE24018904 | 341 WOODLAND ROAD TAHAWAI | Eastern | LINDERMANN RD | 2024-07-04 | 8:49 | 2024-07-04 | 16:16 | 0.055497 | 0.00012415 | 45 | 20115 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV/400v Poles 204425, 204426 & 204427. Replace 11kV cross arms 323976, 204424, 204429, 204430 & 204431. Isolation SB1-025. | .
3876 |  | JE24020575 | 50 LONGACRE ROAD OKOIA WANGANUI | Western | MAKIRIKIRI | 2024-07-04 | 9:19 | 2024-07-04 | 15:31 | 0.025665 | 6.8974e-05 | 25 | 9303 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace multiple defected Poles & X-Arms between 790749 & 790776 | .
3877 |  | JE24020856 | 12 market Rd Greytown | Western | EAST ST | 2024-07-04 | 8:45 | 2024-07-04 | 10:32 | 0.027448 | 0.0002621 | 95 | 9949 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re sag 11kv line and remove incorrect joints | .
3878 |  | JE24020859 | 32 JULIAN ROAD ONEMANA WHANGAMATA | Eastern | OPOUTERE | 2024-07-04 | 9:46 | 2024-07-04 | 11:37 | 0.0018284 | 1.6554e-05 | 6 | 663 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Arms at Pole R12977 | .
3879 |  | JE24020872 | 1062 MANAWA ROAD TINUI TINUI | Western | ANNEDALE | 2024-07-04 | 9:09 | 2024-07-04 | 14:33 | 0.073466 | 0.00022623 | 82 | 26628 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Isolation for vegetation cutting at poles 846352 - 848418, 838413 - 448961 | .
3880 |  | JE24020906 | 37 WAIMEA DRIVE TE PUKE TE PUKE | Eastern | TE MATAI RD | 2024-07-04 | 9:17 | 2024-07-04 | 13:11 | 0.0067864 | 4.9661e-05 | 18 | 2460 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 11kv link box maintenance | .
3881 |  | JE24020989 | 156 TE PARAE ROAD WAINUIORU MASTERTON | Western | WERAITI | 2024-07-04 | 9:32 | 2024-07-04 | 14:26 | 0.021038 | 7.1733e-05 | 26 | 7625 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Change 11kv arms from S164 to end of line | .
3882 |  | JE24021027 | 60 WARD STREET RAETIHI RAETIHI | Western | RAETIHI | 2024-07-04 | 9:00 | 2024-07-04 | 10:18 | 0.001938 | 2.4831e-05 | 9 | 702 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv Xarm at pole 775322. | .
3883 |  | JE24021039 | 201 LINCOLN ROAD INGLEWOOD INGLEWOOD | Western | LEPPERTON | 2024-07-04 | 9:45 | 2024-07-04 | 15:31 | 0.052506 | 0.00015174 | 55 | 19031 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Urgent Napa For crossarm changes on the following poles 742907 , 742910 , 742906 | .
3884 |  | JE24021280 | 18 MELROSE PLACE TOKOROA TOKOROA | Eastern | DALMENY ST | 2024-07-04 | 8:45 | 2024-07-04 | 12:11 | 0.041379 | 0.0002014 | 73 | 14998 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance IC3028-IC3047-IC3036-IC3049 | .
3885 |  | JE24021303 | 129 LOWER PAKIHIKURA ROAD WAITUNA WEST HUNTERVILLE | Western | WAITUNA | 2024-07-04 | 10:01 | 2024-07-04 | 14:41 | 0.003863 | 1.3795e-05 | 5 | 1400 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Switching for Asplundh vegetation contractor to complete works between poles P07466 - P07823 | .
3886 |  | JE24023516 | MANGATEPARU | Eastern | MANGATEPARU | 2024-07-04 | 7:24 | 2024-07-04 | 11:01 | 0.023226 | 0.00050213 | 182 | 8418 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Failed 7/16Cu Conductor @ Pole # K1035 Old damaged Conductor was the cause. Recloser 9320 never seen the fault and remained closed ! the line was on the ground and caused a small grass fire. Sean Molloy put the fire out. Protection on Rec 9320 needs checked!!! | .
3887 |  | JE24023562 | TURAKINA | Western | TURAKINA | 2024-07-04 | 12:08 | 2024-07-04 | 14:25 | 0.0060506 | 4.4143e-05 | 16 | 2193 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Replaced 1 X Insulator at Pole 802373 Isolated at Fuses 1424 | .
3888 |  | JE24023567 | WARDVILLE | Eastern | WARDVILLE | 2024-07-04 | 10:02 | 2024-07-04 | 12:21 | 0.00038279 | 2.759e-06 | 1 | 139 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses FC930 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 12:20 Cause: Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? No | .
3889 |  | JE24023568 | OLD TAURANGA RD | Eastern | OLD TAURANGA RD | 2024-07-04 | 10:07 | 2024-07-04 | 12:28 | 0.003909 | 2.759e-05 | 10 | 1417 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Related to NAPA 112062 - found rotten cross-Arms that needed repairing so isolated further out to repair these ICPs were not advertised, but makes sense to carry out repairs while power isolated - Isolated at FC1463 | .
3890 |  | JE24023582 | OPOUTERE | Eastern | OPOUTERE | 2024-07-04 | 12:04 | 2024-07-04 | 12:54 | 0.019834 | 0.00040005 | 145 | 7189 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 400v Neutral conductor broken in trees Pole R13039 Protection flags (nil where none): n/a CAUSE: Trees in LV & HV lines Location: Pole R13039 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Broken Neutral Conductor caused by trees, Houses could have sustained damage, HV Lines Isolated & earthed to safely to restrain Neutral conductor back up, Franklin Trees advised, SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3891 |  | JE24023592 | MOAWHANGO | Western | MOAWHANGO | 2024-07-04 | 15:31 | 2024-07-04 | 16:50 | 0.0010967 | 1.3795e-05 | 5 | 398 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: Faulty Transformer What was replaced? X1775 Where was it replaced (pole/TX/pillar box)? Pole Is 2R required? Y/N Yes 2R Y - What is the timeframe for repairs? Done same day Additional Info: Transformer for replacement tonight, approved by Paul Elston. Isolation at tx X1775 | .
3892 |  | JE24023644 | MANAIA | Western | MANAIA | 2024-07-04 | 17:11 | 2024-07-04 | 19:28 | 0.00038014 | 2.759e-06 | 1 | 138 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: M4165 CAUSE: Transformer was starting to leak Temp generation (stage details when used): n PERFORMANCE DETAIL DNO (number or state no): n Circuit patrolled & type: n Weather (wind/rain): calm Follow up required (select advisory)?n Additional fault restoration comments:n | .
3893 |  | JE24023670 | 145 PIONEER ROAD, TAHUNA, 3373 | Eastern | PATETONGA | 2024-07-04 | 20:30 | 2024-07-04 | 21:30 | 0.00033227 | 5.5179e-06 | 2 | 120 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Replaced broken cross arm at pole K13037 | .
3894 |  | JE24018899 | 440 WOODLAND ROAD TAHAWAI | Eastern | LINDERMANN RD | 2024-07-03 | 9:01 | 2024-07-03 | 16:00 | 0.052016 | 0.00012415 | 45 | 18854 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV/400v cross arms at Poles 204432, 204435, 204436 & 204443. Replace 11kV/400v Poles 263964, 204434, 204437, 204444. Reconductor 11kV between Poles 263964 & 204434. Isolation SB1-025. | .
3895 |  | JE24020639 | 7 SARJANT ROAD NETHERTON PAEROA | Eastern | AWAITI | 2024-07-03 | 9:15 | 2024-07-03 | 15:07 | 0.034024 | 9.6564e-05 | 35 | 12332 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Poe 877226 and hardware | .
3896 |  | JE24020737 | 262 RUATITI ROAD RAETIHI RAETIHI | Western | RAETIHI | 2024-07-03 | 9:45 | 2024-07-03 | 11:41 | 0.00031967 | 2.759e-06 | 1 | 116 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 2x DDO at TX Y301. Use live line to create linebreak at pole 775768 to help SADI. | .
3897 |  | JE24020835 | 356 WELCOME BAY ROAD WELCOME BAY TAURANGA | Eastern | WELCOME BAY | 2024-07-03 | 9:46 | 2024-07-03 | 16:07 | 0.18075 | 0.00047454 | 172 | 65512 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove temporary link cable between SD4-773 and 14835-4 installed Under NAPA 111496 .Remove cables from SD4-775 and Terminate into RMU 14835-3 , SD4-769 and terminate into 14835-4 and SD4-771 and terminate into 14835-2. Confirm that all cables removed from SD4-775 , SD4-773 , SD4-771 and SD4-769 . Remove old Switchgear | .
3898 |  | JE24020838 | 6379 STATE HIGHWAY 26 TIROHIA PAEROA | Eastern | TIROHIA-KARANGAHAKE | 2024-07-03 | 8:40 | 2024-07-03 | 12:30 | 0.0019015 | 8.2769e-06 | 3 | 689 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace HV arm on Pole N1405, 877044, N1407, N1408, N1409 | .
3899 |  | JE24020844 | 1018 TURAKINA VALLEY ROAD TURAKINA WANGANUI | Western | TUTAENUI | 2024-07-03 | 9:01 | 2024-07-03 | 10:28 | 0.00024012 | 2.759e-06 | 1 | 87 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace defected transformer due to high low voltage readings | .
3900 |  | JE24020853 | 46 PUKAHU ROAD NETHERTON PAEROA | Eastern | RAILWAY ST | 2024-07-03 | 10:01 | 2024-07-03 | 10:50 | 0.00013588 | 2.759e-06 | 1 | 49 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To Repair/Secure 11kv jumpers beyond fuses 14852. | .
3901 |  | JE24020855 | 11 BALMORAL DRIVE TOKOROA TOKOROA | Eastern | LOMOND AVE | 2024-07-03 | 8:45 | 2024-07-03 | 11:25 | 0.00044208 | 2.759e-06 | 1 | 160 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9044-1/2/3 | .
3902 |  | JE24021016 | 70 GLOVER ROAD HAWERA HAWERA | Western | ARGYLE ST | 2024-07-03 | 8:30 | 2024-07-03 | 16:14 | 0.06283 | 0.00013795 | 50 | 22773 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | run new bare weta hv conductor from pole 357039 to pole 722629 & install generator at pole 703704 for Kindy | .
3903 |  | JE24023374 | HAURAKI RD | Eastern | HAURAKI RD | 2024-07-03 | 0:01 | 2024-07-03 | 9:12 | 0.12923 | 0.00097667 | 354 | 46841 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV RECLOSER 9161/2 Protection flags (nil where none): C Ø O/C CAUSE: Car vs Pole Location: Pole 421 505 (Transformer TP3350 structure) Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Calm LFI (Y/N + Comments): Yes, LFI's operated at Pole O12692 on all three phases. Follow up Required (select advisory)? Yes Additional fault restoration comments: 00:18 - NZFS report car V pole - occupants still in car - 2049 SH25 Tu-rua 00:34 - Driver & passengers are trapped in the vehicle with HV Lines down. 01:05 - Field Switcher has taken instructions to Isolate the fault area between ABS IC423 & ABS IC2626 01:26 - After reporting the Isolations, NOC Closed in REC 9161/2 at 01:26 and using a remote back feed NOC Closed in SEC 14394/2 at 01:27 Outage area consists of six Transformers without Power. Field Switcher is currently busy sourcing the material for the job and applying Earths to the work site. 03:49 - Field Switcher carrying out repairs under AP 3374-01 Full power restored | .
3904 |  | JE24023375 | PARK RD | Western | PARK RD | 2024-07-03 | 2:18 | 2024-07-03 | 3:20 | 0.012144 | 0.00019589 | 71 | 4402 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 7607 No. Fuses: 2 Fuse Amp Size: 20 Amp TIME CLOSED: 03:19 Cause: Suspect Line Clash Weather (wind/rain): Windy Follow up required (select advisory)? No Please check Fuses 7607 | .
3905 |  | JE24023384 | MOTUMAOHO | Eastern | MOTUMAOHO | 2024-07-03 | 7:07 | 2024-07-03 | 11:30 | 0.041729 | 0.00050765 | 184 | 15125 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: Rec RC34 Protection flags (nil where none): C phase O/C CAUSE: Parrie / Paradise Duck hit Lines 7/16 Cu Dropped 3 x Lines @ Poles I1186-I13267 Location: 3 x Lines @ Poles I1186-I13267 - 11kV ABS 600 Section of Line Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Curse Weather (wind/rain): Slight Wind LFI (Y/N + Comments): Nil Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3906 |  | JE24023401 | pole_F13075 | Eastern | TE POI | 2024-07-03 | 9:50 | 2024-07-03 | 11:46 | 0.00064082 | 5.5179e-06 | 2 | 232 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | At transformer TC2714 broken stay wire dus to corrosion. Isolated transformer and replaced the broken stay with complete stay assembly. Part power at ICP caused by blown HV fuse 1 x 3A fuse. Full power restored. Fault logged at incorrect transformer. | .
3907 |  | JE24023435 | TIROHIA-KARANGAHAKE | Eastern | TIROHIA-KARANGAHAKE | 2024-07-03 | 11:32 | 2024-07-03 | 12:57 | 0.0093667 | 0.00011036 | 40 | 3395 | Unplanned | THIRD PARTY INTERFERENCE - OVERHEAD CONTACT | REGULATORY INFORMATION Voltage & Device ID: 400V Road crossing Protection flags (nil where none): nil Rec Opened for Safety CAUSE: Low 400v Road Crossing Hit with Tractor with Post Driver on the Back Location: 876969, DTX T1588, 4.2M Road Clearance. HV & LV need restrain. 2r left open to restrain lines. Ferdie to be advised. Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): Nil Follow up Required (select advisory)? Additional fault restoration comments: | .
3908 |  | JE24023458 | CLOTON RD SOUTH | Western | CLOTON RD SOUTH | 2024-07-03 | 14:15 | 2024-07-04 | 0:41 | 0.29705 | 0.0014429 | 523 | 107666 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 12155/2 opened for safety Protection flags (nil where none): Nil CAUSE: Car vs Pole Location: Pole 740727 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): 240 7003 for ABS 5586 Circuit patrolled and type: Yes Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Fault is on Cloton Rd CB 5, NOT CB 3 - Job Logged on wrong feeder HAZARD was reported by Fire Comms and REC 12155/2 was opened for safety. Isolation around the Pole 740727 was carried out. REC 12155/2 was closed in at 14:36 and a back feed from ING11 was put in via Gas switch 6283 at 15:24 Repairs were carried out under AP 3458-1 which had a great volume of work including ABS 5586 which was damaged. 04/07/2024 Power was restored via ABS 5477 at 00:41 and then via ABS 6645 at 00:51 DNO 240 7003 created for ABS 5586 which is still faulty and currently is wired straight through. | .
3909 |  | JE24023505 | ELTHAM TOWN NORTH | Western | ELTHAM TOWN NORTH | 2024-07-03 | 20:38 | 2024-07-04 | 15:28 | 0.078074 | 0.00040557 | 147 | 28298 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: Transformer 4394T Fuses CAUSE: Transformer failed at 4394T Location: Pole 737 176 Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Calm Follow up required (select advisory)? Additional fault restoration comments: Field Switcher found 1 x HV Fuse blown at Transformer 4394T He tried to reload + reliven and the Fuse blew back. (operated) Terrain is a bit challenging, approx 10m drop on one side and it is very dark. Field Switcher will return in the morning on 04/07/2024 Replaced transformer And 3 X DDOs | .
3910 |  | JE24020131 | 149 HOLLIS ROAD WAIKINO WAIHI | Eastern | OLD TAURANGA RD | 2024-07-02 | 9:20 | 2024-07-02 | 11:40 | 0.0065976 | 4.6902e-05 | 17 | 2391 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Pole P1996 | .
3911 |  | JE24020584 | 52 SOLDIERS ROAD WILTSDOWN TOKOROA | Eastern | KAURI ST | 2024-07-02 | 10:30 | 2024-07-02 | 12:56 | 0.0040157 | 2.759e-05 | 10 | 1456 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE POLE B0751 FITTED OUT WITH NEW HARDWARE | .
3912 |  | JE24020588 | 277 TOP ROAD PATETONGA MORRINSVILLE | Eastern | PATETONGA | 2024-07-02 | 9:54 | 2024-07-02 | 14:20 | 0.016177 | 6.0697e-05 | 22 | 5863 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace HV arm and DDO on Pole K13200 | .
3913 |  | JE24020598 | 630A PUKEKAURI ROAD WAIHI WAIHI | Eastern | OLD TAURANGA RD | 2024-07-02 | 9:32 | 2024-07-02 | 12:06 | 0.0029565 | 1.9313e-05 | 7 | 1072 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Arms at Pole 357429 | .
3914 |  | JE24020604 | 831 WAIRIRI ROAD BIDEFORD MASTERTON | Western | IHURAUA | 2024-07-02 | 8:36 | 2024-07-02 | 13:01 | 0.012435 | 4.6902e-05 | 17 | 4507 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace defect pole and crossarms - 831 Wairiri Road, Eketehuna | .
3915 |  | JE24020622 | 168 COLOMBO ROAD MASTERTON MASTERTON | Western | COLOMBO RD | 2024-07-02 | 8:45 | 2024-07-02 | 14:13 | 0.12505 | 0.00038074 | 138 | 45324 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv pole 833070 | .
3916 |  | JE24020748 | 49 MANFIELD STREET TOKOROA TOKOROA | Eastern | HARRIS BLOCK | 2024-07-02 | 10:15 | 2024-07-02 | 13:11 | 0.017393 | 9.9323e-05 | 36 | 6304 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance IC3115-IC3104-IC3101 | .
3917 |  | JE24020764 | 632 UPPER PITONE ROAD PITONE NEW PLYMOUTH | Western | INLAND COAST | 2024-07-02 | 9:46 | 2024-07-02 | 14:48 | 0.040825 | 0.00013519 | 49 | 14797 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Site 4 : Install new Entec eco Switch 121718 plus replace pole 757472. | .
3918 |  | JE24020886 | 300 HAURANGI ROAD RUAKOKOPUTUNA MARTINBOROUGH | Western | DYERVILLE | 2024-07-02 | 9:00 | 2024-07-02 | 11:45 | 0.019516 | 0.00011864 | 43 | 7074 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace broken pole 811366 - Safety measure for LLP 11237-01 removed before livening Fuses 8158 | .
3919 |  | JE24020915 | 45 RIVER ROAD PAEROA PAEROA | Eastern | TIROHIA-KARANGAHAKE | 2024-07-02 | 10:16 | 2024-07-02 | 15:19 | 0.072761 | 0.00024003 | 87 | 26373 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Helicopter fibre between poles WKOPAO045 & WKOPAO040 | .
3920 |  | JE24023121 | 2157 Otaraoa Road, Tarata, 4387 | Western | TARATA | 2024-07-02 | 9:49 | 2024-07-02 | 11:06 | 0.0019252 | 2.4831e-05 | 9 | 698 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: Fuses 8600 No. Fuses: 1 Fuse Amp Size: 8A TIME CLOSED: 11:06 Cause: Line Clash Weather (wind/rain): Wind & Rain Follow up required (select advisory)? Additional Notes: Isolated at Fuses 8600 to Re-Sag lines between Poles 762152 & 762151 under 2R | .
3921 |  | JE24023139 | 132 AUSTIN ROAD, NORMANBY, HAWERA, 4673 | Western | TAWHITI RD | 2024-07-02 | 12:56 | 2024-07-02 | 14:44 | 0.0067155 | 9.1046e-05 | 33 | 2434 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 5 Protection flags (nil where none): Nil CAUSE: Worn out cross arm Location: Pole 722130 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4, Not patrolled. Weather (wind/rain): High wind / Rain LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: HV pin arm complete assembly replaced. Isolation between ABS KA737 and CA413. | .
3922 |  | JE24023176 | HUIROA | Western | HUIROA | 2024-07-02 | 12:10 | 2024-07-03 | 15:12 | 0.18355 | 0.00011312 | 41 | 66529 | Unplanned | HUMAN ERROR - POTENTIAL WORKMANSHIP | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 6413 Protection flags (nil where none): Reported no supply CAUSE: Tree through lines while third party contractor was cutting (CAC in switch pack, cannot see number, non-PAC) Location: Between poles 709281 to 709290 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4, cursory patrolled. Weather (wind/rain): High wind / Rain LFI (Y/N + Comments): no LFI's Follow up Required (select advisory)? No Additional fault restoration comments: 02/07 - 13:14 - Control advised this is unlikely to be restored today, this may require a helicopter to string new conductors to the poles. The trees are an issue and will need to be cleared as well. No eta advised yet. 03/07 - 10:11 - Talked to Downer Hub for an update - they advised Ashley is heading to site today Trees cut by tree contractor. Lines repaired. and livened at 15:12 200m 16mm² HDCu conductor Many MST 16mm² sleeves NDR to follow | .
3923 |  | JE24023186 | TAWHITI RD | Western | TAWHITI RD | 2024-07-02 | 9:33 | 2024-07-02 | 12:16 | 0.030091 | 0.00036694 | 133 | 10907 | Unplanned | LIGHTNING - LIGHTNING STRIKE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 6560/2 (NOC opened) Protection flags (nil where none): None CAUSE: Lightning strike Location: Pole 841159 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4, Cursory patrolled. Weather (wind/rain): Storm LFI (Y/N + Comments): Not installed Follow up Required (select advisory)? No Additional fault restoration comments: Blown Jumper at Rec 6560 Structure - Replaced 3 x 70mm2 Jumpers, HV Surge Arrestor & HV Insulator SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3924 |  | JE24023206 | IHAIA RD | Western | IHAIA RD | 2024-07-02 | 11:12 | 2024-07-02 | 15:45 | 0.0090135 | 3.3108e-05 | 12 | 3267 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Replace cross arm on pole 715117 burnt from fault and weathered badly. Isolated from fuses TA189 Cross arm complete assembly installed | .
3925 |  | JE24023211 | SEAWARD COAST | Western | SEAWARD COAST | 2024-07-02 | 10:00 | 2024-07-02 | 11:01 | 0.00050434 | 8.2769e-06 | 3 | 183 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Cause: Line Down due to Wind What was replaced? Pulled up Lines Where was it replaced (pole/TX/pillar box)? Pole Is 2R required? Y 2R Y - What is the timeframe for repairs? N/A Additional Info: Lines were energised on Arrival. Transformer 1060 was Isolated for repairs to take place. OFF time 10:00 - Restore Time 11:00 | .
3926 |  | JE24023215 | MAIN RD MOTONUI | Western | MAIN RD MOTONUI | 2024-07-02 | 8:04 | 2024-07-02 | 11:20 | 0.0016234 | 8.2769e-06 | 3 | 588 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: Fuses 5248 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 11:20 Cause: Wind Weather (wind/rain): Windy Follow up required (select advisory)? No | .
3927 |  | JE24023217 | TIRAUMEA | Western | TIRAUMEA | 2024-07-02 | 8:07 | 2024-07-02 | 11:25 | 0.020925 | 0.00044143 | 131 | 7584 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 4 Protection flags (nil where none): A, B ph O/C & E/F CAUSE: Broken king bolt Location: 375375 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: Cursory Weather (wind/rain): light wind LFI (Y/N + Comments): N Follow up Required (select advisory)? N Additional fault restoration comments: Line was isolated at ABS's V73 & V76 back feed from ALF I4 - Sect. 10610/2, to replace king pin. | .
3928 |  | JE24023267 | HIKUAI | Eastern | HIKUAI | 2024-07-02 | 9:01 | 2024-07-02 | 9:30 | 0.00016397 | 5.5179e-06 | 2 | 59 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Opened HV Fuses TC6451 to raise Taps Open 09:00 Closed 09:30Hrs | .
3929 |  | JE24023272 | WAREA | Western | WAREA | 2024-07-02 | 13:42 | 2024-07-02 | 16:02 | 0.00038722 | 2.759e-06 | 1 | 140 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Aluminum conductor wore through on the top of the insulator causing it to break. 5m Namu conductor and FT sleeves were used. | .
3930 |  | JE24023343 | WELCOME BAY | Eastern | WELCOME BAY | 2024-07-02 | 17:41 | 2024-07-02 | 18:00 | 0.00031921 | 1.6554e-05 | 6 | 116 | Unplanned | WILDLIFE - POSSUM | Isolated transformer to remove possum Power Off - 17:40 Power On - 18:00 | .
3931 |  | JE24023370 | PONATAHI | Western | PONATAHI | 2024-07-02 | 22:45 | 2024-07-03 | 0:04 | 0.0008733 | 1.1036e-05 | 4 | 317 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV Fuses 7267 Protection flags (nil when none): Nil, HV Fuses did not operate. CAUSE: HV Lines down due to a tree that fell over. (Strong winds) Location: Pole 457 528 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Strong winds Follow up required (select advisory)? Yes Additional fault restoration comments: Field Switcher found HV Lines down in the paddock. HV Fuses 7267 did not operate. Currently busy with Isolation & Earthing so that the HV Lines can be repaired under AP 3370-01 3/07/2024 Repairs completed and Full Power restored at 00:04 Isolation at Fuses 7267 | .
3932 |  | JE24016682 | 3269 TAIRUA ROAD PUKEPOTO HIKUAI | Eastern | HIKUAI | 2024-07-01 | 10:17 | 2024-07-01 | 15:24 | 0.018624 | 6.0697e-05 | 22 | 6750 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole U12632 | .
3933 |  | JE24020108 | 203 Haunui Road Tiraumea | Western | TIRAUMEA | 2024-07-01 | 9:45 | 2024-07-01 | 13:03 | 0.0087264 | 4.4143e-05 | 16 | 3163 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace red tagged pole P02614 | .
3934 |  | JE24020142 | 14 AMEKU ROAD RAETIHI RAETIHI | Western | RAETIHI | 2024-07-01 | 10:01 | 2024-07-01 | 12:22 | 0.010828 | 7.7251e-05 | 28 | 3925 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 776007 | .
3935 |  | JE24020456 | 13 PEAT AVENUE KAI IWI WANGANUI | Western | MISSION RD | 2024-07-01 | 9:00 | 2024-07-01 | 11:01 | 0.037127 | 0.000309 | 112 | 13457 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace broken 11KV Binders on poles 782130 & 769298 | .
3936 |  | JE24020473 | 614 LOWER PAKIHIKURA ROAD WAITUNA WEST HUNTERVILLE | Western | WAITUNA | 2024-07-01 | 8:31 | 2024-07-01 | 14:50 | 0.042907 | 0.00011312 | 41 | 15552 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Switching for Asplundh vegetation contractor to complete works between poles P07406 - P07414 | .
3937 |  | JE24020541 | 3 WILSON STREET BULLS BULLS | Western | PAREWANUI | 2024-07-01 | 9:30 | 2024-07-01 | 14:42 | 0.085186 | 0.00028141 | 102 | 30876 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace crossarms on multiples poles on Wilson street (Pole 803725 to 803759) and Watson street (Pole 803846 & 803854) | .
3938 |  | JE24020574 | 415 KEREONE ROAD MORRINSVILLE MORRINSVILLE | Eastern | KEREONE | 2024-07-01 | 8:41 | 2024-07-01 | 11:39 | 0.0014783 | 8.2769e-06 | 3 | 536 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace Pole I12515 with a new 11m concrete busck | .
3939 |  | JE24020586 | 163 BLUE PACIFIC PARADE RIVERSDALE BEACH MASTERTON | Western | BLAIRLOGIE | 2024-07-01 | 9:55 | 2024-07-01 | 11:45 | 0.00060835 | 5.5179e-06 | 2 | 221 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re level TX T4211 | .
3940 |  | JE24020643 | 699 KAUAERANGA VALLEY ROAD THAMES THAMES | Eastern | TOTARA | 2024-07-01 | 9:16 | 2024-07-01 | 10:52 | 0.0037229 | 3.8625e-05 | 14 | 1349 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REMOVE 11KV RECLOSURE 9930/2 FOR SERVICING THEN RETURN TO SEVICE | .
3941 |  | JE24023004 | OPOUTERE | Eastern | OPOUTERE | 2024-07-01 | 9:19 | 2024-07-01 | 9:25 | 0.0089673 | 0.0014071 | 510 | 3250 | Unplanned | HUMAN ERROR - PROTECTION SETTINGS - INCORRECT/ERROR | RC 28 tripped on over load during switching for NAPA 110376. Trips at 60 amps. Protection are aware of this due to other shut downs. | .
3942 |  | JE24023014 | PEPE RD | Eastern | PEPE RD | 2024-07-01 | 9:50 | 2024-07-01 | 11:53 | 0.12453 | 0.0027424 | 994 | 45137 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: CB 1 and Recloser 9973 Protection flags (nil where none): A, B, C OC CAUSE: Unknown Location: N/A Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): Rain LFI (Y/N + Comments): None Follow up Required (select advisory)? No Additional fault restoration comments: Patrolled nothing found, restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3943 |  | JE24023062 | IHAIA RD | Western | IHAIA RD | 2024-07-01 | 13:17 | 2024-07-01 | 17:04 | 0.10334 | 0.00097116 | 275 | 37454 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB TA1 Protection flags (nil where none): E/F CAUSE: Floating conductor Location: Pole 715299 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4, cursory patrolled. Weather (wind/rain): Rain /windy LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Lines isolated and 1 x binder replaced. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3944 |  | JE24023068 | PIHAMA | Western | PIHAMA | 2024-07-01 | 14:35 | 2024-07-01 | 21:15 | 0.073685 | 0.0010181 | 369 | 26707 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Please patrol from sub to ABS TA875 possible blown jumper or burnt ABS contact. Contact NOC. Repair jumper at Pole 467539/467540 Outage on TA8 and TA9 and TA2. | .
3945 |  | JE24023092 | IRIRANGI | Western | IRIRANGI | 2024-07-01 | 14:24 | 2024-07-01 | 17:13 | 0.0051333 | 3.0349e-05 | 11 | 1861 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 2563 No. Fuses: 2 Fuse Amp Size: 8 Amp TIME CLOSED: 17:12 Cause: Unknown Weather (wind/rain): Windy, Raining Follow up required (select advisory)? N | .
3946 |  | JE24023109 | WERAITI | Western | WERAITI | 2024-07-01 | 14:42 | 2024-07-01 | 16:10 | 0.063212 | 0.00096012 | 348 | 22912 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV CB C830 Protection flags (nil where none): B, C Ph Fault CAUSE: Unknown, No Fault Found Location: Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Windy, Raining LFI (Y/N + Comments): N/A Follow up Required (select advisory)? N Additional fault restoration comments: HLT was applied for tree trimming but they had completed work at time of tripping. | .
3947 |  | JE24023111 | recloser_C421:2 | Western | LONGBUSH | 2024-07-01 | 14:46 | 2024-07-01 | 17:55 | 0.053625 | 0.00034763 | 103 | 19437 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV Recloser C421 Protection flags (nil where none): A, C Ph Fault CAUSE: Tree contacting Lines Location: Between Poles 371672 & 453423 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Windy, Raining LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Yes Additional fault restoration comments: FM to defect trees 19:48 - Downer Hub called me to close off the 1R's as they were having issues earlier. Working off the information I have I will close off this job, looks like trees were made contact with the O/H Lines and full Power was restored at 17:54 - BR | .
3948 |  | JE24023117 | APITI | Western | APITI | 2024-07-01 | 15:18 | 2024-07-01 | 16:15 | 0.00047252 | 8.2769e-06 | 3 | 171 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: Transformer T4/126 No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 16:15 Cause: Weather Weather (wind/rain): Wind Follow up required (select advisory)? No Job at Acknowledged. Needs closing out. Tom Childs needs putting on site | .
3949 |  | JE24023119 | BROWNE ST | Western | BROWNE ST | 2024-07-01 | 17:22 | 2024-07-09 | 14:40 | 0.20385 | 0.00069802 | 69 | 73886 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | PD tracking on Sw/Gear 8929/2 causing tripping. This was identified the next day. Sw/Gear was replaced DNO 2407002 Generators connected to 4535T @ 01:33 02/07/24 and 2970T @01:23 02/07/24. Transformer 4307T @ 10:51 02/07/24. 04/07/24 E00136 Switching to replace sw/gear 8928 & clean terminations. Generation applied to Transformer 2967T @ 09:00 , Removed at 17:11 E00136 was advertised 03/07 at 13:15 08/07/24 Generation off 07:30 on at 08:45 due to fault 09/07/2024 - Remove Generation and connect HV cables E00139 today. Generation removed at 14:00to 4535T, 2970T & 4307T. supply restored at 4535T @ 14:45, 2970T @ 14:40 & 4307T @ 14:50 All work has been completed under Switching 3119, by Blair Gregg | .
3950 |  | JE24023130 | recloser_6413 | Western | HUIROA | 2024-07-01 | 16:01 | 2024-07-01 | 19:35 | 0.017073 | 0.00011312 | 41 | 6188 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 6413/2 Protection flags (nil where none): O/C B - C Ø CAUSE: Unknown, suspect line clash in high winds Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: cursory Weather (wind/rain): windy, heavy rain LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: | .
3951 |  | JE24023150 | recloser_C431:2 | Western | CHESTER RD | 2024-07-01 | 17:56 | 2024-07-01 | 19:35 | 0.029993 | 0.00059318 | 215 | 10871 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Reclosure C431 Protection flags (nil where none): E/F CAUSE: Unknown Location: Unknown Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Windy & rain LFI (Y/N + Comments): Yes but no comms, checked on site. Follow up Required (select advisory)? Yes, to investigate no comms at LFI which is on Pole 825013 Additional fault restoration comments: Full Line Patrol was carried out by the two Field Switchers on site. Full Power restored at 19:35 No fault found. | .
3952 |  | JE24023163 | recloser_14568:2 | Eastern | MAKETU | 2024-07-01 | 18:44 | 2024-07-02 | 1:22 | 0.12568 | 0.0005849 | 212 | 45554 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV SEC 14568/2 Protection flags (nil where none): B Ø O/C & E/F CAUSE: Tree brought down HV Lines Location: Pole 263966 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Rain & wind LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Field Switcher on site & busy with a Line Patrol from SEC 14568/2 to the end which is at two NOP's at ABS IP542 & ABS IP687 Tree was found on the ground and brought down HV Lines past ABS SE7-036 Isolated at ABS SE7-036 & then NOC Closed in SEC 14568/2 at 21:06 Four Transformers still without Power. Repairs are being carried out under AP 3163-01 Full power restored | .
3953 |  | JE24023175 | CLOTON RD NORTH | Western | CLOTON RD NORTH | 2024-07-01 | 22:37 | 2024-07-02 | 0:45 | 0.010231 | 8.001e-05 | 29 | 3708 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Replace 3 x Fuses and resag lines at Pole 734469 | .
3954 |  | JE24023179 | COAST ROAD | Western | COAST ROAD | 2024-07-01 | 22:32 | 2024-07-05 | 14:12 | 1.5363 | 0.0010456 | 188 | 556827 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: CB 4 Protection flags (nil where none): 3 phase OC EF CAUSE: Trees down through forestry block causing multiple poles to break & lines down. Temporary line breaks cut between poles P23629 & P01004 to start restoration at front of feeder. Location: P04335 Temp generation (state details when used): Yes PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): windy LFI (Y/N + Comments): N Follow up Required (select advisory)? Additional fault restoration comments: Received call from customer advising of pole & lines down at 165 Coast Rd. Lines isolated at ABS's V49 & V51 and 2 Temporary line breaks cut between poles P23629 & P01004 . 11kV Generator is connected at Pole P01013 04/07/2024 Gen started with Load up to REC V61 at 00:54 NOC Closed in REC V61 at 00:57 Entry into logbook/dressed on SCADA tile & updated on eMap | .
3955 |  | JE24023184 | MATAROA A | Western | MATAROA A | 2024-07-01 | 23:12 | 2024-07-02 | 9:59 | 0.012497 | 1.9313e-05 | 7 | 4530 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Isolated at Fuses 914 to make safe. Lines are all cross country and will need a quad to patrol. Will return in the morning. Fuses CLOSED at 09:58. Cause was Twisted wires due to Weather | .
3956 |  | JE24022917 | 48 PURIRI STREET, GONVILLE, WANGANUI, 4501 | Western | PURIRI ST | 2024-06-30 | 3:58 | 2024-06-30 | 11:28 | 0.45046 | 0.0010015 | 363 | 163271 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Car V Pole at Pole 765714. Isolated at ABS 736, 1274 & links 4771/6 Pole and hardware replaced, Full power restored to all but 4 customers by 11:27 (HV restored at 11:27), the 4 remaining customers restored by 14:12 as LV cable work was required to reattach LV service cables to new pole | .
3957 |  | JE24022942 | MAKINO | Western | MAKINO | 2024-06-30 | 14:11 | 2024-06-30 | 19:01 | 0.4712 | 0.0038625 | 1400 | 170788 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 22 Protection flags (nil where none): O/C A, B & C CAUSE: Lines down / faulty hardware Location: Pole P18383 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): calm LFI (Y/N + Comments): Y Sw/Gear 10231 operated Follow up Required (select advisory)? n Additional fault restoration comments: Did not liven feeder untill faultman has sited the lines down due to multiple Emergency calls , faulty network isolated at Sw/Gear 227 & 326, 2 x lines down and broken cross arm at Pole P18383, 1 x Line down closer to Sw/Ger 326 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): Firecomms updated Lines on ground outside 70 Lethbridge - F4004187 | .
3958 |  | JE24022945 | REVANS ST | Western | REVANS ST | 2024-06-30 | 17:02 | 2024-06-30 | 19:17 | 0.023863 | 0.00017657 | 64 | 8649 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID:11kV REC C634/2 (Did not trip, used as Isolation point) Protection flags (nil where none): Nil CAUSE: Car vs Pole Location: Pole 798442 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? Yes Additional fault restoration comments: Line was isolated at ABS S505, ABS C634/1 & Links C634/6. Fire Comms confirmed its at Pole 798442 Car vs Pole reported by Fire Comms, no device tripped. 11kV Pole is a straight pin pole, only HV and all conductors remained up in the air. Field Switcher is busying gathering material & a bucket truck before we switch off the Power to repair the fault. Power OFF at 17:02 Isolation & earthing is now taking place, repairs are being carried out under AP 2945-01 by Benjamin Johnston | .
3959 |  | JE24022856 | HUNTERVILLE 22KV | Western | HUNTERVILLE 22KV | 2024-06-29 | 9:13 | 2024-06-29 | 11:23 | 0.0061371 | 4.6902e-05 | 17 | 2224 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 057 No. Fuses: 2 Fuse Amp Size: 6 Amp TIME CLOSED: 11:23 hrs Cause: Unk Weather (wind/rain): Calm Follow up required (select advisory)? | .
3960 |  | JE24022884 | TAVERNER ST | Western | TAVERNER ST | 2024-06-29 | 19:17 | 2024-06-29 | 20:18 | 0.02428 | 0.00039729 | 144 | 8800 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Member of public reported sparking Pole 367896 near 2 Dalefield Road & SH2 Broken jumper at ABS S345 repaired | .
3961 |  | JE24022904 | TE PUNINGA | Eastern | TE PUNINGA | 2024-06-29 | 18:24 | 2024-06-29 | 21:41 | 0.0026665 | 1.3795e-05 | 5 | 967 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses FP761 No. Fuses: 1 Fuse Amp Size: 6A TIME CLOSED: 21:40 Cause: Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? No Fuses Location: Fuses FC2220 No. Fuses: 2 Fuse Amp Size: 20A TIME CLOSED: 21:30 Cause: Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? No | .
3962 |  | JE24022796 | MANGATARATA | Eastern | MANGATARATA | 2024-06-28 | 0:41 | 2024-06-28 | 3:57 | 0.05576 | 0.00035315 | 128 | 20211 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 13066 Protection flags (nil where none): E/F CAUSE: Suspect Opossum, Old one found and removed Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: curse Weather (wind/rain): windy rain LFI (Y/N + Comments): nil Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3963 |  | JE24022799 | OKOROIRE | Eastern | OKOROIRE | 2024-06-28 | 7:54 | 2024-06-28 | 11:56 | 0.044202 | 0.00087183 | 316 | 16021 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 9 Protection flags (nil where none): CB 9 E/F, (Rec RP02 Trip flag Operated O/C A & B) CAUSE: Line down Location: D12885 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): calm LFI (Y/N + Comments): y, Operated at Pole D1703 A & B Follow up Required (select advisory)? n Additional fault restoration comments: Trip info indicated fault past Rec RP02 O/C A & B Trip flags operated, Opened Rec RP02 closed CB 9 & it Tripped, waited for faultman to patrol line, Line down found past ABS 900, isolated ABS 900, Lines repaired, line showed line clash damage, full power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3964 |  | JE24022814 | APATA | Eastern | APATA | 2024-06-28 | 12:26 | 2024-06-28 | 13:54 | 0.028606 | 0.00057111 | 207 | 10368 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 9489/2 Protection flags (nil where none): O/C B & C CAUSE: Unknown Location: na Temp generation (state details when used): na PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): calm LFI (Y/N + Comments): y, operated on site at Pole 205596(Main Line) Follow up Required (select advisory)? n Additional fault restoration comments: Line patrolled, no fault found, full power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3965 |  | JE24022833 | OPOUTERE | Eastern | OPOUTERE | 2024-06-28 | 21:12 | 2024-06-28 | 21:37 | 0.0046621 | 0.00018761 | 68 | 1690 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Cause: Failed 400v Cutout / Andalec Fuse Holder on DTX TC3630 What was replaced? Where was it replaced (pole/TX/pillar box)? DTX TC3630 LV Side Is 2R required? Y/N yes 2R Y - What is the timeframe for repairs? Fast Additional Info: Transformer was Isolated at Sw/G IC2013 to safely replace the Fuseway | .
3966 |  | JE24022842 | OPOUTERE | Eastern | OPOUTERE | 2024-06-28 | 22:56 | 2024-06-28 | 23:19 | 0.0043463 | 0.00018761 | 68 | 1575 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Cause: Deterioration Andelec Cutout Replaced What was replaced? Where was it replaced (pole/TX/pillar box)? DTX TC3630 LV Side Is 2R required? Y/N yes 2R Y - What is the timeframe for repairs? Additional Info: Mitch is going to defect the LV side of DTX TC3630 HV isolation at IC2013 | .
3967 |  | JE24018876 | 313 WOODLAND ROAD TAHAWAI | Eastern | LINDERMANN RD | 2024-06-27 | 9:06 | 2024-06-27 | 15:10 | 0.045161 | 0.00012415 | 45 | 16369 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV/400v Poles 204417, 204418, 204419, 204420, 204421 & 204422. Reconductor 11kV between Poles 204418 & 204419. Isolation SB1-025. | .
3968 |  | JE24020094 | 3376 TARATA ROAD PURANGI INGLEWOOD | Western | TARATA | 2024-06-27 | 9:31 | 2024-06-27 | 15:22 | 0.016452 | 4.6902e-05 | 17 | 5963 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace various crossarms in between poles 762287 - 762308 | .
3969 |  | JE24020096 | 142 DALRYMPLES ROAD PAREWANUI BULLS | Western | PAREWANUI | 2024-06-27 | 9:02 | 2024-06-27 | 14:10 | 0.0076375 | 2.4831e-05 | 9 | 2768 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace three poles, 809719 (Tx 1870) 809718, 809714 | .
3970 |  | JE24020102 | 431 MATARAWA ROAD KINLEITH TOKOROA | Eastern | OLD CAMBRIDGE RD | 2024-06-27 | 8:30 | 2024-06-27 | 11:07 | 0.023291 | 0.00014898 | 54 | 8442 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace pole A0281, HV arm on pole A0244 and screw anchor on Pole 269977 | .
3971 |  | JE24020112 | 40 MILL ROAD PAEROA PAEROA | Eastern | RAILWAY ST | 2024-06-27 | 9:00 | 2024-06-27 | 15:13 | 0.014374 | 3.8625e-05 | 14 | 5210 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE 11KV POLE'S N1243,876692,876691,N13241,N1247,N1248,N1249 | .
3972 |  | JE24020138 | 1068 FITZHERBERT EAST ROAD AOKAUTERE PALMERSTON NORTH | Western | AOKAUTERE | 2024-06-27 | 9:30 | 2024-06-27 | 13:10 | 0.040035 | 0.00018209 | 66 | 14511 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | remove Temp083, temp084 and temp086 | .
3973 |  | JE24020316 | 217 MT HOLDSWORTH ROAD MOUNT HOLDSWORTH CARTERTON | Western | HOLDSWORTH | 2024-06-27 | 9:01 | 2024-06-27 | 12:11 | 0.01104 | 5.7938e-05 | 21 | 4002 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles past fuses 7064 | .
3974 |  | JE24020374 | 20 PIONEER ROAD NEW PLYMOUTH | Western | PORT TARANAKI | 2024-06-27 | 9:15 | 2024-06-27 | 10:49 | 0.00025985 | 2.759e-06 | 1 | 94 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Carry out AUFLS changes to feeder relays at Moturoa sub CB9. Open remove from service only. Work requested by Powerco as URGENT. Have discussed with key customer team see attached email | .
3975 |  | JE24020375 | 254 WAITAWHETA ROAD WAIKINO WAIHI | Eastern | OLD TAURANGA RD | 2024-06-27 | 9:15 | 2024-06-27 | 12:27 | 0.050249 | 0.0002621 | 95 | 18213 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Poles and Arms at P1905, P1908, P1916 | .
3976 |  | JE24020713 | SH 1 KINLEITH TOKOROA | Eastern | OLD CAMBRIDGE RD | 2024-06-27 | 11:30 | 2024-06-27 | 11:40 | 0.00099819 | 9.9323e-05 | 36 | 362 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | at pole 422774 install smart Nav LFIs this is on the isolated side of ABS 1096 | .
3977 |  | JE24022670 | HIKUAI | Eastern | HIKUAI | 2024-06-27 | 8:55 | 2024-06-27 | 9:35 | 0.0004361 | 1.1036e-05 | 4 | 158 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Isolated & Earthed Fuses FP648 to check TFR TC1396 internal Fuses, fuses tested ok (regulatory outage for this TX, the rest is on the related job for the single-phase outage) Fuses Location: FP1354 No. Fuses: 1 Fuse Amp Size: 15 TIME CLOSED: 11:00 Cause: unknown Weather (wind/rain): calm Follow up required (select advisory)?n Line Patrolled | .
3978 |  | JE24019972 | 140 FRANKTON ROAD WAIHI WAIHI | Eastern | OLD TAURANGA RD | 2024-06-26 | 9:15 | 2024-06-26 | 14:19 | 0.025151 | 8.2769e-05 | 30 | 9116 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Arms at poles P12376, P13190, P13199, P13200 | .
3979 |  | JE24019989 | 48 POUAWHA ROAD PIRINOA FEATHERSTON | Western | BURNSIDE | 2024-06-26 | 9:16 | 2024-06-26 | 14:35 | 0.055447 | 0.00017381 | 63 | 20097 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Change 11kv arms from 811070 Pouawha Rd to end of line | .
3980 |  | JE24020022 | 6 KAIMATA ROAD NORTH KAIMATA INGLEWOOD | Western | KAIMATA | 2024-06-26 | 9:26 | 2024-06-26 | 14:42 | 0.011359 | 3.5867e-05 | 13 | 4117 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 759690 and install new recloser/links/tx/abs structure. Recloser ID 12688 | .
3981 |  | JE24020065 | 36 GLOVER ROAD HAWERA HAWERA | Western | GLOVER RD WEST | 2024-06-26 | 8:31 | 2024-06-26 | 14:10 | 0.042121 | 0.00012415 | 45 | 15267 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace 11kv poles 851614 , 703679 and 703680 & install generator at pole 703704 for Kindy | .
3982 |  | JE24020439 | 210 FITZHERBERT EAST ROAD AOKAUTERE PALMERSTON NORTH ( VARIOUS ADDRESSES& TARARUA WIND FARM) | Western | KELVIN GROVE 33kV | 2024-06-26 | 8:04 | 2024-06-26 | 14:13 | 0.0030463 | 8.2769e-06 | 3 | 1104 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 33KV Maintenance of ABS 3215,Z47,Z44,3214,Z221,Z223,Z224,ES Z227,ES Z228. Found 33kV ABS 3215 has a burnt up contact. One phase has been jumpered through. DNO 2406018 | .
3983 |  | JE24022546 | NGAMOTU RD | Western | NGAMOTU RD | 2024-06-26 | 1:50 | 2024-06-26 | 3:01 | 0.11311 | 0.0022182 | 804 | 40998 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Cb 6 Protection flags (nil where none): E/F, O/C A & B CAUSE: Cable Termination fault below Links 12380 Location: 748254 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): 2406016 Circuit patrolled and type: op Weather (wind/rain): calm LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Cable Termination fault below Links 12380, faulty cable isolated, feeder has been back feed, full power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
3984 |  | JE24022614 | PURIRI | Eastern | PURIRI | 2024-06-26 | 18:00 | 2024-06-26 | 22:42 | 0.0021694 | 1.6554e-05 | 3 | 786 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: Transformer No. Fuses: 3 Fuse Amp Size: 3A TIME CLOSED: 22:42 Cause: (unknown) 1972 Transformer Weather (wind/rain): Calm Follow up required (select advisory)?No 1 x 3A Fuse Replaced at TC1729 - unknown cause at first before transformer change - see SIS, replaced defective TX Whole transformer replaced Power on 22:42Hrs | .
3985 |  | JE24022636 | TAIHAPE TOWN NORTH | Western | TAIHAPE TOWN NORTH | 2024-06-26 | 15:04 | 2024-06-26 | 16:11 | 0.0001837 | 2.759e-06 | 1 | 67 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Isolated At ABS 4495 To Repair Jumper L/V side of Transformer 4657W | .
3986 |  | JE24022662 | HARRIS BLOCK | Eastern | HARRIS BLOCK | 2024-06-26 | 18:36 | 2024-06-26 | 20:01 | 0.00047071 | 5.5179e-06 | 2 | 171 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses FP137 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 20:00 Cause: ducks Weather (wind/rain): windy Follow up required (select advisory)? No | .
3987 |  | JE24016693 | 409 TAIRUA ROAD WHANGAMATA WHANGAMATA | Eastern | OPOUTERE | 2024-06-25 | 9:30 | 2024-06-25 | 15:52 | 0.060243 | 0.00016002 | 58 | 21835 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles R0737, R12968, R0748, R12935 & 650020. | .
3988 |  | JE24018623 | 877 LAKE ARAPUNI ROAD ARAPUNI PUTARURU | Eastern | HORAHORA | 2024-06-25 | 8:52 | 2024-06-25 | 14:25 | 0.038624 | 0.00011588 | 42 | 13999 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace HV crossarm on 11kV Pole M12939. Install stay insulator on 11kV Pole M0821. Tighten kingbolt on 11kV Pole M0802. Replace 11kV Pole M0791 with new 11m concrete busck Pole. Replace HV crossarm, DDO and transformer brackets on 11kV Pole M12928. Rebind HV conductor and replace LV crossarm on 11kV Pole M0773. Replace DDO and crossarm on Pole M12943. | .
3989 |  | JE24019918 | 51 FERRY ROAD BULLS BULLS | Western | PAREWANUI | 2024-06-25 | 10:02 | 2024-06-25 | 11:40 | 0.00027134 | 2.759e-06 | 1 | 98 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace termination X arms on pole 809085 (transformer X4330) | .
3990 |  | JE24019935 | 3 MILL RD PAEROA | Eastern | TIROHIA-KARANGAHAKE | 2024-06-25 | 9:01 | 2024-06-25 | 15:44 | 0.06887 | 0.00017106 | 62 | 24962 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE 11KV POLES: N13233,N1237,N1238,N13240,N1240,N1273. RECONDUCTOR 4 SPAN OF HV & LV, INSTALL POLE MT TEMP LINKS AT N13251 and TEMP ABS at N1273 | .
3991 |  | JE24019938 | 18 JANS TERRACE OAKURA OAKURA | Western | OAKURA | 2024-06-25 | 9:02 | 2024-06-25 | 19:07 | 0.27821 | 0.00054352 | 197 | 100840 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove Pole mount TX 1837N and install a new CFC RMU (12767) and a new 500kVA (1837N) ground mount TX. Northpower advise that a LV flash over occurred at their worksite. The NC asked that they submit a safety manager report on this. An incident occurred while carrying out the NAPA, ABS 535 couldn't be opened due to the load beyond it. CB 7 was opened to allow ABS 535 to be opened for the planned work to proceed.. | .
3992 |  | JE24019958 | 3376 TARATA ROAD PURANGI INGLEWOOD | Western | TARATA | 2024-06-25 | 9:31 | 2024-06-25 | 14:33 | 0.014191 | 4.6902e-05 | 17 | 5144 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace various crossarms in between poles 762287 - 762308 | .
3993 |  | JE24019980 | BURNS FORD ROAD BULLS | Western | PAREWANUI | 2024-06-25 | 9:25 | 2024-06-25 | 12:50 | 0.00056384 | 2.759e-06 | 1 | 204 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Terminate 11kv at pole 840891, remove span of conductor and remove pole 809502 | .
3994 |  | JE24019982 | 212 Otaranoho Rd Raetihi | Western | RAETIHI | 2024-06-25 | 9:55 | 2024-06-25 | 14:45 | 0.064815 | 0.00022348 | 81 | 23493 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 777868 & 777849. | .
3995 |  | JE24022373 | RANGIURU | Eastern | RANGIURU | 2024-06-25 | 9:19 | 2024-06-25 | 9:35 | 0.001714 | 0.00011036 | 40 | 621 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuse/Sw SE6-133 No. Fuses: 1 - became all with additional switching, see SIS Fuse Amp Size: 20 Amp 31A installed TIME CLOSED: 09:35 Cause: Suspect Duck strike in big Gully Weather (wind/rain): Calm Follow up required (select advisory)? Yes, SD Unit & Safelink Series 1 RMU's This particular Switchgear is a SD unit and in order to replace the blown Fuse the Switchgear must be de-energized from remote ends before any work can commence. NB! Safelink Series 1 RMU'sl needed to be operated - Field Switcher does not have s the OTA handle in his possession. Field Switcher has patrolled | .
3996 |  | JE24022380 | CENTRAL OTUMOETAI | Eastern | CENTRAL OTUMOETAI | 2024-06-25 | 10:12 | 2024-07-05 | 15:46 | 0.0089397 | 0.0002152 | 39 | 3240 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Cable from Fuses SD4-153 Failed Protection flags (nil where none): none CAUSE: 50yr old cable Failed, Powerco Replacing whole cable Location: Fuses SD4-153 site Temp generation (state details when used): Yes, Gen Set Installed @ 11:00 for DTX TD4-225 PERFORMANCE DETAIL DNO (number or state No): 2406017 Circuit patrolled and type: Curse Weather (wind/rain): Raining LFI (Y/N + Comments): nil Follow up Required (select advisory)? Additional fault restoration comments: Cable faulted un UFB cabinet. | .
3997 |  | JE24022440 | TAWAHA | Western | TAWAHA | 2024-06-25 | 10:34 | 2024-06-25 | 11:35 | 0.016427 | 0.00035867 | 130 | 5954 | Unplanned | THIRD PARTY INTERFERENCE - OVERHEAD CONTACT | REGULATORY INFORMATION Voltage & Device ID: 11kV CB C893 Protection flags (nil where none): DefT E/F CAUSE: Hiab hit lines offloading wood (Company was Mitch Pine) Location: 815223 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: n Weather (wind/rain): calm LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Customer call in fault to advise that Mitch Pine offloading wood contacted lines with Hiab, Line was isolated at Fuses 7201 to check line for damage, line found safe to re-liven. | .
3998 |  | JE24022460 | MOUNTAIN | Eastern | MOUNTAIN | 2024-06-25 | 13:03 | 2024-06-25 | 19:39 | 0.0297 | 0.00016554 | 60 | 10765 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: Rec 13420 Protection flags (nil where none): None CAUSE: Car v Pole Location: Pole 877022 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): LFI (Y/N + Comments): None Follow up Required (select advisory)? No Additional fault restoration comments: Pole 877022 replaced SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): Stu leaving site, another crew attending on 2R -This job associated with NAPA 110570 (planned outage isolation between ABS IC2113/IC505/Sec 14575 from 0900 - ICPs between IC505 and 547 restored at completion of planned outage) | .
3999 |  | JE24022480 | TAIHAPE TOWN NORTH | Western | TAIHAPE TOWN NORTH | 2024-06-25 | 15:07 | 2024-06-25 | 15:23 | 4.4971e-05 | 2.759e-06 | 1 | 16 | Unplanned | ADVERSE WEATHER - SNOW/ICE | Kevin Anderson isolated the transformer 4657W for safety. No fault was found. The transformer and LV panel were inspected and found no sign of burning or damage. The ambient temperature was low + - 5C and raining and the smoke was steam coming off the transformer and cables. A load check was done L - N 230V R Ø - 400V B Ø - 399V C Ø - 399V 157A - R Ø W Ø - 160A B Ø - 136A | .
4000 |  | JE24022510 | KOPU | Eastern | KOPU | 2024-06-25 | 17:05 | 2024-06-25 | 23:54 | 0.045047 | 0.00020692 | 75 | 16328 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | REGULATORY INFORMATION Voltage & Device ID: CB 1 Protection flags (nil where none): None CAUSE: Broken jumper Location: Pole S12461 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (N + Comments): Follow up Required (select advisory)? No Additional fault restoration comments: Shut areaextended from ABS IC363 to ABS IC1364 due safety reasons. Tap off jumpers to ABS IC2627 are underneath the live side wires to ABS IC362 hence Faultman feeling unsafe to use a ladder where jumpers are loose ...so Isolation point moved to ABS IC1364 Jumpers repaired power restored 23:48, 23:54 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4001 |  | JE24022528 | MCCABE ROAD | Eastern | MCCABE ROAD | 2024-06-25 | 20:55 | 2024-06-25 | 21:16 | 0.00027613 | 1.3795e-05 | 5 | 100 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Had to isolate only HV Fuses TC2505 to repair burnt neutral at the transformer HV Fuses ORT of 20:55, UTC 21:15 | .
4002 |  | JE24022534 | KAKARAMEA | Western | KAKARAMEA | 2024-06-25 | 19:22 | 2024-06-26 | 3:05 | 0.12387 | 0.0013795 | 382 | 44898 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB LI7 Protection flags (nil where none): E/F CAUSE: Broken Insulator Location: Pole 727927 Temp generation (state details when used): na PERFORMANCE DETAIL DNO (number or state No): na Circuit patrolled and type: op Weather (wind/rain): windy LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Feeder Tripped, Back feeds put in place, Line patrolled, Broken Insulator found, Isolated at ABS LI764 & LI757, Power restored to un-faulted part of network Insulator replaced, Full power restored, feeder restored to normal configuration. CB LI7 can not be Closed Remotely, Downer to Send Tech to look at Relay, Leave 2R Open Tech went to site and tested CB Li7 it opened and closed a Number of times SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4003 |  | JE24016696 | 2994 TAIRUA ROAD PUKEPOTO HIKUAI | Eastern | HIKUAI | 2024-06-24 | 9:16 | 2024-06-24 | 14:50 | 0.1457 | 0.00043592 | 158 | 52812 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles U0453, 320780 & U12533/U12532 | .
4004 |  | JE24018159 | 20 NORFOLK ROAD LOWER NORFOLK INGLEWOOD | Western | KAIMATA | 2024-06-24 | 9:15 | 2024-06-24 | 13:58 | 0.031165 | 0.00011036 | 40 | 11296 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 761507 and install new Entec/Links/TX structure. Entec ID 12695 | .
4005 |  | JE24018867 | 287 WOODLAND ROAD TAHAWAI | Eastern | LINDERMANN RD | 2024-06-24 | 8:57 | 2024-06-24 | 14:09 | 0.038725 | 0.00012415 | 45 | 14036 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV/400v cross arms at Pole 204408. Replace 11kV/400v Poles 204409, 204410, 204411 & 204412. Isolation SB1-025. | .
4006 |  | JE24019425 | 6 PEPPERILL ROAD LICHFIELD PUTARURU | Eastern | KAURI ST | 2024-06-24 | 9:46 | 2024-06-24 | 12:06 | 0.010004 | 7.1733e-05 | 26 | 3626 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | DEFECT. REPLACE LV CROSSARMS AT POLE M2036, AND REPLACE HV ARM AT POLE M2030 | .
4007 |  | JE24019722 | 62 GLOVER ROAD HAWERA HAWERA | Western | GLOVER RD WEST | 2024-06-24 | 8:31 | 2024-06-24 | 15:14 | 0.050017 | 0.00012415 | 45 | 18129 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace hv poles 703673 , 703676 and 703677 & install generator at pole 703704 for Kindy | .
4008 |  | JE24019819 | Pembroke Road, Stratford | Western | CARDIFF RD | 2024-06-24 | 8:46 | 2024-06-24 | 12:26 | 0.0036413 | 1.6554e-05 | 6 | 1320 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Perform oil maintenance at 8837/1/2/3 | .
4009 |  | JE24022199 | OKAIAWA | Western | OKAIAWA | 2024-06-24 | 7:04 | 2024-06-24 | 10:30 | 0.0068113 | 3.3108e-05 | 12 | 2469 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Fuses MA404 Protection flags (nil where none): Nil CAUSE: Line down Location: Pole 720161 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4, Not patrolled Weather (wind/rain): Calm LFI (Y/N + Comments): Not installed. Follow up Required (select advisory)? No Additional fault restoration comments: HV joint failure, line contacted 400V circuit. Line repaired and inspector checked installations on transformer M3057 and found no damage. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4010 |  | JE24022202 | DAIRY FACTORY | Western | DAIRY FACTORY | 2024-06-24 | 7:03 | 2024-06-24 | 10:46 | 0.0018449 | 8.2769e-06 | 3 | 669 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses 7232 No. Fuses: 2 Fuse Amp Size: 8A TIME CLOSED: 10:46 Cause: Birdstrike Weather (wind/rain): Calm Follow up required (select advisory)? No | .
4011 |  | JE24022262 | COROGLEN | Eastern | COROGLEN | 2024-06-24 | 11:43 | 2024-06-24 | 13:10 | 0.0067363 | 7.7251e-05 | 28 | 2442 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Replace broken Crossarm at pole W1236. Isolated at ABS 315 to allow repairs Cross arm replaced | .
4012 |  | JE24022277 | WESTMERE GLADSTONE | Western | WESTMERE GLADSTONE | 2024-06-24 | 11:54 | 2024-06-24 | 13:34 | 0.042769 | 0.00052696 | 191 | 15502 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV CB C948 Protection flags (nil where none): C ph E/F CAUSE: Unknown Location: ? Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: cursory Weather (wind/rain): rain LFI (Y/N + Comments): N Follow up Required (select advisory)? N Additional fault restoration comments: At time of tripping CB C948 had a HLT applied for tree work under CAC 111336-01, tree contractor contacted and advised that they had not made line contact, were asked to standdown until fault located or supply restored. | .
4013 |  | JE24022291 | 5643 STATE HIGHWAY 29, TIRAU | Eastern | TOTMANS RD | 2024-06-24 | 17:43 | 2024-06-24 | 22:08 | 0.014606 | 5.5179e-05 | 20 | 5294 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: 11kV ABS 2625 Location: Pole E12962 CAUSE: Deterioration (Red defect) Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Calm Follow up required (select advisory)? No Additional fault restoration comments: Pole replacement took place under AP 2291-1 Full Power was then restored at 22:08 | .
4014 |  | JE24022352 | HUNTERVILLE 22KV | Western | HUNTERVILLE 22KV | 2024-06-24 | 17:32 | 2024-06-24 | 19:37 | 0.003433 | 2.759e-05 | 10 | 1244 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 855 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 19:36 Cause: Possible bird strike Weather (wind/rain): calm Follow up required (select advisory)?n Line Patrolled | .
4015 |  | JE24022094 | CLOTON RD INDUSTRIAL | Western | CLOTON RD INDUSTRIAL | 2024-06-23 | 3:31 | 2024-06-23 | 11:46 | 0.083616 | 0.00054627 | 198 | 30307 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV, Rec 8764 Protection flags (nil where none): E/F, O/C A-B phase CAUSE: car v pole Location: 738412 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): wind, rain LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Isolated at ABS 6067, 6930, 6043, 5837, 5861 & 5840, Back feeds put in place, Pole replaced, Full power restored, back feeds removed SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4016 |  | JE24022096 | LOMOND AVE | Eastern | LOMOND AVE | 2024-06-23 | 10:57 | 2024-06-23 | 12:41 | 0.022078 | 0.00021244 | 77 | 8002 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | LV repairs required for TX TC3814. Isolation from CB 2, Sw/G 14726/1 Cause: Deterioration What was replaced? LB bushing repaired Where was it replaced (TX)? Is 2R required? Yes 2R Y - What is the timeframe for repairs? Additional Info: Toma advised TX bushing, all customers on the blue phase will be affected. A 2nd team will come out under the 2 R to completed in a few hours LV BUSHING REPAIRED ON BLUE PHASE | .
4017 |  | JE24022100 | SEAWARD COAST | Western | SEAWARD COAST | 2024-06-23 | 9:02 | 2024-06-23 | 11:12 | 0.011848 | 9.1046e-05 | 33 | 4294 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Line down at Pole 757193 Isolated at Fuses 6663 Line repaired (Line is very old and deteriorated, Downer to Defect), Full power restored, Also replaced 1 x 15A Fuse at Fuses 6664 under outage, line patrolled | .
4018 |  | JE24022101 | BAINESSE | Western | BAINESSE | 2024-06-23 | 6:39 | 2024-06-23 | 9:10 | 0.010878 | 7.1733e-05 | 26 | 3943 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: B20 No. Fuses: 2 Fuse Amp Size: 30 TIME CLOSED: 09:10 Cause: Unknown Weather (wind/rain): Rain Follow up required (select advisory)?n Line patrolled | .
4019 |  | JE24022126 | BAINESSE | Western | BAINESSE | 2024-06-23 | 9:57 | 2024-06-23 | 12:27 | 0.074478 | 0.00088839 | 322 | 26995 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 10277/2 Protection flags (nil where none): E/F, O/C B CAUSE: Broken Binder & insulator Location: P36067 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): wind, rain LFI (Y/N + Comments): no fault past LFI's Follow up Required (select advisory)? n Additional fault restoration comments: Line patrolled, Isolated at Fuses B20, Insulator replaced, full power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4020 |  | JE24022128 | ARAHINA 33KV | Western | ARAHINA 33KV | 2024-06-23 | 10:03 | 2024-06-23 | 11:21 | 0.05399 | 0.0025024 | 907 | 19569 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 33kV CB 3086 Protection flags (nil where none): E/F, O/C B CAUSE: Unknown Location: na Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): wind, rain LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: 33kV Feeder between Arahina & Rata Tripped, back feeds put in place for Rata CB 1350 using automated points, unable to back feed other feeders, Line patrolled, no fault found by faultman, line re-livened, Rata Sub power restored, faultman noted that there were a lot of magpies in the area SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Rata Sub Circuit that tripped: Arahina CB 3086 DTF (KM):na | .
4021 |  | JE24022130 | DEVON RD | Western | DEVON RD | 2024-06-23 | 9:52 | 2024-06-23 | 14:30 | 0.06433 | 0.001476 | 385 | 23317 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 12237/2 Protection flags (nil where none): E/F, O/C B CAUSE: Faulty TFR 1653 Location: 742403 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): lightning, rain LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Small back feed put in place, Line patrolled, Faulty TFR found, Power restored to feeder, TFR 1653 Replaced, feeder restored to normal configuration The adr for this customer is incorrect - 219 Waitara road feeding of TX 2155N Up to 217 Has Power and are fed from TX 383 219 Waitara is the physicl adr - TX 2155N feeds this property - ICP1000562632PCD7F AI e-mailed Yes | .
4022 |  | JE24022132 | MANOEKA RD | Eastern | MANOEKA RD | 2024-06-23 | 10:14 | 2024-06-23 | 13:52 | 0.075702 | 0.0057855 | 967 | 27439 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: TAH CB 4-Donor Feeder Protection flags (nil where none): C Phase EF CAUSE: CRACKED INSULATOR Location: POLE 223397 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): Rain LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Replaced insulator at pole 223397 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4023 |  | JE24022161 | MAIN RD MOTONUI | Western | MAIN RD MOTONUI | 2024-06-23 | 12:57 | 2024-06-23 | 14:23 | 0.0014177 | 1.6554e-05 | 6 | 514 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 4097T No. Fuses: 3 Fuse Amp Size: 2 TIME CLOSED: 14:22 Cause: Lightning Weather (wind/rain): lightning, rain Follow up required (select advisory)?n | .
4024 |  | JE24022170 | WALTON-KEREONE 33KV | Eastern | WALTON-KEREONE 33KV | 2024-06-23 | 14:48 | 2024-06-23 | 15:08 | 0.051362 | 0.0031231 | 1132 | 18616 | Unplanned | DEFECTIVE EQUIPMENT - ZONE SUBSTATION | REGULATORY INFORMATION Voltage & Device ID: CB 3122 & CB 17 Protection flags (nil where none): T1 Pressure REL CAUSE: faulty pressure relief sensor on the tap changer, Replaced under the DNO Location: Walton Sub Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): Yes 2406013 Circuit patrolled and type: Nil Weather (wind/rain): Lightning Rain LFI (Y/N + Comments): Nil Follow up Required (select advisory)? Yes Additional fault restoration comments: Oil level low in the Tap Changer. To check surge float 24/06/24.Refill Tap changer oil and take oil samples TFR T1 Tested, PRV Valve replaced and restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Walton Circuit that tripped: 3122 DTF (KM): N/A | .
4025 |  | JE24022187 | COLYTON | Western | COLYTON | 2024-06-23 | 21:49 | 2024-06-23 | 23:10 | 0.15028 | 0.0035977 | 1304 | 54469 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV, CB13 (Opened by NOC for safety) Protection flags (nil where none): N/A CAUSE: Broken 11kV fuse holder Location: T3/228 Isolation: 10576/3 & K12 Backfed: Yes via 10276 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: N/A Weather (wind/rain): Calm LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: When attempting reliven of Tx T3/228 HV fuse broke and live tail was sitting very close to LV. CB 13 Opened by NOC for safety until fault area could be Isolated. 11kV Fuse Holder and 20A HV fuse replaced. NOTE: Automated Sw/Gear 10576 would not operate by SCADA which increased outage area. OMS job JE24022196 created to check Sw/Gear | .
4026 |  | JE24019803 | 149 CORBETT ROAD BELL BLOCK NEW PLYMOUTH | Western | 149 CORBETT RD | 2024-06-22 | 8:36 | 2024-06-22 | 11:27 | 0.00047185 | 2.759e-06 | 1 | 171 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Perform oil maintenance at 133/1/2/4/5 | .
4027 |  | JE24019879 | Waitoa Sub | Eastern | NZDC INCOMER1 | 2024-06-22 | 6:57 | 2024-06-22 | 17:03 | 0.0016713 | 2.759e-06 | 1 | 606 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Service all 11kV CB's plus all 33kV ABS's and CB's at Waitoa Sub . Arranged with Fonterra . | .
4028 |  | JE24022033 | RANGITIKEI | Western | RANGITIKEI | 2024-06-22 | 0:01 | 2024-06-22 | 1:03 | 0.00017165 | 2.759e-06 | 1 | 62 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Advertised under E00134 on 21/06 at 13:55, outage is unplanned. Urgent outage to repair damaged LV cables connected to TX T6/694. | .
4029 |  | JE24022039 | recloser_4848 | Western | CLOTON RD INDUSTRIAL | 2024-06-22 | 9:16 | 2024-06-22 | 11:24 | 0.013012 | 0.00010208 | 37 | 4716 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Broken eye bolt at Recloser, low lines Isolated at ABS 5693 & 5861 3 eye bolts replaced due to rust & old age, Line pulled back up, Full power restored | .
4030 |  | JE24022089 | TAWAHA | Western | TAWAHA | 2024-06-22 | 21:46 | 2024-06-22 | 23:44 | 0.001297 | 1.1036e-05 | 4 | 470 | Unplanned | WILDLIFE - BIRD | Fuses Location: 8044 No. Fuses: 2 Fuse Amp Size: 8 TIME CLOSED: 23:43 Cause: Ducks Weather (wind/rain): Rain Follow up required (select advisory)? | .
4031 |  | JE24019435 | 60 HETHERINGTON ROAD TIRAU TIRAU | Eastern | OKOROIRE | 2024-06-21 | 8:31 | 2024-06-21 | 12:56 | 0.0242 | 9.1046e-05 | 33 | 8771 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace pole D12884 and ABS 900, HV arm on Pole D1662 and LV arm on Pole D12879 | .
4032 |  | JE24019665 | 27 OLD WAITEKAURI ROAD WAIKINO WAIHI | Eastern | WAITAWHETA | 2024-06-21 | 9:17 | 2024-06-21 | 15:48 | 0.19951 | 0.00051041 | 185 | 72313 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Stringing fibre between poles P13060 & 391361 | .
4033 |  | JE24019852 | 175 KURANUI ROAD MOTUMAOHO MORRINSVILLE | Eastern | MOTUMAOHO | 2024-06-21 | 9:46 | 2024-06-21 | 13:18 | 0.12833 | 0.00060421 | 219 | 46516 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | DEFECT. AT POLE I1300 REPLACE HV AND LV CROSSARMS FITTED OUT WITH NEW HARDWARE | .
4034 |  | JE24021898 | CLOTON RD SOUTH | Western | CLOTON RD SOUTH | 2024-06-21 | 0:35 | 2024-06-21 | 2:11 | 0.039087 | 0.0018982 | 688 | 14167 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kv CB 3 Protection flags (nil where none): B Phase Intrp E/F CAUSE: Unknown Location: Unknown Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): no Circuit patrolled and type: Patrolled Nothing Found Weather (wind/rain): Calm & COLD LFI (Y/N + Comments): Yes But set at Pole 738894 Flashing Outside on Scada But Middle on Site & Ones at Pole 737366 Flashing Middle Follow up Required (select advisory)? Additional fault restoration comments: Back feed in At Sec 12593 to Rec 4812 | .
4035 |  | JE24021905 | JE24021904 | Eastern | WHAKAMARAMA | 2024-06-21 | 5:54 | 2024-06-21 | 12:16 | 0.041558 | 0.00012139 | 44 | 15063 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Link Box TD2-008 Fuse L2 No. Fuses: 2 Fuse Amp Size: 20 Amp ( Oil ) TIME CLOSED: 12:15 Cause: Unknown (suspect bird strike) Weather (wind/rain): Clear Follow up required (select advisory)? No Suspect Fuses blown at Link Box TD2-008 at L2 Phil Brown is arranging crew support & testing equipment. Isolation: Fuses SD2-017 Test Permit taken to test HV Cable - results are all positive. Replaced Oil Fuses and then closed in at Fuses SD2-017 at 12:15 Cause unknown - suspect bird strike on the O/H Network | .
4036 |  | JE24022002 | TIKORANGI | Western | TIKORANGI | 2024-06-21 | 15:30 | 2024-06-21 | 16:50 | 0.028238 | 0.00040833 | 148 | 10235 | Unplanned | THIRD PARTY INTERFERENCE - OVERHEAD CONTACT | REGULATORY INFORMATION Voltage & Device ID: 11kV sectionaliser 12581 Protection flags (nil where none): EF & A phase OC CAUSE: truck tip bed making contact with lines Location: pole 762 560 Temp generation (state details when used): no PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: n/a Weather (wind/rain): fine LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4037 |  | JE24022024 | KIWITAHI | Eastern | KIWITAHI | 2024-06-21 | 20:15 | 2024-06-22 | 3:09 | 0.054233 | 0.0010512 | 373 | 19657 | Unplanned | WILDLIFE - POSSUM | REGULATORY INFORMATION Voltage & Device ID: DTX TC3498 Protection flags (nil where none): E/F CAUSE: Opossum Climbed Guy wire then caused flash over , Damaged Strains & Drop outs, Termination arms were in poor condition replaced all the equipment. Location: TC3498 Site Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: curse Weather (wind/rain): Fine LFI (Y/N + Comments): nil Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4038 |  | JE24022030 | COROGLEN | Eastern | COROGLEN | 2024-06-21 | 23:10 | 2024-06-22 | 0:17 | 0.008198 | 0.00012139 | 44 | 2971 | Unplanned | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Sec 13199, CB 4 A/R Protection flags (nil where none): E/F CAUSE: Suspect Opossum, Multiple on road when driving to Fault Contractor Reports. Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Curse Weather (wind/rain): Fine LFI (Y/N + Comments): Nil Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4039 |  | JE24018861 | 257 WOODLAND ROAD TAHAWAI | Eastern | LINDERMANN RD | 2024-06-20 | 9:03 | 2024-06-20 | 14:36 | 0.041314 | 0.00012415 | 45 | 14975 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV/400v cross arms at Pole 204403. Reconductor 11kV between Poles 204395 & 204413. Reconductor 11kV between Poles 204402 & 204403. Isolation SB1-025. | .
4040 |  | JE24019370 | 1436 CAPE PALLISER ROAD CAPE PALLISER FEATHERSTON | Western | BURNSIDE | 2024-06-20 | 9:31 | 2024-06-20 | 14:35 | 0.21594 | 0.00070905 | 257 | 78269 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 476859 and re sag 11kv conductors at multiple sites past C639/2 | .
4041 |  | JE24019410 | 122 PAPARAMU ROAD PIARERE TIRAU | Eastern | CAMBRIDGE RD TIRAU | 2024-06-20 | 9:23 | 2024-06-20 | 12:28 | 0.018366 | 9.9323e-05 | 36 | 6657 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace HV and LV arms at poles D0569 and D0584 | .
4042 |  | JE24019412 | 13 Rawhiti Rd, te Aroha | Eastern | MOUNTAIN | 2024-06-20 | 9:16 | 2024-06-20 | 10:15 | 0.00016246 | 2.759e-06 | 1 | 59 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Repair Stay Wire through HV and LV lines @ pole C1429 | .
4043 |  | JE24019422 | 22 NO7 Rd Waihou | Eastern | TATUANUI | 2024-06-20 | 12:30 | 2024-06-20 | 13:10 | 0.0028753 | 7.1733e-05 | 26 | 1042 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Repair Stay Wire through HV lines @ TX TP583 | .
4044 |  | JE24019432 | 84 GLOVER ROAD HAWERA HAWERA | Western | GLOVER RD WEST | 2024-06-20 | 8:30 | 2024-06-20 | 15:03 | 0.04872 | 0.00012415 | 45 | 17659 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace 11kv poles 703669 , 703670 , 703671 , 847976 & install generator at pole 703704 for Kindy | .
4045 |  | JE24019436 | 25 STANLY STREET EKETAHUNA EKETAHUNA | Western | EKETAHUNA | 2024-06-20 | 8:54 | 2024-06-20 | 14:33 | 0.12503 | 0.0003697 | 134 | 45317 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles P15233, P15154, 859087 and P12362. Replace transformer T8/6. Repair defect on ABS U4. | .
4046 |  | JE24019444 | NO 3 LINE | Western | NO 3 LINE | 2024-06-20 | 9:01 | 2024-06-20 | 13:54 | 0.075149 | 0.00025658 | 93 | 27238 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace X arms on poles 790995, 792031, 792034, 792035 re-sag conductor between poles 792130 and 455644 | .
4047 |  | JE24019985 | 4 WAIHIRERE DRIVE TUATEAWA COROMANDEL | Eastern | KAPANGA ROAD | 2024-06-20 | 8:36 | 2024-06-20 | 15:55 | 0.064524 | 0.00030349 | 55 | 23387 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To cut existing 11kV cable near base of pole V13384 and joint to new cable connected to switch /3 of CFCF. Turn existing 11kV cable into fuse switch /2 of new CFCF and terminate. Cut existing 11kV cable near intersection of Waihirere Drive from TX TC5029 and Kowhai Place and joint to new cable from fuse switch /4 to supply TX TC5079. Cut cables in front of sw/gear FC5057 and joint cables. Remove FC5057. ** Not all completed unable to thrust bore for SW 4 Transformer | .
4048 |  | JE24020873 | OTANE RD & TOP RD PATETONGA | Eastern | PATETONGA | 2024-06-20 | 9:42 | 2024-06-20 | 14:27 | 0.0031467 | 1.1036e-05 | 4 | 1141 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE LV XARMS AND INSTALL STAYWIRE INSULATORS. DEFECTS | .
4049 |  | JE24021762 | OPOUTERE | Eastern | OPOUTERE | 2024-06-20 | 7:47 | 2024-06-20 | 10:14 | 0.045752 | 0.00040005 | 145 | 16583 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Sec 13403 Protection flags (nil where none): E/F CAUSE: Suspect Tree Cutters hit lines, they know nothing! Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: curs, Weather (wind/rain): Fine LFI (Y/N + Comments): no Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4050 |  | JE24021816 | OKOROIRE | Eastern | OKOROIRE | 2024-06-20 | 16:37 | 2024-06-20 | 18:00 | 0.00068671 | 8.2769e-06 | 3 | 249 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: Isolated between ABS 829 & ABS 2650 Protection flags (nil where none): nil CAUSE: truck/tractor vs pole Location: Pole D1735 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: de-energised for pole replacement no tripping SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4051 |  | JE24021820 | BELVEDERE | Western | BELVEDERE | 2024-06-20 | 13:35 | 2024-06-20 | 15:04 | 0.00073949 | 8.2769e-06 | 3 | 268 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 7569 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 15:03 Cause: UNKNOWN Weather (wind/rain): Follow up required (select advisory)? | .
4052 |  | JE24021889 | TARATA | Western | TARATA | 2024-06-20 | 23:56 | 2024-06-21 | 1:08 | 0.01801 | 0.00025107 | 91 | 6528 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: 2337T No. Fuses: 1 (became all) Fuse Amp Size: TIME CLOSED: Cause: Barrel would not stay in so replaced all 3 Fuses via isolation at ABS 5275 Weather (wind/rain): Follow up required (select advisory)? | .
4053 |  | JE24019196 | 415 kotukuraeroa Rd, Taihape | Western | PAPAKAI | 2024-06-19 | 10:00 | 2024-06-19 | 10:06 | 0.00015478 | 2.4831e-05 | 9 | 56 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace ABS 424 due to stuck contacts. DNO2404007 | .
4054 |  | JE24019221 | 34 RAWAKA DRIVE KATIKATI KATIKATI | Eastern | WHARAWHARA ROAD | 2024-06-19 | 10:01 | 2024-06-19 | 12:05 | 0.0051462 | 4.1384e-05 | 15 | 1865 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Link box maintenance for TD4-094, TB1-095, TB1-118 and TB1-097 | .
4055 |  | JE24019269 | 313 PAHOIA ROAD WHAKAMARAMA TAURANGA | Eastern | PAHOIA | 2024-06-19 | 9:06 | 2024-06-19 | 10:36 | 0.0014959 | 1.6554e-05 | 6 | 542 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace xarms on pole 209036 | .
4056 |  | JE24019342 | 870 BIDWILLS CUTTING ROAD MORRISONS BUSH GREYTOWN | Western | TAWAHA | 2024-06-19 | 9:01 | 2024-06-19 | 14:51 | 0.022255 | 6.3456e-05 | 23 | 8066 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Repair conductor at pole 815235 and repair other defects past links 8040 | .
4057 |  | JE24021611 | PAHAUTEA 33KV TIE | Western | PAHAUTEA 33KV TIE | 2024-06-19 | 2:50 | 2024-06-19 | 3:03 | 0.036392 | 0.0027755 | 1006 | 13190 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: Recloser 3139/3141 Protection flags (nil where none): BC Fault, EF TUH, CAUSE: Unknown Location: N/A Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Calm LFI (Y/N + Comments): Yes on 11kV S598 ABS Follow up Required (select advisory)? No Additional fault restoration comments: Patrolled nothing found but suspected insultor fault at ABS S572 Bidwells SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4058 |  | JE24021698 | WHAKAMARAMA | Eastern | WHAKAMARAMA | 2024-06-19 | 14:02 | 2024-06-19 | 18:39 | 0.2428 | 0.0024555 | 570 | 88003 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 2 Protection flags (nil where none): O/C A - B - C Ø CAUSE:1st fault Tree fell onto lines 3Ø down // 2nd fault blown jumper Location: 1st fault at 209955 // 2nd fault at 263959 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4, cursory patrolled. Weather (wind/rain): Calm LFI (Y/N + Comments): Not installed Follow up Required (select advisory)? No Additional fault restoration comments: NDR to follow 1st fault - Tree fell onto lines caused all three lines down, repaired and livened but found part power once live. 2nd fault found blown off jumper at pole 263959 lines isolated and repaired SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4059 |  | JE24021751 | WAITUNA | Western | WAITUNA | 2024-06-19 | 21:56 | 2024-06-20 | 0:57 | 0.037128 | 0.00030624 | 111 | 13457 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV REC K45 Protection flags (nil where none): A, B & C Ph O/C CAUSE: unknown Location: ? Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: cursory Weather (wind/rain): calm LFI (Y/N + Comments): N - LFI comms failed pole P08848 Follow up Required (select advisory)? n Additional fault restoration comments: Line was Sectionalized and patrolled no fault found. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4060 |  | JE24021753 | THAMES COAST | Eastern | THAMES COAST | 2024-06-19 | 23:26 | 2024-06-20 | 1:36 | 0.10396 | 0.00079734 | 289 | 37680 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 4 Protection flags (nil where none): Nil - isolation between Rec 9228 and Sw/G 9571/1 CAUSE: Broken jumper to fuse link base Location: TC3597 Fuses Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: N/A Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Back feeds installed, Line isolated and jumper repaired as well as 3 x hv fuse bases, holders and 3 x 10A fuses Hamish McMillan assisted with Reg 9620 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4061 |  | JE24018830 | 24 TUAPIRO ROAD TAHAWAI | Eastern | BOWENTOWN | 2024-06-18 | 9:21 | 2024-06-18 | 12:45 | 0.00056412 | 2.759e-06 | 1 | 204 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Crossarms at pole 207080 | .
4062 |  | JE24018847 | 251 WOODLAND ROAD TAHAWAI | Eastern | LINDERMANN RD | 2024-06-18 | 8:59 | 2024-06-18 | 14:43 | 0.042698 | 0.00012415 | 45 | 15476 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV/400v Poles 204394, 204395, 262461, 204413, 204415, 204414. Replace 11kV cross arms at Pole 204416. Isolation SB1-025. | .
4063 |  | JE24018874 | 9041 STATE HIGHWAY 2 WAIHI WAIHI | Eastern | WAITAWHETA | 2024-06-18 | 9:17 | 2024-06-18 | 14:58 | 0.10166 | 0.00029797 | 108 | 36846 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Stringing fibre between poles P2145 & WKOGC019 | .
4064 |  | JE24018924 | 50 LONGACRE ROAD OKOIA WANGANUI | Western | NO 3 LINE | 2024-06-18 | 9:31 | 2024-06-18 | 15:04 | 0.047698 | 0.00014347 | 52 | 17288 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace cross arms on 11kV Poles 790750, 790791, 790786 & 790856. | .
4065 |  | JE24018937 | 2806 LAKE FERRY ROAD PIRINOA FEATHERSTON | Western | BURNSIDE | 2024-06-18 | 9:56 | 2024-06-18 | 13:50 | 0.0012948 | 5.5179e-06 | 2 | 469 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | change HV arms 797800 , 797804 , 797805 | .
4066 |  | JE24018944 | 2812 LAKE FERRY ROAD PIRINOA FEATHERSTON | Western | BURNSIDE | 2024-06-18 | 9:16 | 2024-06-18 | 12:39 | 0.00066785 | 1.1036e-05 | 4 | 242 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Change cross arms at 11kV Poles 797814, 797815 & 366085. | .
4067 |  | JE24018949 | 217 MANGAETUROA SOUTH ROAD RAETIHI RAETIHI | Western | RAETIHI | 2024-06-18 | 9:30 | 2024-06-18 | 11:15 | 0.0052202 | 4.9661e-05 | 18 | 1892 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv Xarm at pole 777137 And Staywire at pole 777118. | .
4068 |  | JE24019355 | 112 GLOVER ROAD HAWERA HAWERA | Western | ARGYLE ST | 2024-06-18 | 8:31 | 2024-06-18 | 18:31 | 0.0082677 | 1.3795e-05 | 5 | 2997 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace 11kv poles 722629 , 722630 , 703665 , 703667 and arms at pole 703666 | .
4069 |  | JE24020382 | 10 ARAWATA AVENUE WELCOME BAY TAURANGA | Eastern | WELCOME BAY | 2024-06-18 | 9:30 | 2024-06-18 | 15:45 | 0.094016 | 0.00025382 | 92 | 34076 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove cable at 9554-1 and terminate new 300 3C cable from 14839-1. Remove cable feeding TD4-548 at Link box SD4-158, extend and terminate into RMU 14839-2. Remove cable from Switchgear SD4-775 at Link box TD4-548, extend and terminate into RMU 14846/4. Install new cable from Fuse Switch 14846-2 to Transformer TD4-541 at Link box SD4-156. Remove Link box SD4-156 and 11kV Link box Fuses TD4-541-L1. Cap existing cables between TD4-541 and SD4-156. | .
4070 |  | JE24021450 | KEITH ST 24 | Western | KEITH ST 24 | 2024-06-18 | 7:03 | 2024-06-18 | 8:16 | 0.020094 | 0.00027314 | 99 | 7283 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: G161/T No. Fuses: 3 Fuse Amp Size: 30 TIME CLOSED: 08:16 Cause: Unknown Weather (wind/rain): Fine Follow up required (select advisory)? No Reliven L/V At 08:45 All tests good - see SIS for outage times | .
4071 |  | JE24021462 | COONOOR | Western | COONOOR | 2024-06-18 | 8:26 | 2024-06-18 | 9:06 | 0.0012066 | 3.0349e-05 | 11 | 437 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 11kV FusesT26 No. Fuses: 2 Fuse Amp Size: 8 TIME CLOSED: 09:05 Cause: suspected bird strike Weather (wind/rain): Follow up required (select advisory)? | .
4072 |  | JE24021493 | CASTLEHILL | Western | CASTLEHILL | 2024-06-18 | 11:42 | 2024-06-18 | 17:21 | 0.024504 | 0.00018485 | 47 | 8881 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11KV CB I15 Protection flags (nil where none): A Phase E/F CAUSE: Line Down due to broken conductor Location: pole PO6767 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Light Rain LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: | .
4073 |  | JE24021496 | COONOOR | Western | COONOOR | 2024-06-18 | 11:46 | 2024-06-18 | 14:37 | 0.00047188 | 2.759e-06 | 1 | 171 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: T7/329 No. Fuses: 2 Fuse Amp Size: 2 TIME CLOSED: 14:36 Cause: Unknown Weather (wind/rain): Rain Follow up required (select advisory)? | .
4074 |  | JE24021540 | 1207 MANAIA ROAD, KAPONGA, HAWERA, 4679 | Western | DUTHIE RD | 2024-06-18 | 14:24 | 2024-06-18 | 14:33 | 9.9323e-05 | 1.1036e-05 | 4 | 36 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | HV Fuses of transformer 3499T replaced and found to be cause of high impedance Fuses 399T opened 14:23 closed 1432 | .
4075 |  | JE24021547 | PIRINOA | Western | PIRINOA | 2024-06-18 | 13:34 | 2024-06-18 | 16:06 | 0.024842 | 0.00027314 | 99 | 9004 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | REGULATORY INFORMATION Voltage & Device ID: 11kv CB C926 Protection flags (nil where none): No Flags CAUSE: Twisted Conductor Location: at pole 797891 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): no Circuit patrolled and type: Cursory Weather (wind/rain): Light Rain LFI (Y/N + Comments): Yes Not Flashing at pole 848476 Follow up Required (select advisory)? No Additional fault restoration comments: | .
4076 |  | JE24021551 | PUTORINO | Western | PUTORINO | 2024-06-18 | 14:00 | 2024-06-18 | 16:22 | 0.0046833 | 3.3108e-05 | 12 | 1697 | Unplanned | WILDLIFE - OTHER | Fuses Location: Fused ABS4172 No. Fuses: 2 Fuse Amp Size: 20 TIME CLOSED: 16:21 Cause: cattle rubbing against stay wire on pole 945000, stay wire removed will be replaced under 2R with barrier to stop cattle Weather (wind/rain): Follow up required (select advisory)? stay wire replaced, barrier for cattle erected. | .
4077 |  | JE24021596 | TUTAENUI | Western | TUTAENUI | 2024-06-18 | 19:58 | 2024-06-18 | 21:56 | 0.013984 | 0.00011864 | 43 | 5068 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 426 No. Fuses: 2 Fuse Amp Size: 25 TIME CLOSED: 21:56 Cause: unknown Weather (wind/rain): calm Follow up required (select advisory)? | .
4078 |  | JE24017487 | 34 SHAW AVENUE PAEROA PAEROA | Eastern | SHAW AVE | 2024-06-17 | 8:53 | 2024-06-17 | 12:58 | 0.023591 | 9.6564e-05 | 35 | 8551 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Finish changing Safelink unit 13535/3 and /1 to remote control, with a control box motor. Same switching as NAPA 109654 . | .
4079 |  | JE24018526 | 210 MCQUOID ROAD PREECE POINT COROMANDEL | Eastern | MANAIA COROMANDEL | 2024-06-17 | 10:08 | 2024-06-17 | 13:00 | 0.0033218 | 1.9313e-05 | 7 | 1204 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace leaking transformer TC3410 | .
4080 |  | JE24018681 | 4816 STATE HIGHWAY 4 KAKATAHI WANGANUI | Western | PARAPARA | 2024-06-17 | 9:19 | 2024-06-17 | 15:04 | 0.0087892 | 0.00012415 | 29 | 3186 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Repair 11kV Conductor at Pole 783663.Replace 11kV Pole 783669 using digger. | .
4081 |  | JE24018795 | 305 AHU AHU VALLEY ROAD PAPARANGI WANGANUI | Western | WATERWORKS RD | 2024-06-17 | 8:35 | 2024-06-19 | 15:21 | 0.010754 | 2.4831e-05 | 3 | 3898 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Isolate 11kv line past fuses 1079 for tree felling | .
4082 |  | JE24021243 | WAIHI-WHANGAMATA 33KV | Eastern | WAIHI-WHANGAMATA 33KV | 2024-06-17 | 0:04 | 2024-06-17 | 11:09 | 10.3603 | 0.021992 | 6499 | 3755134 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 33kV WHI CB 3252 Protection flags (nil where none): B Ø E/F , Res E/F CAUSE: Broken suspension eyebolt Location: Pole P13725 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Rain & wind LFI (Y/N + Comments): Yes, none operated on SCADA. (33kV) Follow up Required (select advisory)? Yes Additional fault restoration comments: WHI CB 3252 Tripped and WGM BESS CB1112 & CB11 Tripped NOC opened WGM CB 19 & CB 17 NOC tried a closure on WHI CB3252 and it tripped & locked out. Trying to back feed WGM feeders, started with WGM CB1 NOC Opened. NOC Closed in SEC 9712/2 via WHI3 Very limited options on back feeding WGM S/S Field Switchers are busy carrying out a Line Patrol on the 33kV WHI CB3252 to WGM S/S 05:32 - Escalated to Haden Power to inform Media Team 09:18 - Nick & Wayde Off-Site on-stand-down. Crew has replaced them for repairs Broken suspension eyebolt on center phase found on pole P13725. Was repaired and livened at 10:35. Full restoration followed to Whangamata / Waihi Subs and was completed by 11:30 Batteries went flat on the back feed devices, no bypass ABS's SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): WGM S/S Circuit that tripped: 33kV WHI CB 3252 | .
4083 |  | JE24021250 | PYES PA | Eastern | PYES PA | 2024-06-17 | 2:16 | 2024-06-17 | 7:14 | 0.054509 | 0.00023727 | 73 | 19757 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV SEC 13578/2 Protection flags (nil where none): A B C Ø O/C & E/F CAUSE: Deterioration Location: Pole 217 036 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Rain LFI (Y/N + Comments): No Follow up Required (select advisory)? Yes Additional fault restoration comments: Feeder fault crew dispatched. Field Switcher on site busy with a Line Patrol. HV Lines down past Pole 217 036 Isolation at ABS TEMP022 On Friday 14/06/2024 the same fault happened past the same pole, performance team to investigate state of the O/H network at this site. Lines repaired 5m 16mm² HDCu. Broken HV Conductors repaired past Pole 217036. Full Power Restored 0714. | .
4084 |  | JE24021253 | KAITUNA | Eastern | KAITUNA | 2024-06-17 | 4:18 | 2024-06-17 | 15:43 | 0.045146 | 0.0002014 | 73 | 16363 | Unplanned | VEGETATION - OUTSIDE ZONE | Fuses Location: Fuse/Sw 9376/2 No. Fuses: 3 Fuse Amp Size: 56A HRC HV TIME CLOSED: 15:43 Cause: Tree brought down HV Lines Location: At TX TE6-020 Weather (wind/rain): Rain Follow up required (select advisory)? Please check Fuse/Sw 9376/2 SD Oil Filled Sw/Gear - Must be Isolated on remote ends to change Fuse, don't carry spares with them, only back at the depot. Mike James is busy with a Line Patrol. Tree brought down HV Lines at TX TE6-020 17/06/23 - Took Michael James off site as he is on stand-down, the crew will be out this morning to complete repairs - NDR - ND120380. 2nd 1R not required. Lines repaired and HV fuses replaced via isolation at ABS SE6-223 and SE6-009. 25mm² HD Cu conductor 3 x 56A HRC HV fuses | .
4085 |  | JE24021260 | MOROA | Western | MOROA | 2024-06-17 | 7:13 | 2024-06-17 | 10:52 | 0.0030216 | 1.3795e-05 | 5 | 1095 | Unplanned | WILDLIFE - BIRD | Fuses Location: 7495 No. Fuses: 2 Fuse Amp Size: 1 TIME CLOSED: 10:52 Cause: Wildlife - Birds Weather (wind/rain): Rain Follow up required (select advisory)? NIL | .
4086 |  | JE24021261 | TGA Sub - CB 19 - REC 9483 | Eastern | BETHLEHEM | 2024-06-17 | 7:32 | 2024-06-17 | 8:42 | 0.09462 | 0.0016305 | 591 | 34296 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 9483/2 Protection flags (nil where none): Nil / UV protection CAUSE: Unknown Location: Unknown Temp generation (state details when used): N/A PERFORMANCE DETAIL DNO (number or state No): 2406010 Circuit patrolled and type: F3 / Cursory patrolled. Weather (wind/rain): Rain LFI (Y/N + Comments): Yes fitted, no activation Follow up Required (select advisory)? Yes Additional fault restoration comments: Lines patrolled no fault found. The Rec 9483 was DNO'd as this has tripped multiple times in the last few months. The network has been back fed via Sec 9888/2 TGA14. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4087 |  | JE24021274 | PIAKOITI RD | Eastern | PIAKOITI RD | 2024-06-17 | 10:15 | 2024-06-17 | 11:45 | 0.0019853 | 2.2072e-05 | 8 | 720 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: 11kV Fuses FP947 No. Fuses: 3 Fuse Amp Size: TIME CLOSED: 11:45 Cause: Isolated at FP947 to replace broken cross arm at pole G0470 (see SIS) Weather (wind/rain): Follow up required (select advisory)? | .
4088 |  | JE24021337 | DUTHIE RD | Western | DUTHIE RD | 2024-06-17 | 11:23 | 2024-06-17 | 14:03 | 0.011441 | 7.1733e-05 | 26 | 4147 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2 x HV cross arms badly deteriorated poles 731772 & 731773 Isolated for replacement between ABS 5992, 5972 & 6017 OMS jumps past ABS 5972 to Zone Sub CB | .
4089 |  | JE24021341 | OLD TAURANGA RD | Eastern | OLD TAURANGA RD | 2024-06-17 | 11:12 | 2024-06-17 | 13:31 | 0.00076679 | 5.5179e-06 | 2 | 278 | Unplanned | WILDLIFE - BIRD | Fuses Location: 11kV Fuses FP1974 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 13:30 Cause: bird strike Weather (wind/rain): Follow up required (select advisory)? | .
4090 |  | JE24021351 | CARLTON AVE | Western | CARLTON AVE | 2024-06-17 | 11:51 | 2024-06-17 | 14:11 | 0.10332 | 0.0020002 | 725 | 37450 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 4 Protection flags (nil where none): A, B, C ph O/C & E/F CAUSE: Bird Strike Location: 362118 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: cursory Weather (wind/rain): rain LFI (Y/N + Comments): N Follow up Required (select advisory)? n Additional fault restoration comments: After line was sectionalized and isolated at ABS 1353 & Sw/Gear 4532/1 the Faultman found burnt bird on ground at pole 362118. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4091 |  | JE24021392 | RANGIURU | Eastern | RANGIURU | 2024-06-17 | 17:10 | 2024-06-27 | 15:24 | 0.00043711 | 5.5179e-06 | 1 | 158 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Fuses SF6-031 O.R.T @ 17:10 hrs. Trf TE6-168- Gen in Service at 19:30 Hrs.. DNO 2406012 Created, cable to be replaced under DNO work order. | .
4092 |  | JE24021400 | 7 NO. 9 ROAD, SPRINGDALE | Eastern | TE PUNINGA | 2024-06-17 | 19:56 | 2024-06-17 | 21:55 | 0.00033006 | 2.759e-06 | 1 | 120 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Transformer TC3329 REPLACED. Power off 19:55 Power ON 21:55 | .
4093 |  | JE24021401 | AOKAUTERE | Western | AOKAUTERE | 2024-06-17 | 15:38 | 2024-06-18 | 11:38 | 0.1787 | 0.0005242 | 190 | 64769 | Unplanned | HUMAN ERROR - POTENTIAL WORKMANSHIP | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 10225/2 Protection flags (nil where none): B ph O/C & E/F CAUSE: Tree through line Location: Multiple Pole Past P00908 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: cursory Weather (wind/rain): Fine LFI (Y/N + Comments): N Follow up Required (select advisory)? N Additional fault restoration comments: Tree contractor felling trees working on CAC 73088 call to report that a tree had come down and brought down the lines, Line was isolated at Fuses H34 to repair the lines down. Multiple lines down between poles P00903 & P00904, P00906 & P00907 & P00907 & P00908. Line to remain off over night from Fuses H34 due to- to dangerous to repair the lines in dark as no vehicle access as is in a forestry block, and has to done on foot, crews will return first thing in morning to repair the lines. Lines Repaired 18/06/24 : | .
4094 |  | JE24021434 | MAIN RD MOTONUI | Western | MAIN RD MOTONUI | 2024-06-17 | 18:31 | 2024-06-17 | 21:00 | 0.011109 | 7.4492e-05 | 27 | 4027 | Unplanned | WILDLIFE - POSSUM | Fuses Location: 5193 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 21:00 Cause: Possum Weather (wind/rain): calm Follow up required (select advisory)?n | .
4095 |  | JE24018965 | 154 HEADS ROAD GONVILLE WANGANUI | Western | GONVILLE AVE | 2024-06-16 | 9:01 | 2024-06-16 | 16:56 | 0.086493 | 0.00018209 | 66 | 31350 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replacing two high voltage poles number 770915 and 770919 | .
4096 |  | JE24021163 | 88 Te Puna Rd | Eastern | WAIPUNA | 2024-06-16 | 5:19 | 2024-06-17 | 15:44 | 0.15653 | 0.00044143 | 75 | 56735 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 9803/2 Protection flags (nil where none): Nil CAUSE: Car vs Pole Location: Pole 200 669 (Transformer Pole - TD3-025) Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? Yes Additional fault restoration comments: Car vs Pole. ETA required please - 35 Min Transformer TD3-025 is leaking oil. Busy replacing Transformer & Pole under AP 1163-01 SAFETY MANAGER required for oil spill. All HV restored 11:30 - except TD3-025 Transformer still not connected but HV RESTORED AT 11:30.Transformer pole still on the deck -Fatigue to Crew 18:10 Hrs Clint Johnstone--Looking for Gen Sets to Hook Trf TD3-025 20:20 Generators connected to LV Network at existing location of TX TD3-025 Full Power restored to all ICP's as per field switcher. 17-06-24 Temp line break was cut at pole 322630 to limit SAIDI and to supply the cool stores. Pole 200669 and 50kVa transformer TD3-025 replaced. The temp line break was closed and the network normalized. | .
4097 |  | JE24021168 | cnr Kimbolton & Haythorne Rds | Western | COLYTON | 2024-06-16 | 6:27 | 2024-06-16 | 10:32 | 0.017607 | 7.1733e-05 | 26 | 6382 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 7 Protection flags (nil where none): N/A feeder did not trip CAUSE: Car vs Pole Location: Pole P37087 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: N/A Weather (wind/rain): calm LFI (Y/N + Comments): N Follow up Required (select advisory)? n Additional fault restoration comments: Feeder was isolated at ABS's P1, P5, P36 & P37 to replace pole P37087 Report of car v Pole. Cnr Kimbolton Rd & Haythorne Rd, Kiwitea | .
4098 |  | JE24021173 | KUMENGA | Western | KUMENGA | 2024-06-16 | 7:39 | 2024-06-16 | 9:37 | 0.0012983 | 1.1036e-05 | 4 | 471 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses 7043 No. Fuses: 2 Fuse Amp Size: 8A TIME CLOSED: 09:36 Cause: Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)?No | .
4099 |  | JE24021179 | OKAIAWA | Western | OKAIAWA | 2024-06-16 | 12:18 | 2024-06-16 | 13:31 | 0.0038169 | 5.242e-05 | 19 | 1383 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | HV cross arm split, insulator almost falling out - Pole 718415 - Called in by Poltech. Line was isolated at ABS's MA453, 6440 & Links 12570/4 to replace damaged cross arm on pole 718415. | .
4100 |  | JE24021190 | WAOTU | Eastern | WAOTU | 2024-06-16 | 9:42 | 2024-06-16 | 10:50 | 0.00037883 | 5.5179e-06 | 2 | 137 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses FC4254 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 10:50 Cause: Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? No | .
4101 |  | JE24021195 | COROGLEN | Eastern | COROGLEN | 2024-06-16 | 10:01 | 2024-06-16 | 14:31 | 0.0014883 | 5.5179e-06 | 2 | 539 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: Transformer TC3449 No. Fuses: 2 Fuse Amp Size: 2A + Barrel TIME CLOSED: 14:30 Cause: Customer fault at the water pump Weather (wind/rain): Calm Follow up required (select advisory)? No Caused by Burnt out meter box at the customers water pump. Extra LV repairs, old porcelain fuses x 2 and safety disconnection for water pump A22082 | .
4102 |  | JE24021197 | KATERE 5 | Western | KATERE 5 | 2024-06-16 | 10:06 | 2024-06-16 | 11:46 | 0.0041136 | 4.1384e-05 | 15 | 1491 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: 8196 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 11:45 Cause: Lightning Weather (wind/rain): rain Follow up required (select advisory)?n | .
4103 |  | JE24021204 | BETHLEHEM | Eastern | BETHLEHEM | 2024-06-16 | 11:00 | 2024-06-16 | 12:08 | 0.11132 | 0.0016305 | 591 | 40348 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: Recloser 9483 Protection flags (nil where none): UV CAUSE: unknown Location: N/A Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): Follow up Required (select advisory)? Yes Additional fault restoration comments: Patrolled nothing found. Recloser may need a protection review. Also tripped last week on UV SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4104 |  | JE24021227 | SPRINGDALE | Eastern | SPRINGDALE | 2024-06-16 | 15:50 | 2024-06-16 | 17:04 | 0.00040506 | 5.5179e-06 | 2 | 147 | Unplanned | WILDLIFE - BIRD | Fuses Location: FC4233 No. Fuses: 2 Fuse Amp Size: 6 Amp TIME CLOSED: 17:03 Cause: Bird strike Weather (wind/rain): Calm Follow up required (select advisory)? No | .
4105 |  | JE24021235 | MANAIA | Western | MANAIA | 2024-06-16 | 18:50 | 2024-06-16 | 20:39 | 0.0015032 | 1.3795e-05 | 5 | 545 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faulty TFR M4255 Isolated at TFR M4255 Fuses Faulty TFR Replaced, new cable guard installed over LV cable going up pole, full power restored | .
4106 |  | JE24021238 | MATAROA A | Western | MATAROA A | 2024-06-16 | 19:02 | 2024-06-16 | 21:01 | 0.00065517 | 5.5179e-06 | 2 | 237 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: 2729 No. Fuses: 2 Fuse Amp Size: 2 TIME CLOSED: 21:00 Cause: unknown Weather (wind/rain): calm Follow up required (select advisory)?n | .
4107 |  | JE24018811 | 36 DAIRY FARM ROAD MASSEY UNIVERSITY | Western | RUAPEHU DR | 2024-06-15 | 9:00 | 2024-06-15 | 9:43 | 0.00035128 | 8.2769e-06 | 3 | 127 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Check phasing as S/W 10220/2 by closing S/W 25 so that DNO2305007 can be removed. FS15,FS15,FS139 not to be operated live, isolate at 10220/2 first. | .
4108 |  | JE24021089 | TAIRUA NORTH | Eastern | TAIRUA NORTH | 2024-06-15 | 0:33 | 2024-06-15 | 3:11 | 0.0013066 | 8.2769e-06 | 3 | 474 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Isolate HV Transformer TC6157 Fuses for safety to complete LV repairs on Cable Repair cable on red and blue phase | .
4109 |  | JE24021094 | WAIHI NORTH | Eastern | WAIHI NORTH | 2024-06-15 | 0:44 | 2024-06-15 | 6:10 | 0.15603 | 0.0018264 | 662 | 56554 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: CB 3 Protection flags (nil where none): A phase EF CAUSE: floating conductor Location: Pole 853591 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: cursory Weather (wind/rain): rain, windy LFI (Y/N + Comments): Y indicated correctly Follow up Required (select advisory)? Additional fault restoration comments: Replace cross arm SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4110 |  | JE24021095 | SPRINGVALE | Western | SPRINGVALE | 2024-06-15 | 2:00 | 2024-06-15 | 4:39 | 0.30999 | 0.0073802 | 1904 | 112358 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | REGULATORY INFORMATION Voltage & Device ID: 11kV, CB 9 Protection flags (nil where none): E/F, B phase CAUSE: Stick sitting on crossarm shorting lines Location: Pole 707692 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Yes / Cursory Weather (wind/rain): Heavy Rain LFI (Y/N + Comments): N/A Follow up Required (select advisory)? No Additional fault restoration comments: Branch removed from lines using Hot Stick SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4111 |  | JE24021097 | MANGATARATA | Eastern | MANGATARATA | 2024-06-15 | 5:47 | 2024-06-15 | 7:30 | 0.00056838 | 5.5179e-06 | 2 | 206 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses FP1117 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 07:30 Cause: Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)?No | .
4112 |  | JE24021099 | KEREONE | Eastern | KEREONE | 2024-06-15 | 6:19 | 2024-06-15 | 19:04 | 0.078535 | 0.0011036 | 326 | 28466 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: CB 6 Protection flags (nil where none): A & B phase EF CAUSE: Car V Pole Location: Poles 263704, 263705 & I12486 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Fire coms called in car v pole F3995327 Three HV Poles were replaced due to the Car vs Pole Full Power restored at 18:41 | .
4113 |  | JE24021116 | MANGATAINOKA | Western | MANGATAINOKA | 2024-06-15 | 14:00 | 2024-06-15 | 17:23 | 0.0039189 | 1.9313e-05 | 7 | 1420 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Burnt up cross arms at Pole P18288, due to broken insulators Isolated at Fuses R31 Cross Arms replaced, Full power restored | .
4114 |  | JE24021120 | OTAMARAKAU | Eastern | OTAMARAKAU | 2024-06-15 | 16:22 | 2024-06-15 | 16:45 | 0.00038156 | 1.6554e-05 | 6 | 138 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | No Fuses replaced -HV OPENED 16:22,CLOSED 16:45 to carry out LV REPAIRS. No fuses replaced LV repairs done replaced 4 x PG Clamps at pole 853934 | .
4115 |  | JE24021146 | DALMENY ST | Eastern | DALMENY ST | 2024-06-15 | 20:15 | 2024-06-15 | 21:26 | 0.0081616 | 0.00011588 | 42 | 2958 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Cause: Deterioration What was replaced? 1 x LV HRC Fuse ( 150 Amp) Where was it replaced (pole/TX/pillar box)? At G/M Transformer TC4310 Is 2R required? Yes 2R Y - What is the timeframe for repairs? Repaired on site. Additional Info: HV Switching was carried out to create safety panel to replace blown LV Fuse using LV Gloves. Back feed was closed at Sw/Gear 9652/2 via BRD4 HV Isolation at Sw/Gear 9598/3 & Sw/Gear IC3068 Only Transformer TC4310 was turned off during this outage. LV Fuse replaced and Full Power restored at 21:25 | .
4116 |  | JE24021162 | RANGITANUKU RD | Eastern | RANGITANUKU RD | 2024-06-15 | 22:59 | 2024-06-16 | 5:14 | 0.064183 | 0.00097116 | 352 | 23263 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC RC05 Protection flags (nil where none): E/F CAUSE: Transformer defective (Internal fault) Location: TC1662 (Pole F12985) Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Calm LFI (Y/N + Comments): Yes at Pole 498966 on B Ø (Worked 100%) Follow up Required (select advisory)? No Additional fault restoration comments: Field crew dispatched & asked to start line patrol & investigate LFI at Pole 498966 Field switcher opened ABS 2567 and confirmed LFI operated at Pole 498966 NOC closed in REC RC05 at 23:56 16/06/2024 Carry out line patrol from ABS 2567 to ABS 756 Field Switcher found 1 x HV Fuse blown at TX TC1662 ( B Ø ) Field staff proved the rest of the network to be fault free. Transformer TC1662 is defective, suspect internal fault. Busy arranging new transformer & traffic management to site. Field switcher is busy changing the faulty transformer under AP 1162-01 Repairs complete & full Power restored at 05:13 | .
4117 |  | JE24018541 | 1152 FITZHERBERT EAST ROAD AOKAUTERE PALMERSTON NORTH | Western | AOKAUTERE | 2024-06-14 | 9:30 | 2024-06-14 | 12:01 | 0.0033299 | 2.2072e-05 | 8 | 1207 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Reconductor LV Between 11kV Pole P35423 and P35418. | .
4118 |  | JE24018566 | 187 NGAMOTU ROAD SPOTSWOOD NEW PLYMOUTH | Western | NGAMOTU RD | 2024-06-14 | 9:31 | 2024-06-14 | 11:47 | 0.11279 | 0.00083045 | 301 | 40881 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replacement of arms on pole 748594 Red defect hot spot | .
4119 |  | JE24018682 | 120 GLOVER ROAD HAWERA HAWERA | Western | ARGYLE ST | 2024-06-14 | 9:00 | 2024-06-14 | 10:24 | 0.020155 | 0.00025382 | 92 | 7305 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Cut HV & LV line break at pole 441163 and join through LV conductor at pole 359616 for LV back feed. HV Line break to be used as isolation for future works, will be removed on NAPA 110227 9/7/24. | .
4120 |  | JE24020949 | WAIHI NORTH | Eastern | WAIHI NORTH | 2024-06-14 | 2:57 | 2024-06-14 | 12:48 | 0.0048928 | 8.2769e-06 | 3 | 1773 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: TX TC5030 No. Fuses: 2 Fuse Amp Size: 3 Amp TIME CLOSED: Failed closure at 07:30 Cause: Transformer TC5030 failed Weather (wind/rain): Heavy rain. Follow up required (select advisory)? No 07:30 - Reloaded and Closed TX TC5030 Fuses & 1 Fuse failed (blew back) Field switcher is busy investigating further into what the fault is. Confirmed Transformer TC5030 failed, suspect internal fault. Isolation: TX TC5030 Fuses CAUSE: Internal fault Pole: P13673 Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Heavy rain Follow up required (select advisory)? No Additional fault restoration comments: 08:23 - Field switcher is busy arranging a new Transformer to site & traffic management. Transformer was replaced under AP and Full Power restored at 12:48. | .
4121 |  | JE24020986 | KEENAN RD | Eastern | KEENAN RD | 2024-06-14 | 11:20 | 2024-06-14 | 12:34 | 0.0020587 | 2.759e-05 | 10 | 746 | Unplanned | VEGETATION - OUTSIDE ZONE | Fuses Location: Fuses SE3-085 No. Fuses: 2 Fuse Amp Size: 10 Amp TIME CLOSED: 12:34 Cause: Tree through HV Lines Weather (wind/rain): Rain & Windy Follow up required (select advisory)? No | .
4122 |  | JE24021000 | COROGLEN | Eastern | COROGLEN | 2024-06-14 | 12:42 | 2024-06-14 | 16:12 | 0.019704 | 9.3805e-05 | 34 | 7142 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 13588/2 Protection flags (nil where none): A & B Ø O/C CAUSE: Large pine tree fell over HV Lines. Location: Pole W1257 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Rain & wind. LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Feeder fault dispatched. During the line patrol field switcher came across large pine tree that fell over and brought down the HV Lines past Pole W1257 Repairs are being carried out under AP 1000-01 Full Power restored at 16:11 | .
4123 |  | JE24021001 | KAIMAI DRIVE | Eastern | KAIMAI DRIVE | 2024-06-14 | 14:20 | 2024-06-15 | 17:13 | 0.0028266 | 1.9313e-05 | 4 | 1025 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV Fuses SE2-012 Protection flags (nil when none): ARC upstream on REC 9275/2 CAUSE: Rain & windy conditions brought tree down Location: Pole 217 237 Temp generation (state details when used): Yes PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Rain & wind. Follow up required (select advisory)? Yes Additional fault restoration comments: Advised customer multiple times not to go near any lines. Tree brought down HV Lines, field switcher isolated at Fuses SE2-012 TLB at Pole 217 237 created and then TX TE2-011 was energized at 16:20 Busy connecting a Generator to Transformer TE2-033 Generator in service at: 17:30 15/06: Poles replaced and conductors re strung. Generator removed 16:07, Normal power restored 17:13 | .
4124 |  | JE24021002 | TAUMANGI RD | Eastern | TAUMANGI RD | 2024-06-14 | 12:51 | 2024-06-14 | 14:52 | 0.0082071 | 0.00011036 | 40 | 2975 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | REGULATORY INFORMATION Voltage & Device ID: 11KV SECTIONALISER 9941, Rec 1459 A/R Protection flags (nil where none): A & B PHASEOC CAUSE: TREE BRANCH Location: POLE M2466 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): WIND 77 RAIN LFI (Y/N + Comments): YES BUT VIA SITE TELEMETERING NOT WORING, LFI JUST PAST ABS 883 Follow up Required (select advisory)? No Additional fault restoration comments: | .
4125 |  | JE24021011 | PYES PA | Eastern | PYES PA | 2024-06-14 | 13:45 | 2024-06-14 | 19:25 | 0.05984 | 0.00023727 | 73 | 21689 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV SEC 13578/2 Protection flags (nil where none): A B C Ø O/C & E/F CAUSE: Strong winds and rain. Location: Pole 217 036 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Rain LFI (Y/N + Comments): No Follow up Required (select advisory)? Yes Additional fault restoration comments: 14:52 - Field Switcher on site to start with the line patrol, heavy rain at the moment, very rural area. Advised field switcher of the protection operated. 15:25 - Field switcher was busy with his line patrol when he came across the HV Conductors that had come down from Pole 217 036 (All three phases) across a flooded gully. Isolation was carried out at ABS TEMP022 28 Transformers have No Power 17:12 - AP 1011-01 taken to carry out the repairs. | .
4126 |  | JE24021014 | RIVERSDALE GEN | Western | RIVERSDALE GEN | 2024-06-14 | 14:04 | 2024-06-14 | 21:03 | 0.077543 | 0.00031176 | 81 | 28106 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec C281/2 Protection flags (nil where none): E/F CAUSE: Jumper from Tfr fuses sitting on crossarm Location: Pole 945548 / Tfr T146 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): NO Circuit patrolled and type: cursory Weather (wind/rain): windy, heavy rain LFI (Y/N + Comments): installed but did not operate Follow up Required (select advisory)? Additional fault restoration comments: | .
4127 |  | JE24021032 | HORAHORA | Eastern | HORAHORA | 2024-06-14 | 14:57 | 2024-06-14 | 15:55 | 0.01024 | 0.00017657 | 64 | 3711 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 11kV sectionaliser 14299 opened for safety 14:57, restored 15:55 15:00 - Rung Downer Hub To advise that controller has dropped feeder 400V fuses for TC386 removed due to broken LV cross arm causing lines to hang low Replace 2 x cross arms at Pole M0379 | .
4128 |  | JE24021069 | CHURCH ST | Western | CHURCH ST | 2024-06-14 | 19:18 | 2024-06-14 | 19:27 | 0.0016247 | 0.0002014 | 73 | 589 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Repair jumper at Tfr T1410 - isolation at TX fuses | .
4129 |  | JE24021077 | WESTMERE GLADSTONE | Western | WESTMERE GLADSTONE | 2024-06-14 | 18:23 | 2024-06-14 | 23:15 | 0.057932 | 0.00025107 | 91 | 20998 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: REC 7417 Protection flags (nil where none): A / B phase OC CAUSE: Unknown Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: cursory Weather (wind/rain): windy and raining LFI (Y/N + Comments): yes, indicated past ABS S323 Follow up Required (select advisory)? Additional fault restoration comments: | .
4130 |  | JE24021082 | MANGATAINOKA | Western | MANGATAINOKA | 2024-06-14 | 19:19 | 2024-06-14 | 22:31 | 0.058365 | 0.00094632 | 232 | 21155 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV, Rec R12 Protection flags (nil where none): E/F CAUSE: Unk Location: Unk Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Yes / Cursory Weather (wind/rain): Heavy Rain LFI (Y/N + Comments): Yes. Pole P26697 indicated correctly Follow up Required (select advisory)? No Additional fault restoration comments: No fault found SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4131 |  | JE24017467 | 14 KAWAU ROAD TAIHAPE TAIHAPE | Western | TAIHAPE TOWN SOUTH | 2024-06-13 | 9:31 | 2024-06-13 | 15:13 | 0.00094499 | 2.759e-06 | 1 | 343 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 2 pole structure 789531 & 789532.Using Digger. | .
4132 |  | JE24018148 | 123 WHAKAMARAMA ROAD WHAKAMARAMA | Eastern | WHAKAMARAMA | 2024-06-13 | 9:01 | 2024-06-13 | 14:33 | 0.0045796 | 1.3795e-05 | 5 | 1660 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace TX and Fly arms on pole 259958 | .
4133 |  | JE24018154 | 26 TIRAU STREET PUTARURU PUTARURU | Eastern | BENT ST | 2024-06-13 | 22:00 | 2024-06-14 | 2:20 | 0.049518 | 0.00019037 | 69 | 17948 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance IC1579-IC2039-IC1594-IC1590-FC5036. Found Sw/Gear Leaking oil & Bus Bar Insulation has Deteriorated badly. DNO 2406007 Raised | .
4134 |  | JE24018158 | 92 Tawhari Street Matamata | Eastern | RAWHITI AVE | 2024-06-13 | 8:52 | 2024-06-13 | 13:28 | 0.02515 | 9.1046e-05 | 33 | 9116 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace burnt LV Frame in Transformer TC3943 | .
4135 |  | JE24018166 | Cnr Napier Road & Main Street, Palmerston North | Western | MAIN ST 11 | 2024-06-13 | 8:30 | 2024-06-13 | 16:10 | 0.13313 | 0.00028969 | 105 | 48253 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace G134/A/B/C/T with CFCC 10889 | .
4136 |  | JE24018271 | 214 WOODLAND ROAD TAHAWAI | Eastern | LINDERMANN RD | 2024-06-13 | 8:59 | 2024-06-13 | 15:27 | 0.048178 | 0.00012415 | 45 | 17462 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv/400vt poles 204392 ,204393 ,204397 ,204398 & 204399: Isolation 11kV ABS SB1-025. Note: Fuses SB1-025 replaced with ABS SB1-025 in previous shut under NAPA 110408 11/06/2024. | .
4137 |  | JE24018289 | 18 PLYMOUTH ROAD OMATA NEW PLYMOUTH | Western | PIONEER RD | 2024-06-13 | 9:45 | 2024-06-13 | 12:06 | 0.0034908 | 2.4831e-05 | 9 | 1265 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Safety isolation of TX 607 to replace deteriorated LV arms on pole 756362 | .
4138 |  | JE24018291 | 1080 FITZHERBERT EAST ROAD AOKAUTERE PALMERSTON NORTH | Western | AOKAUTERE | 2024-06-13 | 9:31 | 2024-06-13 | 13:23 | 0.0051333 | 2.2072e-05 | 8 | 1861 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | reconductor lv between pole 367060 and P35429 | .
4139 |  | JE24018299 | 380 MOUNT STEWART HALCOMBE ROAD HALCOMBE PALMERSTON NORTH | Western | MT STEWART | 2024-06-13 | 9:16 | 2024-06-13 | 12:29 | 0.028723 | 0.00014898 | 54 | 10411 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace defected HV crossarms on 11kV Poles P21724 to P21728, P21743. Replace rusty 11kV Transformer T3/506. | .
4140 |  | JE24019826 | 50 CARDIFF ROAD CARDIFF STRATFORD | Western | CLOTON RD NORTH | 2024-06-13 | 10:05 | 2024-06-13 | 17:15 | 0.077143 | 0.00017933 | 65 | 27961 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace new 33kv recloser switch 3545 | .
4141 |  | JE24020824 | MANGOREWA | Eastern | MANGOREWA | 2024-06-13 | 6:54 | 2024-06-13 | 7:47 | 0.00086397 | 2.4831e-05 | 9 | 313 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | 1x blown fuse at SE6-053 - re-loaded and closed at 07:08. Additional isolation done at Fuse/Sw SE6-171, SE6-169, SE6-173, SE6-152 for patrol - no fault found. Fuses Location: SE6-053 No. Fuses: 1 Fuse Amp Size: 25 Amp TIME CLOSED: 07:08 Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)? No Older network with Overhead & Cable including Link Boxes. Line Patrol was carried out and nothing abnormal was found. Full Power restored at 07:46 | .
4142 |  | JE24020864 | PUTORINO | Western | PUTORINO | 2024-06-13 | 11:11 | 2024-06-13 | 13:34 | 0.0071159 | 4.9661e-05 | 18 | 2579 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 628 No. Fuses: 2 Fuse Amp Size: `5 TIME CLOSED: 13:33 Cause: no fault found Weather (wind/rain): Follow up required (select advisory)? Please check JE24020865 on Completion | .
4143 |  | JE24020885 | BROOKLANDS 7 | Western | BROOKLANDS 7 | 2024-06-13 | 13:37 | 2024-06-13 | 19:34 | 0.19503 | 0.0059345 | 2151 | 70690 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 7 Protection flags (nil where none): A Phase E/F CAUSE: Truck Vs Pole Location: SH 3/ Hydro Rd Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Rain LFI (Y/N + Comments): Nil Follow up Required (select advisory)? no Additional fault restoration comments: Updated to Emergency. Informed SMC Fire, Police and Ambulance are attending. ETA 15-20mins - FComms have been advised During fault Brooklands CB 7 tripped and was supplying the whole of Brooklands CB 6 (for planned maintenance) Upon faultman getting to site isolation down to Fuses 8252 to repair lines and change pole if required | .
4144 |  | JE24020939 | WAITOTARA | Western | WAITOTARA | 2024-06-13 | 19:31 | 2024-06-13 | 22:03 | 0.024312 | 0.00016002 | 58 | 8812 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Isolate at ABS 1372 to repair line down at Pole 841742. Unknown why lines were down. Not related to the fault but Ben also identified that there are trees overhanging the lines in this area. He has taken photos and will defect next tomorrow. | .
4145 |  | JE24020947 | TUTAENUI | Western | TUTAENUI | 2024-06-13 | 23:53 | 2024-06-14 | 12:45 | 0.1116 | 0.0014678 | 215 | 40451 | Unplanned | THIRD PARTY INTERFERENCE - OVERHEAD CONTACT | REGULATORY INFORMATION Voltage & Device ID: REC 4566 Protection flags (nil where none): EF CAUSE: REDUNDANT TELECOM WIRE SNAPPED AND WENT ACROSS HV LINES Location: POLEs 802911 & 802900 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Rain LFI (Y/N + Comments): LFI's lit at Fuses 645 Follow up Required (select advisory)? No Additional fault restoration comments: TRANSFORMER X2025 LEFT WITH FUSES OPEN REMOVED AND TAGGED, BAD STATE AND REDUNDANT FAULTMAN TO DEFECT NDR being completed for telco lines | .
4146 |  | JE24017278 | 44 SUFFOLK ROAD SOUTH NORFOLK INGLEWOOD | Western | KAIMATA | 2024-06-12 | 9:01 | 2024-06-12 | 14:26 | 0.021414 | 6.6215e-05 | 24 | 7762 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove ABS 5382 from pole 761406, re-use existing termination crossarms, add new HV insulators and sleeve conductors back together. Replace pole 761407 and install new recloser/links/TX/ABS structure. Recloser ID 12690 | .
4147 |  | JE24017886 | 78 MORIKAU ROAD RANANA WANGANUI | Western | RAETIHI | 2024-06-12 | 9:46 | 2024-06-12 | 11:26 | 0.0044158 | 4.4143e-05 | 16 | 1601 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Dismantle transformer site X1684 as no longer required. | .
4148 |  | JE24018116 | 1256 STATE HIGHWAY 3 MARTON MARTON | Western | LAKE ALICE | 2024-06-12 | 9:28 | 2024-06-12 | 14:36 | 0.027175 | 8.8287e-05 | 32 | 9850 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace multiple defected 6.6KV poles & X-arms past 6.6KV Fuses 973 between poles 806271 & 806304 | .
4149 |  | JE24018119 | 296 CAMBRIDGE ROAD BETHLEHEM TAURANGA | Eastern | BETHLEHEM | 2024-06-12 | 8:30 | 2024-06-12 | 16:16 | 0.12071 | 0.00025934 | 94 | 43751 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace 11kV cable, and liven new section of 33kV cable and OH. Remove existing 33kV OH line. | .
4150 |  | JE24018121 | 41 AKURA ROAD MASTERTON MASTERTON | Western | HOPE ST | 2024-06-12 | 23:00 | 2024-06-13 | 0:04 | 0.029286 | 0.00046351 | 168 | 10615 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install Temp Links 144 and 150 at pole 831377 on Coradine and Hope st feeders | .
4151 |  | JE24018124 | 11 STOKES ROAD TAHAWAI | Eastern | LINDERMANN RD | 2024-06-12 | 9:01 | 2024-06-12 | 16:05 | 0.017573 | 4.1384e-05 | 15 | 6370 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Pole 204467 | .
4152 |  | JE24018125 | 36 TAUPO STREET PUTARURU PUTARURU | Eastern | KENNEDY DRIVE | 2024-06-12 | 23:01 | 2024-06-13 | 1:26 | 0.00040019 | 2.759e-06 | 1 | 145 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance 9401-1/2/3 | .
4153 |  | JE24018127 | 848 JUNCTION ROAD MATAU STRATFORD | Western | HUIROA | 2024-06-12 | 9:01 | 2024-06-12 | 13:30 | 0.0081921 | 3.0349e-05 | 11 | 2969 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | asplundh to remove trees from between poles 709376 to 709383 | .
4154 |  | JE24018136 | 3 SEABREEZE PLACE PAPAMOA BEACH TAURANGA | Eastern | GLOUCESTER RD | 2024-06-12 | 8:33 | 2024-06-12 | 15:25 | 0.092188 | 0.00022348 | 81 | 33414 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re-level SD 9090 to help remedy oil leak (high oil level) and minor corrosion repairs. | .
4155 |  | JE24018138 | 922 BEACONSFIELD ROAD STRATFORD STRATFORD | Western | CLOTON RD SOUTH | 2024-06-12 | 9:31 | 2024-06-12 | 13:35 | 0.0047113 | 1.9313e-05 | 7 | 1708 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | extend hv lines and move insulator to correct postion at pole 740514. replace hv xarm at pole 740515 | .
4156 |  | JE24018139 | 6 Owahanga Road PONGAROA PONGAROA | Western | COAST ROAD | 2024-06-12 | 8:50 | 2024-06-12 | 12:17 | 0.0074136 | 3.5867e-05 | 13 | 2687 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Coast Road FFT - Akitio outage 4/4 - Remedial work on P04503 & P04510; resag lines between P04455-P04493 replace xarms P04521 | .
4157 |  | JE24018145 | 541 KAPOWAI ROAD COROGLEN WHITIANGA | Eastern | COROGLEN | 2024-06-12 | 9:15 | 2024-06-12 | 17:13 | 0.0092199 | 1.9313e-05 | 7 | 3342 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 66/11kV pole W1341. | .
4158 |  | JE24020442 | 45A HEATH ROAD WAIHI WAIHI | Eastern | WAIHI-WHANGAMATA 33KV | 2024-06-12 | 7:02 | 2024-06-12 | 16:54 | 3.164 | 0.007085 | 2543 | 1146821 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles WHIWGH004 , R12367 ( 13079 ) , R12368 , New pole 14 between poles WHIWGM121 & WHIWHG122 , WHIWGM132 , WHIWGM133. Raise 11kV fuses and transformer on poles R13096 ( TC987 ) & WHIWGM140 ( TP2125 ) . Temp generation installed on TC4848 - Outside work area . | .
4159 |  | JE24020671 | WAITOTARA | Western | WAITOTARA | 2024-06-12 | 9:30 | 2024-06-12 | 11:09 | 0.0035346 | 3.5867e-05 | 13 | 1281 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: Line Clash in strong wind Location: Pole 781344-781345 Isolation: Fuses 684 What was replaced? 4x cu. sleeves, 8mtrs 16mm cu. conductor & HV fuse link Where was it replaced (pole/TX/pillar box)? Pole 781345 Is 2R required? Yes 2R Y - What is the timeframe for repairs? Completed Additional Info: FM found blown HV fuse due to HV line down Weather: Windy / Heavy Rain | .
4160 |  | JE24020751 | MOTUMAOHO | Eastern | MOTUMAOHO | 2024-06-12 | 13:19 | 2024-06-12 | 15:41 | 0.00039277 | 2.759e-06 | 1 | 142 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: dtx No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 15:41 Cause: deterioration Weather (wind/rain): calm Follow up required (select advisory)? | .
4161 |  | JE24020771 | WEST TOWN | Western | WEST TOWN | 2024-06-12 | 14:52 | 2024-06-12 | 20:33 | 0.16517 | 0.0055207 | 2001 | 59867 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 21 Protection flags (nil where none): A,B O/C, E/F CAUSE: Hit Pole Location: Pole P37626 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: Cursory Weather (wind/rain): Fine LFI (Y/N + Comments): Yes Sw/Gear 10232/3 & 4 Follow up Required (select advisory)? No Additional fault restoration comments: | .
4162 |  | JE24020788 | 147B PUKETUTU ROAD, MATAMATA, 3472 | Eastern | FIRTH ST | 2024-06-12 | 17:17 | 2024-06-12 | 17:55 | 0.00053685 | 1.3795e-05 | 5 | 195 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: Fuses FP1719 CAUSE: Deterioration Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Calm Follow up required (select advisory)? No Additional fault restoration comments: Stay-wire was found broken at Transformer TC3489 Repairs carried out and full Power restored at 17:55 | .
4163 |  | JE24017976 | 22 PRINCES STREET PUTARURU PUTARURU | Eastern | BENT ST | 2024-06-11 | 23:30 | 2024-06-12 | 0:15 | 0.0018623 | 4.1384e-05 | 15 | 675 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance IC2035-FC5021-IC1571 When the power went off the traffic lights, railway crossing and signal lights also went off and during the time to setup and was noted that two loaded trains went through the crossing, as a result Electrix contacted NOC and asked what should be done as this was unsafe for the public, the instruction was given to abort the shut as the traffic management did not have the correct signage for the railway crossing. A generator should be provided for the duration of the shut. | .
4164 |  | JE24017984 | 522 PAKARAKA ROAD TAPAPA TIRAU | Eastern | RANGITANUKU RD | 2024-06-11 | 8:53 | 2024-06-11 | 9:16 | 0.00032234 | 1.3795e-05 | 5 | 117 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To carry out SWER earth tests on transformer TC2759 | .
4165 |  | JE24017987 | 22 NURSERY ROAD HOMEBUSH MASTERTON | Western | CHURCH ST | 2024-06-11 | 8:46 | 2024-06-11 | 13:37 | 0.018484 | 6.3456e-05 | 23 | 6700 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Repair defects past fuses 7046 | .
4166 |  | JE24018076 | 371A Matai Road, Matamata | Eastern | STATION RD | 2024-06-11 | 9:16 | 2024-06-11 | 14:27 | 0.0249 | 8.001e-05 | 29 | 9025 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace HV Cross Arms at Poles G0049 and Pole G0098 During restoration switching, Rec 9664 tripped on close, no alarms. See related job raised for tech. No additional outage to ICPs as backfeed was still in place - left backfed until rec checked | .
4167 |  | JE24018083 | 2497 COAST ROAD PONGAROA PONGAROA | Western | COAST ROAD | 2024-06-11 | 8:30 | 2024-06-11 | 14:30 | 0.12105 | 0.00033659 | 122 | 43874 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Coast Road FFT - Akitio outage 3/4 - Execute pole straightening and cross arm changes -P04628,P26827 & 446370 Cross arm replacement P01102 & P04432 also straighten. | .
4168 |  | JE24018090 | 24 KEEPA AVENUE PAEROA PAEROA | Eastern | SHAW AVE | 2024-06-11 | 9:10 | 2024-06-11 | 12:33 | 0.0011233 | 5.5179e-06 | 2 | 407 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Shut down TC5154 to disconnect & remove from foundation. Remove nearby tree & roots in ground to level foundation for TC 5154. Re-install TC5154, re-connect & test. Generator to be connected to notable customer service switchboard main switch. Sw/Gear labeled different on site to SCADA, Required 1min outage to DTX TC2929 to identify Correct Transformer, SCADA was wrong & Corrected, Jerry Photo's Sent RRB | .
4169 |  | JE24018096 | 1529 TINUI VALLEY ROAD TINUI VALLEY TINUI | Western | CASTLEPOINT | 2024-06-11 | 9:21 | 2024-06-11 | 14:50 | 0.0072579 | 2.2072e-05 | 8 | 2631 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Vegetation cutting between poles 837914 and 837915 | .
4170 |  | JE24018106 | 194 WOODLAND ROAD TAHAWAI | Eastern | MURAL TOWN | 2024-06-11 | 8:46 | 2024-06-11 | 15:21 | 0.10676 | 0.00027038 | 98 | 38696 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv/400vt poles 204363,204364,204390 267850. Replace Fuses SB1-025 with ABS. HV Recon Run 1 204362 â€“ 380368: isolation point 14598/4 , ABS 66 & ABS 1049. | .
4171 |  | JE24018117 | 600 HALCOMBE ROAD HALCOMBE FEILDING | Western | MT STEWART | 2024-06-11 | 9:31 | 2024-06-11 | 12:27 | 0.010663 | 6.0697e-05 | 22 | 3865 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replacing HV arm on Multiple structures | .
4172 |  | JE24020522 | DYERVILLE | Western | DYERVILLE | 2024-06-11 | 1:11 | 2024-06-11 | 16:01 | 0.052673 | 0.00029245 | 66 | 19092 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: Recloser 8179 Protection flags (nil where none): EF Phase C OC CAUSE: Broken wooden pole Location: Pole 811365 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Isolated at Fuses 8158 Line break made at Pole 811366, Pole to be replaced later today Isolation at Line break at Pole 811366, Pole 811365 was replaced, Isolated at Fuses 8158 Line break at pole 811366 closed, full power restored | .
4173 |  | JE24020523 | DUTHIE RD | Western | DUTHIE RD | 2024-06-11 | 3:26 | 2024-06-11 | 6:05 | 0.056313 | 0.0012333 | 299 | 20411 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 2 Protection flags (nil where none): A & C ph E/F CAUSE: Line Down - due to joint failure Location: 731752 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: Cursory Weather (wind/rain): calm LFI (Y/N + Comments): N Follow up Required (select advisory)? n Additional fault restoration comments: Line was isolated at ABS's 5972 & 6008 to repair line down. | .
4174 |  | JE24020535 | TE MAUNGA | Eastern | TE MAUNGA | 2024-06-11 | 8:03 | 2024-06-11 | 8:10 | 0.025293 | 0.0044474 | 1612 | 9168 | Unplanned | HUMAN ERROR - POTENTIAL SWITCHING ERROR | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 37,38,1,3,5,7 Protection flags (nil where none): CB 7 A,B,C E/F CB 7 Fast Bus, CB 37 Fast Bus CAUSE: Human Error E/S 9569/3 Closed onto Live CB 7 Circuit SIS 111264 Item 3 Closed E/S 3 rather than Sw/ 3 Location: Sw/G 9569/3 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): half bus outage to Matapihi sub Circuit that tripped: DTF (KM): Part of NAPA 111264 | .
4175 |  | JE24020570 | 910 SKEET ROAD, KAPUNI, HAWERA, 4675 | Western | MATAPU | 2024-06-11 | 11:07 | 2024-06-11 | 12:25 | 0.0099119 | 0.00012691 | 46 | 3593 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Pole 461128 badly damaged jumper only a few strands left Emergency shut down isolated between ABS 6713 & ABS KA749 to replace jumper | .
4176 |  | JE24020585 | TOTMANS RD | Eastern | TOTMANS RD | 2024-06-11 | 11:44 | 2024-06-11 | 18:03 | 0.015241 | 0.0004166 | 151 | 5524 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Pole 389 317 hit , new pole # is 440889 Truck hit lines , de-energised for safety De-energised recloser 13260 to recloser 13085 When faultman on site isolation was reduced to Fuses FP1559 Main line restored 12:16 , Fuses FP1559 restored for final restoration 18:03 | .
4177 |  | JE24020591 | MANAWAPOU RD | Western | MANAWAPOU RD | 2024-06-11 | 12:38 | 2024-06-11 | 12:59 | 0.0052097 | 0.00025934 | 94 | 1888 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: high winds What was replaced? 1 x 63 A fuse and holder. Where was it replaced (pole/TX/pillar box)? pole Is 2R required? Y 2R Y - What is the timeframe for repairs? Additional Info: Arcing and low lines reported, isolation from Sw/G 12746/2 to check for safety. | .
4178 |  | JE24020607 | OTAMARAKAU | Eastern | OTAMARAKAU | 2024-06-11 | 12:54 | 2024-06-11 | 15:30 | 0.002579 | 1.6554e-05 | 6 | 935 | Unplanned | WILDLIFE - BIRD | Fuses Location: DTX No. Fuses: 3 & 3 x Barrels also 3 x 100A LV Fuses Replaced Fuse Amp Size: 3 TIME CLOSED: 15:30 Cause: Line Clash Bird strike Weather (wind/rain): Calm Follow up required (select advisory)? | .
4179 |  | JE24020659 | COROGLEN | Eastern | COROGLEN | 2024-06-11 | 18:51 | 2024-06-11 | 20:07 | 0.0092391 | 0.00012139 | 44 | 3349 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV Sec 13199/2 Protection flags (nil where none): E/F CAUSE: Bamboo touching lines Location: TC3996 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4, cursory patrolled. Weather (wind/rain): Calm LFI (Y/N + Comments): None installed Follow up Required (select advisory)? Yes, Trees need trimming. Additional fault restoration comments: Bamboo removed with Hot Stick from lines, no damage caused. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4180 |  | JE24020660 | WAITOTARA | Western | WAITOTARA | 2024-06-11 | 20:24 | 2024-06-11 | 22:00 | 0.0034528 | 3.5867e-05 | 13 | 1251 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faultman found line down at pole 781344, line was isolated at Fuses 684 to repair line, cause was due to deuteriation at pin arm. Weather: calm & light rain | .
4181 |  | JE24017508 | 1673 HINEKURA ROAD HINAKURA MARTINBOROUGH | Western | COLOGNE ST | 2024-06-10 | 10:00 | 2024-06-10 | 12:11 | 0.023158 | 0.00017657 | 64 | 8394 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace cross arms on h pole 816718 | .
4182 |  | JE24017763 | 977 FITZHERBERT EAST ROAD AOKAUTERE PALMERSTON NORTH | Western | AOKAUTERE | 2024-06-10 | 9:46 | 2024-06-10 | 13:36 | 0.0050691 | 2.2072e-05 | 8 | 1837 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Reconductor lv between P34773 and P35447 | .
4183 |  | JE24017892 | 66 TE HOUHOU ROAD HUNTERVILLE MARTON | Western | PUTORINO | 2024-06-10 | 9:11 | 2024-06-10 | 14:05 | 0.021117 | 7.1733e-05 | 26 | 7654 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | SCANPOWER to replace pole 805655 and replace bolts on pole 805651. DOWNER to replace all crossarms on pole 805613 & TX X1837. Replace all crossarms on pole 805600 & TX X2270. | .
4184 |  | JE24017913 | 68 POWNALL STREET MASTERTON MASTERTON | Western | CORNWALL ST | 2024-06-10 | 23:00 | 2024-06-11 | 2:38 | 0.35491 | 0.0016278 | 590 | 128640 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install new ABS 11464 at pole 842181 for future work | .
4185 |  | JE24017915 | 112 PAHOIA ROAD WHAKAMARAMA TAURANGA | Eastern | PAHOIA | 2024-06-10 | 9:03 | 2024-06-10 | 12:33 | 0.06955 | 0.00033108 | 120 | 25209 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv x-arms on pole 207981 & 209007 "pole top photography" | .
4186 |  | JE24017962 | 45 RIVER ROAD PAEROA PAEROA | Eastern | TIROHIA-KARANGAHAKE | 2024-06-10 | 9:16 | 2024-06-10 | 16:11 | 0.099708 | 0.00024003 | 87 | 36140 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Draw rope with drone between poles 859952 & N1778 / WKOPAO045. Re-instate pole N2929. | .
4187 |  | JE24020310 | OTAKEHO | Western | OTAKEHO | 2024-06-10 | 9:15 | 2024-06-10 | 11:21 | 0.0066015 | 5.242e-05 | 19 | 2393 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Fuses Location: MA574 No. Fuses: 3 Fuse Amp Size: TIME CLOSED: 11:20 Cause: Blown Jumper at pole 718390, all three jumpers replaced Other defects on pole fixed during outage - see SIS for details Weather (wind/rain): Follow up required (select advisory)? | .
4188 |  | JE24020336 | TE KIRI | Western | TE KIRI | 2024-06-10 | 10:54 | 2024-06-10 | 12:29 | 0.0013038 | 1.3795e-05 | 5 | 473 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | LV lines down 1 HV fuse found blown on arrival 11kV Fuses transformer T7325 isolated 10:54, restored 12:28 LV Lines down at Pole # 714462 | .
4189 |  | JE24020350 | WAIMAPU | Eastern | WAIMAPU | 2024-06-10 | 8:43 | 2024-06-10 | 22:05 | 0.24489 | 0.0022403 | 669 | 88763 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 1 // Rec 9182 Protection flags (nil where none): O/C // O/C E/F CAUSE: Car V Pole Location: Pole 481273 & 211002 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F3/F4, around the accident scene Weather (wind/rain): Raining LFI (Y/N + Comments): Yes activated Follow up Required (select advisory)? No Additional fault restoration comments: Car V pole & transformer TE4-168. Temp line break cut at pole 386145 to limit SAIDI. Pole 386145 and 481273 replaced including Transformer TE4-168 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): No Circuit that tripped: N/A DTF (KM): N/A | .
4190 |  | JE24020353 | WORKS | Western | WORKS | 2024-06-10 | 9:12 | 2024-06-10 | 11:50 | 0.04737 | 0.00030073 | 109 | 17169 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: Pole 32395 11kV Lead off 11kV cable connection Protection flags (nil where none): nil CAUSE: Deterioration Location: Pole 32395 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Photo's included Additional fault restoration comments: | .
4191 |  | JE24020387 | MAIN RD MOTONUI | Western | MAIN RD MOTONUI | 2024-06-10 | 10:07 | 2024-06-10 | 12:49 | 0.0004449 | 2.759e-06 | 1 | 161 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 11kV Fuses 3416T 2x 2A Fuses replaced 12:48 Re-terminated cable found faulted | .
4192 |  | JE24020389 | MOUNTAIN | Eastern | MOUNTAIN | 2024-06-10 | 10:14 | 2024-06-10 | 11:35 | 0.00090224 | 1.1036e-05 | 4 | 327 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses FC2132 (NOT Tx TC3230 Fuses - Job Would not Push Up To Spur Line Fuses FC2132) No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 11:35 Cause: Suspected to be Wind Related Weather (wind/rain): Wind & Rain Follow up required (select advisory)? | .
4193 |  | JE24020423 | TE PUNA | Eastern | TE PUNA | 2024-06-10 | 12:04 | 2024-06-10 | 16:07 | 0.0060243 | 2.4831e-05 | 9 | 2184 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | HV fuses FP1963 opened for safety due to report of fire at 12:04. Found 400V termination on the LV panel blown. Termination was repaired and 2 x 250A HRC fuses replaced. Fuses FP1963 closed at 16:06 | .
4194 |  | JE24020458 | TAWHITI RD | Western | TAWHITI RD | 2024-06-10 | 15:55 | 2024-06-10 | 17:51 | 0.004784 | 4.1384e-05 | 15 | 1734 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Transformer C6610 replaced due to not being safe to leave in service as per hazard. Isolation at 11kV line fuses CA407 Power off 15:55 power restored 17:50 | .
4195 |  | JE24017792 | 41 MALEME STREET GREERTON TAURANGA | Eastern | MALEME EXPRESS | 2024-06-09 | 8:31 | 2024-06-09 | 16:53 | 0.07215 | 0.00033935 | 85 | 26151 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | DNO - To replace pole 216417 with double 11m concrete busck, replace BS SD4-310 and remove temporary inline links TEMP60 on Pole 216421 via liveline process GB-40 | .
4196 |  | JE24020232 | TIROHIA-KARANGAHAKE | Eastern | TIROHIA-KARANGAHAKE | 2024-06-09 | 1:48 | 2024-06-09 | 3:04 | 0.088338 | 0.0011698 | 424 | 32018 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | REGULATORY INFORMATION Voltage & Device ID: 11kV POA CB3 Protection flags (nil where none): A & B Ø O/C + Ground Fault CAUSE: Unknown (Inside large paddock) Location: Poles N13217 & 33/11kV WKOPAO 075 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Calm LFI (Y/N + Comments): Yes, at Pole 876695 on B Ø (LFI cleared after repairing twisted conductors) Follow up Required (select advisory)? No Additional fault restoration comments: 33kV WAIKINO 2212 - PAEROA auto reclosed at 01:48 (TPWR called NOC) Field Switcher to start the Line Patrol from POA S/S CB3 towards REC RC33 and ABS IC505. (Investigate LFI's at Pole 876695) Upon Inspection HV Conductors were found twisted together one span from HV Cable outside POA S/S Between Poles N13217 & 33/11kV WKOPAO 075 This was undone using a hot stick from ground level. NOC then restored network by closing in POA CB3 at 03:03 and then closing in REC RC33 at 03:04. REC 9420 failed to close via remote and the field staff could not gain access as the gate was locked - Tirohia Landfill 09/06/24 - Access gained and trip flags reset, Rec 9420 closed. | .
4197 |  | JE24020234 | 4A CAMERON ROAD, TE PUKE, 3119 | Eastern | MANOEKA RD | 2024-06-09 | 10:35 | 2024-06-09 | 15:59 | 0.12364 | 0.00038074 | 138 | 44816 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 4 Protection flags (nil where none): Nil CAUSE: Car V pole Location: Pole 222801 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Either side of pole 222801 Weather (wind/rain): Overcast LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Called in by Firecomms F3991373 Isolation from ABS SE5-274 to Sw/Gear 9444/3 1 x 11m pole replaced 1 x HV pin arm complete assembly 1 x LV double pin arm complete assembly NDR to follow SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4198 |  | JE24020250 | TGA Sub - CB 19 - Recloser 9483 | Eastern | BETHLEHEM | 2024-06-09 | 11:51 | 2024-06-09 | 13:53 | 0.17022 | 0.0016305 | 591 | 61696 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 9483/2 Protection flags (nil where none): Nil CAUSE: Unknown lines patrolled. Location: Unknown Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F3, Cursory patrolled Weather (wind/rain): Overcast LFI (Y/N + Comments): fitted none flagged Follow up Required (select advisory)? No Additional fault restoration comments: Lines patrolled from Rec 9483/2 to end, no fault cause could be found. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4199 |  | JE24020255 | WELCOME BAY | Eastern | WELCOME BAY | 2024-06-09 | 13:51 | 2024-06-09 | 14:23 | 0.13494 | 0.004395 | 1593 | 48910 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 3 Protection flags (nil where none): Nil CAUSE: Bird contact Location: Pole 215257 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: No, reported by member of the public. Weather (wind/rain): Overcast LFI (Y/N + Comments): Follow up Required (select advisory)? No Additional fault restoration comments: Bird removed from pole with Hot Sticks, no visible damage caused. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4200 |  | JE24020262 | 187 LEVERS ROAD, MATUA, TAURANGA, 3110 | Eastern | MATUA POINT | 2024-06-09 | 17:07 | 2024-06-10 | 1:20 | 0.09779 | 0.00019865 | 72 | 35444 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: CB 1 Protection flags (nil where none): None CAUSE: Car v Pole Location: Pole 202200 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Pole 202200 replaced Power on 01:24Hrs. 2 services off pole 202200 will be connected in the morning. Fatigue on the crew SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4201 |  | JE24020265 | WAIPUNA | Eastern | WAIPUNA | 2024-06-09 | 16:55 | 2024-06-09 | 18:04 | 0.063416 | 0.00091598 | 332 | 22985 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV Sec 9678/2, CB 1 A/R Protection flags (nil when none): O/C CAUSE: Tree branch on lines Location: Pole 481332 Temp generation (state details when used): NO PERFORMANCE DETAIL DNO (number or state no): N/A Circuit patrolled & type: F4, Yes cursory patrolled. Weather (wind/rain): Light rain Follow up required (select advisory)? No Additional fault restoration comments: Tree branch fell onto lines, the tree is outside the notice zone. Removed with Hot Stick no damage caused. NDR to follow SUBTRANSMISSION DETAIL LOS to sub (no or sub name): Circuit that tripped: DTF (KM): | .
4202 |  | JE24020268 | COROGLEN | Eastern | COROGLEN | 2024-06-09 | 17:11 | 2024-06-09 | 19:48 | 0.19399 | 0.0025548 | 512 | 70311 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: Recloser RC15 Protection flags (nil where none): EF, Phase C OC CAUSE: Broken Insulator Location: Pole W0848 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Insulator replaced at Pole W0848 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4203 |  | JE24020278 | PUNGAREHU | Western | PUNGAREHU | 2024-06-09 | 22:17 | 2024-06-10 | 2:06 | 0.019546 | 8.5528e-05 | 31 | 7085 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Line patrolled, Line down found between Poles 711180 & 462436, conductor has broken due to the bad weather Isolated at Fuses PU364 Lines repaired, Full power restored Line is in bad condition, multiple joints through out, faultman counted over 40 Joints, Line up grade required | .
4204 |  | JE24020286 | OTAKEHO | Western | OTAKEHO | 2024-06-09 | 19:54 | 2024-06-09 | 23:21 | 0.24103 | 0.002163 | 784 | 87362 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 6 Protection flags (nil where none): E/F, O/C c CAUSE: Line down due to Weather Location: 717754 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): wind, rain LFI (Y/N + Comments): y where not in the path of the fault Follow up Required (select advisory)? y Additional fault restoration comments: Line patrolled, Line down at Pole 717754, conductor broke at the insulator, Isolated at ABS 6619 & MA191 Line fixed, full power restored CB 6 back feeding MNA CB 5 & Part of TAS CB 8 SEC 12567/2 did not trip open to isolate faulted network on CB 6 A/R, Sec 12567/2 & Rec 12137/2 lost comm's as soon as the power went out so batteries need to be replaced SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4205 |  | JE24020294 | BURNSIDE | Western | BURNSIDE | 2024-06-09 | 22:43 | 2024-06-09 | 23:21 | 0.00083247 | 2.2072e-05 | 8 | 302 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | REGULATORY INFORMATION Voltage & Device ID: CB C928 , Fuses 8183 Protection flags (nil where none): Phase A Fault, Ground CAUSE: Floating Conductor Location: Pole 368222 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): Windy LFI (Y/N + Comments): Yes at Pole 797807 Follow up Required (select advisory)? No Additional fault restoration comments: Restrung floating conductor , power restored 23:20Hrs | .
4206 |  | JE24020183 | SOUTH RD NGARIKI | Western | SOUTH RD NGARIKI | 2024-06-08 | 6:18 | 2024-06-08 | 12:56 | 0.0068371 | 4.4143e-05 | 11 | 2478 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: NG377 No. Fuses: 2 Fuse Amp Size: 15amp TIME CLOSED: 08:30 Cause: Blown transformer N3052 Weather (wind/rain): Fine Follow up required (select advisory)? No Isolation: NG377 CAUSE: Defective Tfr N3082 Temp generation (stage details when used): no Additional fault restoration comments: Tfr N3082 was isolated to replace Transformer. N3082 fuses closed 12:56 | .
4207 |  | JE24020194 | 432 WAINUIORU ROAD, HINAKURA, MASTERTON, 5883 | Western | LONGBUSH | 2024-06-08 | 11:50 | 2024-06-08 | 13:06 | 0.0014584 | 1.9313e-05 | 7 | 529 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: Fuses 7103 Protection flags (nil where none): Nil CAUSE: Low Lines Location: Fuses 7103 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: cursory Weather (wind/rain): calm LFI (Y/N + Comments): Nil Follow up Required (select advisory)? No Additional fault restoration comments: Low lined repaired Power off 11:50, Power ON 13:05 | .
4208 |  | JE24016918 | 731 AWAITI ROAD AWAITI PAEROA | Eastern | TIROHIA-KARANGAHAKE | 2024-06-07 | 10:00 | 2024-06-07 | 13:23 | 0.0022377 | 1.1036e-05 | 4 | 811 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE 11KV DOUBLE PIN XARM AT POLE N0052 | .
4209 |  | JE24017212 | 51 MAKAKAHO ROAD NGAMATAPOURI WANGANUI | Western | WAITOTARA | 2024-06-07 | 9:23 | 2024-06-07 | 10:29 | 0.0051076 | 7.7251e-05 | 28 | 1851 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re-Conductor 11KV from pole 780559 to X2991 Job was called off due to machinery Damage, (Digger had hit something on the way to job site damaging the hydraulic ram) | .
4210 |  | JE24017486 | 498B STATE HIGHWAY 1 BULLS BULLS | Western | CROFTON | 2024-06-07 | 9:16 | 2024-06-07 | 13:19 | 0.0047078 | 1.9313e-05 | 7 | 1706 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace transformer X2337. Downgrade from 150kVA to 30kVA and upgrade earth bank. | .
4211 |  | JE24017490 | 76 MELLINGTON ROAD HUNTERVILLE MARTON | Western | PUTORINO | 2024-06-07 | 9:00 | 2024-06-07 | 9:48 | 0.0014577 | 3.0349e-05 | 11 | 528 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV crossarm on pole 805888. | .
4212 |  | JE24017496 | 217 MILLARS ROAD LONGBUSH CARTERTON | Western | PARK RD | 2024-06-07 | 9:08 | 2024-06-07 | 12:32 | 0.0022486 | 1.1036e-05 | 4 | 815 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Repair Transformer Foundation at TX T4446 | .
4213 |  | JE24017509 | 3891 WESTERN LAKE ROAD OCEAN BEACH FEATHERSTON | Western | PIRINOA | 2024-06-07 | 9:31 | 2024-06-07 | 11:36 | 0.00034482 | 2.759e-06 | 1 | 125 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re-terminate 11kv cable @ HV fuses 7003 | .
4214 |  | JE24017510 | 401 NGAUMU ROAD NGAUMU MASTERTON | Western | WERAITI | 2024-06-07 | 9:15 | 2024-06-07 | 10:31 | 0.0075568 | 9.9323e-05 | 36 | 2739 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv crossarm at pole 827507 | .
4215 |  | JE24017524 | 49 FOX ROAD SPRINGVALE WANGANUI | Western | HEADS RD | 2024-06-07 | 9:46 | 2024-06-07 | 10:04 | 0.0032625 | 0.00018209 | 66 | 1183 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Top transformer X3158 up with oil | .
4216 |  | JE24019398 | 286 RUAKIWI ROAD KOURARAU HILL MASTERTON | Western | WESTMERE GLADSTONE | 2024-06-07 | 10:45 | 2024-06-07 | 13:11 | 0.004821 | 3.3108e-05 | 12 | 1747 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv pole 829633 | .
4217 |  | JE24020047 | WAIHI NORTH | Eastern | WAIHI NORTH | 2024-06-07 | 2:00 | 2024-06-07 | 4:13 | 0.0010998 | 8.2769e-06 | 3 | 399 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: FC2172 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 04:12 Cause: possible bird strike Weather (wind/rain): Follow up required (select advisory)? | .
4218 |  | JE24020051 | HETHERINGTON RD | Eastern | HETHERINGTON RD | 2024-06-07 | 7:37 | 2024-06-07 | 7:38 | 0.0063276 | 0.0059759 | 2166 | 2293 | Unplanned | DEFECTIVE EQUIPMENT - ZONE SUBSTATION | Testing of BESS. BESS didn't transition back to grid tied mode. momentary outage | .
4219 |  | JE24020111 | ELTHAM WEST 33KV | Western | ELTHAM WEST 33KV | 2024-06-07 | 12:21 | 2024-06-07 | 13:41 | 0.00066597 | 8.2769e-06 | 3 | 241 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: CB 2822 Protection flags (nil where none): B phase EF CAUSE: Unknown Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: cursory Weather (wind/rain): light rain LFI (Y/N + Comments): not indicating Follow up Required (select advisory)? Additional fault restoration comments: 11kV incomer at ELT Sub failed to open meaning line stayed live through the ELT 1kV bus. Deenergised the lines by opening CB R08 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Waihapa Circuit that tripped: DTF (KM): | .
4220 |  | JE24020154 | PIHAMA | Western | PIHAMA | 2024-06-07 | 19:23 | 2024-06-07 | 20:06 | 0.00011965 | 2.759e-06 | 1 | 43 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Fuses TA817 Protection flags (nil where none): CAUSE: Tipped Crossarm, Centre bolt fell out Location: Pole 71498 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4221 |  | JE24020179 | WHITIANGA-COROMANDEL 66KV | Eastern | WHITIANGA-COROMANDEL 66KV | 2024-06-07 | 23:02 | 2024-06-07 | 23:05 | 0.025485 | 0.0082796 | 3001 | 9237 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 66kV WHT CB50 & 66kV TAI CB60 Protection flags (nil where none): A Ø E/F & Line E/F CAUSE: Unknown Location: Unknown Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Full Line Patrol requested for 07:00 on 08/06/2024 Weather (wind/rain): Unknown LFI (Y/N + Comments): Yes, LFI's at Pole 858511 & Pole CGNWHT037 operated. Follow up Required (select advisory)? Yes Additional fault restoration comments: After the 66kV Circuit tripped and COR S/S was without supply. LFI's at Pole 858511 & Pole CGNWHT037 operated, the suspected faulty section was Isolated by NOC Opening MABS 3602. Once this was completed the supply was restored via WHT CB 50 at 23:03 to prove that section was fault free and then supply was restored at COR S/S by closing in CB 17 & CB 19 at 23:04 A full Line Patrol has been requested for 07:00 on 08/06/2024 (Downer Hub has been notified)- Helicopter patrol requested by Shane Walker at 06:50, Authorised by David Spellman at 06:52 (08/06/24) LINE PATROLLED, NOTHING FOUND Protection issue:- distance to fault indicated the it was 2.93 km Tairua sub. LFI's indicated further than this as well, Maybe a scaling issue?? SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): COR S/S Circuit t | .
4222 |  | JE24020180 | IND ESTATES | Western | IND ESTATES | 2024-06-07 | 23:08 | 2024-06-08 | 0:51 | 0.00053394 | 8.2769e-06 | 3 | 194 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 4 Protection flags (nil where none): A, B & C ph O/C & E/F CAUSE: Car vs Sw/Gear 10435 Location: Sw/Gear 10435 Temp generation (state details when used): Y on Tfr 7464P PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: N/A Weather (wind/rain): Unk LFI (Y/N + Comments): Operated Correctly at 10426 Follow up Required (select advisory)? Additional fault restoration comments: Voltage source installed on Tfr 7464P on Emap as customer is on Generator. Sw/Gear and cables are being replaced under planned NAPA 112035 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4223 |  | JE24016963 | 62 HIKUAI SETTLEMENT ROAD DUCK CREEK HIKUAI | Eastern | HIKUAI | 2024-06-06 | 9:45 | 2024-06-06 | 15:30 | 0.0095161 | 2.759e-05 | 10 | 3449 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To divert 11kV lines in readiness for fibre install | .
4224 |  | JE24016966 | 86 Hill Road Tirau | Eastern | CAMBRIDGE RD TIRAU | 2024-06-06 | 9:15 | 2024-06-06 | 12:20 | 0.0030624 | 1.6554e-05 | 6 | 1110 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace HV Arms at Poles 877869 and 877870 | .
4225 |  | JE24016969 | 252 POUARUA ROAD SOUTH NGATEA NGATEA | Eastern | KAIHERE | 2024-06-06 | 9:15 | 2024-06-06 | 11:44 | 0.0012284 | 8.2769e-06 | 3 | 445 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace DDO arm at TC274 | .
4226 |  | JE24016974 | 104 THAMES COAST ROAD WHAKATETE BAY THAMES | Eastern | THAMES COAST | 2024-06-06 | 10:24 | 2024-06-06 | 13:47 | 0.0011179 | 5.5179e-06 | 2 | 405 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Repair TC1293 doors | .
4227 |  | JE24016977 | 547 UPPER OHAUITI ROAD OHAUITI TAURANGA | Eastern | OHAUITI RD | 2024-06-06 | 10:16 | 2024-06-06 | 13:16 | 0.0019894 | 1.1036e-05 | 4 | 721 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace HV pole 212707 with anew 11m concrete busck | .
4228 |  | JE24017128 | 280 SOUTH ROAD HAWERA HAWERA | Western | KETEMARAE RD | 2024-06-06 | 10:01 | 2024-06-06 | 15:13 | 0.066858 | 0.0002152 | 78 | 24233 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove WH297 & WH160. Sleeve O/H jumpers through at both sites. | .
4229 |  | JE24017180 | 11 CAMPBELL ROAD AORANGI FEILDING | Western | CROWN | 2024-06-06 | 9:30 | 2024-06-06 | 14:29 | 0.00082272 | 2.759e-06 | 1 | 298 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Make linebreak P32378 replace ABS J90 close linebreak | .
4230 |  | JE24017424 | 4073 Whanganui River Rd, Raetihi | Western | RAETIHI | 2024-06-06 | 9:45 | 2024-06-06 | 14:26 | 0.058819 | 0.00020968 | 76 | 21319 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Site 2 & 3. Replace 11kv pole 777604 and install new stay at 777613. | .
4231 |  | JE24017427 | 125 WHAKATOMOTOMO ROAD PIRINOA FEATHERSTON | Western | BURNSIDE | 2024-06-06 | 9:38 | 2024-06-06 | 14:31 | 0.031525 | 0.0001076 | 39 | 11426 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Change HV arms & poles from S538 to end of line | .
4232 |  | JE24017453 | 85613 STATE HIGHWAY 2 MOUNT BRUCE MASTERTON | Western | RONGOKOKAKO | 2024-06-06 | 9:46 | 2024-06-06 | 15:03 | 0.015742 | 4.9661e-05 | 18 | 5706 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To clear trees from pole P12703 | .
4233 |  | JE24017456 | 63 BAIRD ROAD TOKOROA TOKOROA | Eastern | DUKE ST | 2024-06-06 | 10:30 | 2024-06-06 | 13:06 | 0.030909 | 0.00019865 | 72 | 11203 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9468/1/2/3 | .
4234 |  | JE24017507 | 85 HENDERSONS LINE MARTON MARTON | Western | HENDERSON | 2024-06-06 | 9:16 | 2024-06-06 | 12:39 | 0.0016867 | 8.2769e-06 | 3 | 611 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace transformer X3106 due to Rust | .
4235 |  | JE24017902 | 368 IRONWORKS ROAD HUNTERVILLE HUNTERVILLE | Western | HUNTERVILLE 22KV | 2024-06-06 | 8:36 | 2024-06-06 | 13:42 | 0.026184 | 8.5528e-05 | 31 | 9490 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Stage_10: Reconductoring the 11kv lines between poles 807604 to pole 807648 | .
4236 |  | JE24018258 | CNR OLD TAUPO RD & CAMBELL RD TOKOROA | Eastern | OLD CAMBRIDGE RD | 2024-06-06 | 10:16 | 2024-06-06 | 15:56 | 0.045987 | 0.00013519 | 49 | 16668 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE POLE KINMAR033 AND INSTALL NEW NOJA RECLOSER. REUSE EXISTING ABS 1005 AS A BYPASS 14843/1. | .
4237 |  | JE24013529 | 192 PUKEMIKU ROAD MANGAMUTU PAHIATUA | Western | MANGATAINOKA | 2024-06-05 | 8:46 | 2024-06-05 | 14:43 | 0.019738 | 5.5179e-05 | 20 | 7154 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To remove trees from 11kv lines between pole 471446 & 356104 | .
4238 |  | JE24016819 | 41 WOLSELEY ROAD TANNERS POINT | Eastern | BOWENTOWN | 2024-06-05 | 8:30 | 2024-06-05 | 10:39 | 0.0057151 | 4.4143e-05 | 16 | 2071 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace HV arm on Pole 207185 and Pole 207188 | .
4239 |  | JE24016826 | 17 MOUNTIER ROAD WHAKAMARAMA | Eastern | APATA | 2024-06-05 | 12:15 | 2024-06-05 | 13:14 | 0.0056425 | 9.6564e-05 | 35 | 2045 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace HV arm on Pole 205734 | .
4240 |  | JE24016847 | 3610 STATE HIGHWAY 29 TE POI MATAMATA | Eastern | TE POI | 2024-06-05 | 9:21 | 2024-06-05 | 10:49 | 0.0007314 | 8.2769e-06 | 3 | 265 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace L1 Cross Arm at Pole F1765 | .
4241 |  | JE24016894 | 21 MILFORD PARK DRIVE PAENGAROA TE PUKE | Eastern | ROYDEN DOWNS RD | 2024-06-05 | 9:49 | 2024-06-05 | 14:54 | 0.0067201 | 2.2072e-05 | 8 | 2436 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | HV link box maintenance | .
4242 |  | JE24016896 | 1974 HINEKURA ROAD HINAKURA MARTINBOROUGH | Western | COLOGNE ST | 2024-06-05 | 9:16 | 2024-06-05 | 13:29 | 0.0027926 | 1.1036e-05 | 4 | 1012 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace transformer structure T1330 | .
4243 |  | JE24016900 | 15 NICHOLSON ROAD PIARERE TIRAU | Eastern | TOTMANS RD | 2024-06-05 | 11:45 | 2024-06-05 | 13:51 | 0.0034657 | 2.759e-05 | 10 | 1256 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace L1 Arm and DDO arm at pole E12578 | .
4244 |  | JE24016905 | 710 AWAITI RD PAEROA | Eastern | TIROHIA-KARANGAHAKE | 2024-06-05 | 9:39 | 2024-06-05 | 13:01 | 0.00044668 | 5.5179e-06 | 2 | 162 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE 11KV XARMS AT POLES'S N2843,N2845,N0066 AND N0092 | .
4245 |  | JE24016930 | 134 OMAHU VALLEY ROAD PURIRI PAEROA | Eastern | PURIRI | 2024-06-05 | 10:16 | 2024-06-05 | 13:17 | 0.010972 | 6.0697e-05 | 22 | 3977 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace HV x-arms | .
4246 |  | JE24016936 | 104C WAINUI SOUTH ROAD WHAKAMARAMA | Eastern | APATA | 2024-06-05 | 9:17 | 2024-06-05 | 10:47 | 0.00074078 | 8.2769e-06 | 3 | 269 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv x-arms at poles 205680 & 205681 "pole top photography" | .
4247 |  | JE24016939 | 533 WAINUI SOUTH ROAD WHAKAMARAMA | Eastern | PAHOIA | 2024-06-05 | 12:07 | 2024-06-05 | 13:17 | 0.009443 | 0.00013519 | 49 | 3423 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv & l.v x-arms at pole 209465 "pole top photography" | .
4248 |  | JE24016944 | 70 ROCK ROAD PAHIATUA PAHIATUA | Western | KONINI | 2024-06-05 | 9:30 | 2024-06-05 | 12:13 | 0.010796 | 6.6215e-05 | 24 | 3913 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace pole P47567 | .
4249 |  | JE24017052 | 277 SNODGRASS ROAD WHAKAMARAMA | Eastern | TE PUNA | 2024-06-05 | 8:45 | 2024-06-05 | 13:57 | 0.0043051 | 1.3795e-05 | 5 | 1560 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | connect HV bridges to new 11kv Recloser # 14815 @ pole 483530 and leave in operation mode. Isolation and issuer earths @ links temp 025 and sw/gear 13890/3. | .
4250 |  | JE24017056 | 66 DOUGLAS NORTH ROAD HUIROA STRATFORD | Western | HUIROA | 2024-06-05 | 9:00 | 2024-06-05 | 14:16 | 0.0060999 | 1.9313e-05 | 7 | 2211 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | asplundh to cut trees between poles 759577 & 759544 | .
4251 |  | JE24017063 | 66 ELIZABETH DRIVE TOKOROA TOKOROA | Eastern | THOMPSON DR | 2024-06-05 | 10:01 | 2024-06-05 | 14:15 | 0.035763 | 0.00014071 | 51 | 12963 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - FC3311-IC1915-IC1828 | .
4252 |  | JE24017102 | 1051 TE WHARAU ROAD KOURARAU HILL MASTERTON | Western | WESTMERE GLADSTONE | 2024-06-05 | 9:47 | 2024-06-05 | 15:02 | 0.12503 | 0.00039729 | 144 | 45317 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Vegetation cutting, site 1- between poles 829681 and 829682, site 2- between poles 365142 and 829619 | .
4253 |  | JE24017899 | 368 IRONWORKS ROAD HUNTERVILLE HUNTERVILLE | Western | HUNTERVILLE 22KV | 2024-06-05 | 8:32 | 2024-06-05 | 14:42 | 0.031663 | 8.5528e-05 | 31 | 11476 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 807603, 807604, 807630, 807631, 807633, 807643 & fit SVD's on pole 345129. Remove OH LV conductor from 807630 - 807639. Upgrade TX X210 on pole 807633 with 15kVa 3ph TX (Number to remain) | .
4254 |  | JE24018611 | 27 RAILWAY CRESCENT MASTERTON MASTERTON | Western | CORADINE ST | 2024-06-05 | 8:45 | 2024-06-05 | 10:49 | 0.0078474 | 6.3456e-05 | 23 | 2844 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace T1640 | .
4255 |  | JE24019715 | SEAWARD COAST | Western | SEAWARD COAST | 2024-06-05 | 16:00 | 2024-06-05 | 16:36 | 0.0048285 | 0.00013519 | 49 | 1750 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Cause: Deterioration What was replaced? 1x63A fuse and Fuse holder Where was it replaced (pole/TX/pillar box)? Pole 757771 Is 2R required? Y 2R Y - What is the timeframe for repairs? Complete Additional Info: Using the 2R due to Access issues At Pole 757771 - the LV Bushings are below the LV Fuses - Bucket Truck and Traffic Management required. Wait on callback from FM for additional notes - HM. Lead from DTX Bushing to Cutout Replaced 05/06/24 Job Complete HV isolation from TX fuses on 05/06 | .
4256 |  | JE24019769 | KAITEMAKO RD | Eastern | KAITEMAKO RD | 2024-06-05 | 7:38 | 2024-06-05 | 9:58 | 0.32253 | 0.0029631 | 1074 | 116902 | Unplanned | WILDLIFE - OTHER | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 13859/2 & WBY CB4 Protection flags (nil where none): A & C Ø O/C on REC 13859/2 CAUSE: Cattle (Bulls) rubbing against stay-wire. Location: Pole 249679 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Calm & clear. LFI (Y/N + Comments): Nothing on SCADA, only in the field which Field Switcher is going to investigate at Sw/Gear 13306/3 - LFI did not operate. Follow up Required (select advisory)? Yes Additional fault restoration comments: Called 1 X FM advised to redirect to check hazard at 174 Kaitmako Road - HE24002303 Linked a second job at 09.43 05/06/24 323 WAITAHA ROAD, TAURANGA reported sparks on pole Site 1: Hazard - Big flash/arc at Transformer TP3808 Field Switcher found HV Lines had crossed over each other and were tangled up at Pole 222219. This was resolved and put back to normal using a hot stick. Site 2: Field Switcher found cattle (Bulls) rubbing against stay-wire at Pole 249679 which we think may have caused the initial fault. (Lines clashed) Weather was calm and beautiful and no LFI's had operated in the field. Advisory has been selected - Investigate a plan to install fence or structure around stay-wire to prevent this from happening | .
4257 |  | JE24019810 | TE PUNINGA | Eastern | TE PUNINGA | 2024-06-05 | 11:30 | 2024-06-05 | 19:13 | 0.0012749 | 2.759e-06 | 1 | 462 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Transformer TC4031 is faulty. Isolation: TX TC4031 Fuses (job was created at the wrong device) CAUSE: Internal Fault. Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Calm Follow up required (select advisory)? No Additional fault restoration comments: HV Transformer is faulty at TC4031 Field Switcher is busy sourcing a new Transformer. Repairs to be carried out this afternoon. Transformer has been replaced under AP 9810-01 Full Power restored at 19:12 Voltage checks were confirmed and are correct. | .
4258 |  | JE24019816 | PIONEER RD | Western | PIONEER RD | 2024-06-05 | 10:06 | 2024-06-05 | 13:21 | 0.0005385 | 2.759e-06 | 1 | 195 | Unplanned | OTHER | During planning/approval/advertising timeframes no ICPs listed on transformer. One ICP affected on the date of outage for NAPA 111151. | .
4259 |  | JE24019838 | ROYDEN DOWNS RD | Eastern | ROYDEN DOWNS RD | 2024-06-05 | 12:07 | 2024-06-17 | 14:38 | 0.0014035 | 1.1036e-05 | 2 | 509 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Isolation: Fused ABS SF6-026 CAUSE: Suspect HV Cable fault. Temp generation (stage details when used): Yes, at Transformer TF6-075. Confirm Generator in service at : 15:58 PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Calm Follow up required (select advisory)? Yes Additional fault restoration comments: Upon arrival Field Switcher found Fuses blown at Fused ABS SF6-026 Suspect HV Cable is faulty, Generator is being put on for tonight and a Test permit will be taken tomorrow to identify the root cause. (06/06/2024) 06/06/2024 Test Permit taken and results indicate HV Cable fault. Will return on the 07/06/2024 to carry out repairs. 13/06/2024 DNO 2406006 created so HV Cable fault can be repaired. 17/06 - cable replaced, GEN/DNO removed | .
4260 |  | JE24019846 | 1974 HINEKURA ROAD HINAKURA MARTINBOROUGH | Western | COLOGNE ST | 2024-06-05 | 12:59 | 2024-06-05 | 13:29 | 0.0048475 | 0.00016554 | 60 | 1757 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | To Repair Jumper Found on live section of network during NAPA 110218. Location: Fuses 7374 Isolation: ABS S591 Cause: Aged / Corrosion Shutdown to re-terminate broken jumper found during planned shutdown | .
4261 |  | JE24019878 | MATAKANA RD | Eastern | MATAKANA RD | 2024-06-05 | 15:00 | 2024-06-05 | 17:57 | 0.0029198 | 1.6554e-05 | 6 | 1058 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses SC3-067 No. Fuses: 2 + Barrel Fuse Amp Size: 6 Amp TIME CLOSED: 17:56 Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)? No | .
4262 |  | JE24019894 | GULLIVER RD | Eastern | GULLIVER RD | 2024-06-05 | 18:00 | 2024-06-05 | 19:35 | 0.00078231 | 8.2769e-06 | 3 | 284 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses FP894 No. Fuses: 2 + 2 Barrels Fuse Amp Size: 8 Amp TIME CLOSED: 19:34 Cause: Suspect bird strike. Weather (wind/rain): Clear Follow up required (select advisory)? No | .
4263 |  | JE24019901 | WHITELEY ST | Western | WHITELEY ST | 2024-06-05 | 21:30 | 2024-06-05 | 23:23 | 0.12896 | 0.0028086 | 627 | 46742 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kv CB7 Protection flags (nil where none): B Phase E/F CAUSE: Cable fault Location: Between Sw/Gear 83/3 & Magnefix 306/1 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): 2406002 Circuit patrolled and type: Weather (wind/rain): Fine LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Hospital Auto Change over did not work | .
4264 |  | JE24012718 | 12 CHESTER ROAD CLAREVILLE CARTERTON | Western | CHESTER RD | 2024-06-04 | 8:48 | 2024-06-04 | 11:40 | 0.0014276 | 8.2769e-06 | 3 | 517 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Straighten and re block transformer pole T2479 | .
4265 |  | JE24016785 | 10014 STATE HIGHWAY 2 WAIHI WAIHI | Eastern | WAIHI BEACH RD | 2024-06-04 | 9:00 | 2024-06-04 | 10:40 | 0.008336 | 8.5528e-05 | 31 | 3021 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Arm at Pole P0090 Outage details incomplete only recording for ABS 448 open. Links TEMP11 not in emap and line break did not create a job either | .
4266 |  | JE24016786 | 485 WOODLANDS ROAD WAIHI WAIHI | Eastern | WAIHI BEACH RD | 2024-06-04 | 12:00 | 2024-06-04 | 13:14 | 0.0087751 | 0.00011864 | 43 | 3181 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace arm at pole P0349 | .
4267 |  | JE24016808 | 8402 PAEROA KOPU ROAD HIKUTAIA PAEROA | Eastern | PURIRI | 2024-06-04 | 10:30 | 2024-06-04 | 12:30 | 0.029355 | 0.00024555 | 89 | 10640 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove ABS TEMP39 and ABS TEMP35 | .
4268 |  | JE24016815 | 1795 WHITE ROCK ROAD TUTURUMURI MARTINBOROUGH | Western | TUTURUMURI | 2024-06-04 | 9:00 | 2024-06-04 | 13:18 | 0.003551 | 1.3795e-05 | 5 | 1287 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace existing broken concrete pole 372025 with new 11m busck concrete pole | .
4269 |  | JE24016816 | 829 KAHUTARA ROAD KAHUTARA FEATHERSTON | Western | KUMENGA | 2024-06-04 | 9:30 | 2024-06-04 | 9:50 | 0.00027153 | 1.3795e-05 | 5 | 98 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv jumper off fuses 7315 | .
4270 |  | JE24016817 | 393 WORK ROAD AONGATETE | Eastern | APATA | 2024-06-04 | 8:56 | 2024-06-04 | 11:10 | 0.015126 | 0.00011312 | 41 | 5482 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace HV arm on Pole 205394 and remove brace pole 205395 | .
4271 |  | JE24016818 | 1663 PORT CHARLES ROAD PORT CHARLES COROMANDEL | Eastern | COLVILLE | 2024-06-04 | 10:01 | 2024-06-04 | 10:59 | 0.0041462 | 7.1733e-05 | 26 | 1503 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove 11kV SWER Recloser 9927 for repair - DNO2203018. | .
4272 |  | JE24016833 | 269 THOMPSONS TRACK AONGATETE KATIKATI | Eastern | KATIKATI | 2024-06-04 | 12:26 | 2024-06-04 | 14:11 | 0.016127 | 0.0001545 | 56 | 5845 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace HV arm on Pole 208038 | .
4273 |  | JE24016845 | 1385 CHELTENHAM HUNTERVILLE ROAD WAITUNA WEST REWA | Western | WAITUNA | 2024-06-04 | 9:15 | 2024-06-04 | 12:22 | 0.014943 | 8.001e-05 | 29 | 5416 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV crossarms on poles P11997, P09700, P09702 and P09703. | .
4274 |  | JE24016848 | 10 BONNY DALE LANE PAENGAROA TE PUKE | Eastern | ROYDEN DOWNS RD | 2024-06-04 | 9:31 | 2024-06-04 | 11:22 | 0.0024389 | 2.2072e-05 | 8 | 884 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | HV link box maintenance | .
4275 |  | JE24016854 | 134 WILSON ROAD SOUTH PAENGAROA TE PUKE | Eastern | MAKETU | 2024-06-04 | 13:02 | 2024-06-04 | 14:05 | 0.00034469 | 5.5179e-06 | 2 | 125 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Link box maintenance | .
4276 |  | JE24017039 | 14 WHAREROA ROAD HAWERA HAWERA | Western | MANAWAPOU RD | 2024-06-04 | 9:00 | 2024-06-04 | 16:23 | 0.015464 | 3.5867e-05 | 13 | 5605 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install & commission CCCC RMU 12746. Run new HV UG cable from each bay to poles 459279, 732006, 728567 & 362149 while terminating the existing 11kV OH at each pole, removing all OH lines and poles 728568, 722858 in between. Remove ABS WH116 & WH251. Replace 11kV cross arm on poles 732007 & 732009. TXs 5394E and W1009 not advertised, on linked related job as unplanned | .
4277 |  | JE24017046 | 2 ERICA PLACE BELL BLOCK NEW PLYMOUTH | Western | KATERE 12 | 2024-06-04 | 9:15 | 2024-06-07 | 13:08 | 0.12757 | 0.0031204 | 342 | 46240 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | ELE020758 TAR GM Switchgear - Magnefix. Systematic/staged 4 day replacement of Magnefix 204 with new Safelink unit. | .
4278 |  | JE24019618 | PARAPARA | Western | PARAPARA | 2024-06-04 | 5:35 | 2024-06-04 | 11:10 | 0.017532 | 5.242e-05 | 19 | 6355 | Unplanned | WILDLIFE - OTHER | REGULATORY INFORMATION Voltage & Device ID: 11kV Fuses 1339 Protection flags (nil where none): CAUSE: Cattle rubbing poles causing wires to clast on narrow crossarms 1.4m Arms Location: Fuses 1339 section Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: oper Weather (wind/rain): windy LFI (Y/N + Comments): no Follow up Required (select advisory)? Additional fault restoration comments: Faultman isolated line at Fuses 1339, as second time fuse has blown i few hours, line will need to be patrolled at day light as goes across areas that can not be seen at night. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4279 |  | JE24019621 | NO 3 LINE | Western | NO 3 LINE | 2024-06-04 | 6:38 | 2024-06-04 | 13:23 | 0.1038 | 0.00025658 | 93 | 37622 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Report came in of Car vs Pole. NOC Operator opened Recloser 4849 to de-energise line before FM reached site. Location: 455644 Isolation: 4849/6 & 4793/6 Cause: Car vs Pole Replaced 11kV Pole, Crossarm, & Hardware. NDR to follow Weather: Calm | .
4280 |  | JE24019622 | TAVERNER ST | Western | TAVERNER ST | 2024-06-04 | 7:00 | 2024-06-04 | 7:40 | 0.00011169 | 2.759e-06 | 1 | 40 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses 7959 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 07:40 Cause: Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? No | .
4281 |  | JE24019703 | WAREA | Western | WAREA | 2024-06-04 | 14:01 | 2024-06-04 | 14:42 | 0.00022311 | 5.5179e-06 | 2 | 81 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Fuses PU251 Protection flags (nil where none): CAUSE: Tipped Crossarm, Centre Bolt fell out Location: Pole 709719 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4282 |  | JE24020061 | MANAWAPOU RD | Western | MANAWAPOU RD | 2024-06-04 | 9:00 | 2024-06-04 | 16:08 | 0.0047221 | 1.1036e-05 | 4 | 1712 | Unplanned | OTHER | ICPs part of planned work on HV NAPA 110004 - not advertised so outage is unplanned. | .
4283 |  | JE24019583 | 215 MILSON LINE, MILSON, PALMERSTON NORTH, 4414 | Western | TE ARAKURA | 2024-06-03 | 0:54 | 2024-06-03 | 3:10 | 0.011242 | 8.2769e-05 | 30 | 4075 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Sparking Lines at intersection of Milson Line & Newburn Line - Reported by Fire Comms F398710 Faultman found loose cable termination on pole 456640, line was isolated at ABS's D80, D79/1 and at Links D79/6 & 10249/6 to repair cable termination. | .
4284 |  | JE24019588 | KATERE 5 | Western | KATERE 5 | 2024-06-03 | 7:01 | 2024-06-03 | 8:16 | 0.0010334 | 1.3795e-05 | 5 | 375 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 8642 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 08:15 Cause: Unknown Weather (wind/rain): Fine Follow up required (select advisory)? | .
4285 |  | JE24019589 | BUNNYTHORPE | Western | BUNNYTHORPE | 2024-06-03 | 7:50 | 2024-06-03 | 12:17 | 0.13235 | 0.0014705 | 373 | 47971 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kv Rec4258 Protection flags (nil where none): B Phase O/C E/F CAUSE: 2 Blown Insulators Location: Pole P38969 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Light Rain LFI (Y/N + Comments): Yes but not Flashing Follow up Required (select advisory)? No Additional fault restoration comments: | .
4286 |  | JE24019590 | COLOGNE ST | Western | COLOGNE ST | 2024-06-03 | 7:53 | 2024-06-03 | 10:49 | 0.0077708 | 4.4143e-05 | 16 | 2817 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 7379 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 10:49 Cause: suspect bird strike , near swamp but unconfirmed Weather (wind/rain): Follow up required (select advisory)? | .
4287 |  | JE24019605 | PARAPARA | Western | PARAPARA | 2024-06-03 | 16:57 | 2024-06-03 | 19:23 | 0.0076624 | 5.242e-05 | 19 | 2777 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 1339 No. Fuses: 2 Fuse Amp Size: 8 TIME CLOSED: 19:23 Cause: unknown Weather (wind/rain): calm Follow up required (select advisory)? N | .
4288 |  | JE24019541 | TUTAENUI | Western | TUTAENUI | 2024-06-02 | 0:29 | 2024-06-02 | 4:01 | 0.019274 | 9.1046e-05 | 33 | 6986 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | Fuses Location: 939 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 04:00 Cause: Gum Bark across the line at Pole 476097 Weather (wind/rain): windy Follow up required (select advisory)?n Line Patrolled, Gum Bark removed with Hotstick | .
4289 |  | JE24019552 | NGARIKI RD | Western | NGARIKI RD | 2024-06-02 | 9:10 | 2024-06-02 | 11:11 | 0.0010004 | 8.2769e-06 | 3 | 363 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: N1115 No. Fuses: 2 reload and blow the first one Disconnect LV hold in Fine on Next Reload Fuse Amp Size: 2 TIME CLOSED: 11:10 Cause: Fault on Service Line Or in Shed Diso Tag A42688 Weather (wind/rain): Fine Follow up required (select advisory)? | .
4290 |  | JE24019562 | INLAND COAST | Western | INLAND COAST | 2024-06-02 | 13:01 | 2024-06-02 | 15:32 | 0.001255 | 8.2769e-06 | 3 | 455 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: transformer 1140 No. Fuses: 2 Fuse Amp Size: 2 TIME CLOSED: 15:32 Cause: Unknown Maybe Bird Weather (wind/rain): Fine Follow up required (select advisory)? | .
4291 |  | JE24018059 | 612 WAIHEKAU ROAD WAITOA - INGHAMS SUB | Eastern | INGHAMS 1 | 2024-06-01 | 9:07 | 2024-06-01 | 14:14 | 0.00084613 | 2.759e-06 | 1 | 307 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Service T1 Bank plus CB17, CB22, CB1, CB2 and CB3 at Ingahms Sub. (Inghams Site will be Isolated and Earthed from 09.00am to 15.00 hours) | .
4292 |  | JE24019488 | TOKO | Western | TOKO | 2024-06-01 | 4:49 | 2024-06-01 | 6:14 | 0.0063773 | 7.4492e-05 | 27 | 2311 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: 4957 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 06:14 Cause: unknown Weather (wind/rain): foggy Follow up required (select advisory)?n Line Patrolled | .
4293 |  | JE24019491 | BURNSIDE | Western | BURNSIDE | 2024-06-01 | 11:02 | 2024-06-01 | 11:55 | 0.0010207 | 1.9313e-05 | 7 | 370 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Broken HV jumper at pole 797415 due to corrosion, repaired and relivened. Isolation via Fuses 7450. | .
4294 |  | JE24019508 | MOUNT BRUCE | Western | MOUNT BRUCE | 2024-06-01 | 11:55 | 2024-06-01 | 14:35 | 0.0013319 | 8.2769e-06 | 3 | 483 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 7714 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 14:35 Cause: Unknown, lines patrolled. Weather (wind/rain): Windy Follow up required (select advisory)? No | .
4295 |  | JE24012716 | 30 MITCHELL ROAD WESTMERE WANGANUI | Western | MISSION RD | 2024-05-31 | 9:02 | 2024-05-31 | 13:55 | 0.038829 | 0.00013243 | 48 | 14074 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace TX Pole 774434 - X2400 | .
4296 |  | JE24016714 | 41 LONDON STREET WHANGANUI WANGANUI | Western | ARAMOHO RIVERSIDE | 2024-05-31 | 9:06 | 2024-05-31 | 13:45 | 0.00077053 | 2.759e-06 | 1 | 279 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace transformer X3070 due to oil leak and rust Job was late been taken out due to problem with LV back feed. The Fuses 16131 to Tfr X3070 are not connected on emap, job had to be made by off lining the transformer, will need to be drawn. | .
4297 |  | JE24016801 | 368 IRONWORKS ROAD HUNTERVILLE HUNTERVILLE | Western | HUNTERVILLE 22KV | 2024-05-31 | 8:45 | 2024-05-31 | 16:24 | 0.030395 | 6.6215e-05 | 24 | 11017 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Stage 4: Replace pole 807662, 807665, 807669, 807670, 807671, 807672, 807668. Replace X-arms 807664, 807666. Reuse Tx X395 at pole 807672 | .
4298 |  | JE24018055 | 15 MOREA ROAD ARARATA HAWERA | Western | TAWHITI RD | 2024-05-31 | 16:43 | 2024-05-31 | 17:13 | 8.2723e-05 | 2.759e-06 | 1 | 30 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | reinstate powerlines from poles 725021 to 725026 & 725010 to 725016 with new squirrel conductor. reinstate line break & remove generators. | .
4299 |  | JE24019329 | KATIKATI | Eastern | KATIKATI | 2024-05-31 | 2:03 | 2024-05-31 | 5:49 | 0.035039 | 0.0001545 | 56 | 12700 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: SC2-006 No. Fuses: 2 Fuse Amp Size: 30 Amp TIME CLOSED: 05:49 Cause: Suspect Line Clash Weather (wind/rain): High winds Follow up required (select advisory)? No Please check Fuses SC2-006 Line Patrol was carried out, high winds in the area. Field Switcher mentioned new Poles were installed recently. | .
4300 |  | JE24019376 | LINDERMANN RD | Eastern | LINDERMANN RD | 2024-05-31 | 13:31 | 2024-05-31 | 14:28 | 0.00031746 | 5.5179e-06 | 2 | 115 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: wind What was replaced? re bound conductor Where was it replaced (pole/TX/pillar box)? pole Is 2R required? N 2R Y - What is the timeframe for repairs? Additional Info: HV isolation from TX TB1-128 fuses | .
4301 |  | JE24019400 | RAETIHI | Western | RAETIHI | 2024-05-31 | 11:28 | 2024-05-31 | 13:22 | 0.00031418 | 2.759e-06 | 1 | 114 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Transformer X4031 Fuses No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 13:21 Cause: Unknown Weather (wind/rain): Weather Follow up required (select advisory)? | .
4302 |  | JE24019464 | WAIMAPU | Eastern | WAIMAPU | 2024-05-31 | 17:57 | 2024-05-31 | 20:00 | 0.001018 | 8.2769e-06 | 3 | 369 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: FP858 No. Fuses: 2 Fuse Amp Size: 10 Amp TIME CLOSED: 20:00 Cause: Suspect bird strike. Weather (wind/rain): Calm Follow up required (select advisory)? No | .
4303 |  | JE24012604 | Opp - 247A WAIPUNA ROAD RAETIHI RAETIHI | Western | RAETIHI | 2024-05-30 | 9:26 | 2024-05-30 | 11:26 | 0.0013221 | 1.1036e-05 | 4 | 479 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Resag lines at pole 777320. | .
4304 |  | JE24013189 | 2007 SOUTH ROAD PITONE NEW PLYMOUTH | Western | INLAND COAST | 2024-05-30 | 10:00 | 2024-05-30 | 13:55 | 0.025954 | 0.00011036 | 40 | 9407 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Site 2:To install Entec 12705 and remove hv fuses 8462 and replace pole 757626 Fault repaired beyond Fuses 8409 during this outage - ref JE24019083 | .
4305 |  | JE24018916 | MATAKANA RD | Eastern | MATAKANA RD | 2024-05-30 | 11:53 | 2024-05-30 | 13:03 | 0.0075158 | 0.0001076 | 39 | 2724 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Isolation from Fuses SC3-071 on 30/05 Replaced broken jumper at TC3-008, | .
4306 |  | JE24019039 | ROLLESTON ST | Eastern | ROLLESTON ST | 2024-05-30 | 21:10 | 2024-05-31 | 16:30 | 0.028809 | 2.4831e-05 | 9 | 10442 | Unplanned | VEGETATION - OUTSIDE ZONE | Fuses Location: TX TP3408 No. Fuses: 1 Fuse Amp Size: 6Amp TIME CLOSED: 15:54 Cause: Trees through the LV O/H Lines. Weather (wind/rain): Wind & rain. Follow up required (select advisory)? SMC advised off multiple properties affected LV O/H Line on the ground due to trees. HV Fuses could not be reloaded and closed in due to LV O/H Lines down. Isolation: TX TP3408 Fuses O, R & T 30/05 Tree cutting required, will return tomorrow. (31/05/2024) Trees removed and Fuses reloaded | .
4307 |  | JE24019114 | TATUA 33kV | Eastern | TATUA 33kV | 2024-05-30 | 1:14 | 2024-05-30 | 1:21 | 3.6369e-05 | 5.5179e-06 | 2 | 13 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 33kV CB3252 / CB3142 Protection flags (nil where none): Auto-reclosed several times. CAUSE: Unknown Location: Unknown Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): No wind & no rain. LFI (Y/N + Comments): No Follow up Required (select advisory)? Yes Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Farmer Rd (momentary) & Tatua S/S Circuit that tripped: Opened by NOC DTF (KM): Unknown Multiple Line trips that were happening and NOC carried out Load Shift from PKO3 to FRM6. (PKO carries Tatua S/S) Line Patrol was carried out - From my understanding no cause was found. Switching to Liven the Ripple Plant was carried out. Load was then transferred back from WHU GXP to PAO GXP and the Network was returned to it's normal state. | .
4308 |  | JE24019134 | TE ARAKURA | Western | TE ARAKURA | 2024-05-30 | 7:34 | 2024-05-30 | 10:50 | 0.032972 | 0.00033659 | 122 | 11951 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 10823/2 Protection flags (nil where none): E/F, O/C C CAUSE: Broken binder/Joint Failure Location: P33064 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): wind, rain LFI (Y/N + Comments): y, not woring back to scada, LFI at Pole P41432 Follow up Required (select advisory)? n Additional fault restoration comments: Line down at Pole P33064, HV/LV Clash, Isolated at ABS D87 & D89, 6 x Fargo Joints removed from Pole P33028, Line repaired at Pole P33064, 1141 Rangitikei Lane (Isolated at Main Switch, Meter needs to be replaced) 1147 Rangitikei Lane (Isolated at Main Switch, Meter needs to be replaced) 1150 Rangitikei Lane (Isolated, needs there Meters replaced, Tag A43197) 1162 Rangitikei Lane 2 x meter points, woolshed (Isolated at Main Switch, Meter needs to be replaced), House Isolated Tag A39124, No Access to check meter SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4309 |  | JE24019147 | JE24019144 | Western | TOKO | 2024-05-30 | 8:19 | 2024-05-30 | 10:50 | 0.01127 | 7.4492e-05 | 27 | 4085 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses 4957 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 10:50 Cause: Birdstrike Weather (wind/rain): Calm Follow up required (select advisory)? No | .
4310 |  | JE24019166 | KEITH ST 21 | Western | KEITH ST 21 | 2024-05-30 | 8:46 | 2024-05-30 | 12:16 | 0.0017358 | 8.2769e-06 | 3 | 629 | Unplanned | OTHER | Affected by NAPA 110969 Correct DTX G221 Iona Street & Ashford Avenue affected as well, not notified Passed on to Network Access Planning Power due back on 15:00 2R - Left open to close job | .
4311 |  | JE24019181 | HAURAKI RD | Eastern | HAURAKI RD | 2024-05-30 | 9:57 | 2024-05-30 | 15:06 | 0.00085156 | 2.759e-06 | 1 | 309 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: Fuses FC4045 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 15:05 Cause: WEATHER Weather (wind/rain): Yes Follow up required (select advisory)? No | .
4312 |  | JE24019194 | MANOEKA RD | Eastern | MANOEKA RD | 2024-05-30 | 12:43 | 2024-05-30 | 13:09 | 7.1273e-05 | 2.759e-06 | 1 | 26 | Unplanned | WILDLIFE - BIRD | Fuses Location: Transformer TP1365 No. Fuses: 1 (became 2-phase b/c of isolation for safety) Fuse Amp Size: 2A TIME CLOSED: 13:09 Cause: Bird Weather (wind/rain): Wind/rain Follow up required (select advisory)? Note: Open & Close Times for Fuses FP185 - isolated to safely remove the bird at Transformer TP1365 and replace fuse. | .
4313 |  | JE24019215 | ELIZABETH ST | Eastern | ELIZABETH ST | 2024-05-30 | 14:04 | 2024-05-30 | 21:13 | 0.30831 | 0.0031949 | 653 | 111748 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 9780/2 Protection flags (nil where none): Nil - Recloser did not trip. CAUSE: Car vs Pole Location: Pole G0675 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Fire advised ETA 10min Police advised 10 min Car V Pole at Pole G0675 Open TLB at Pole G0674 to reduce outage area down. NDR to follow Pole has been replaced and TLB has been closed. Full Power ON at 21:13 | .
4314 |  | JE24019223 | CHURCH ST | Western | CHURCH ST | 2024-05-30 | 13:44 | 2024-05-30 | 14:30 | 0.00063909 | 1.3795e-05 | 5 | 232 | Unplanned | WILDLIFE - BIRD | Fuses Location: 7026 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 14:30 Cause: bird strike, Pole 446149 Weather (wind/rain): calm Follow up required (select advisory)?n Line patrolled | .
4315 |  | JE24012603 | 3499 STATE HIGHWAY 4 KAKATAHI WANGANUI | Western | MAKIRIKIRI | 2024-05-29 | 9:57 | 2024-05-29 | 13:01 | 0.0020267 | 1.1036e-05 | 4 | 735 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Defected Transformer X603 | .
4316 |  | JE24015141 | 190 ORCHARD EAST ROAD TURUA THAMES | Eastern | HAURAKI RD | 2024-05-29 | 9:40 | 2024-05-29 | 10:25 | 0.0047143 | 0.00010484 | 38 | 1709 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole O12854 | .
4317 |  | JE24018800 | BROOKLANDS 7 | Western | BROOKLANDS 7 | 2024-05-29 | 9:06 | 2024-05-29 | 10:56 | 0.011857 | 0.0001076 | 39 | 4298 | Unplanned | VEGETATION - OUTSIDE ZONE | Trees in the lines and lines down between Pole 752667 & 752668 Isolate at Fuses 8423 and ABS 393 to repair NDR to follow | .
4318 |  | JE24018802 | 138 TATE ROAD, WAITARA, 4382 | Western | DEVON RD | 2024-05-29 | 10:48 | 2024-05-29 | 11:01 | 0.0010545 | 7.7251e-05 | 28 | 382 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | Isolate between ABS 6506 and 501 to remove tree bark on the lines at Pole 741780 using hot sticks | .
4319 |  | JE24018821 | INLAND COAST | Western | INLAND COAST | 2024-05-29 | 9:14 | 2024-05-29 | 12:22 | 0.0015518 | 8.2769e-06 | 3 | 562 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: Transformer 1140 No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 12:18 Cause: Line Clash due to Weather Weather (wind/rain): Wind Follow up required (select advisory)? No | .
4320 |  | JE24018839 | MVILLE NORTH | Eastern | MVILLE NORTH | 2024-05-29 | 10:01 | 2024-05-29 | 17:33 | 0.36262 | 0.0033273 | 1206 | 131433 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV PKO CB 1 Protection flags (nil where none): B, C Ø O/C & E/F CAUSE: Tree through HV Lines Location: Pole I065 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Rain & Strong winds. LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Tree went through the HV Lines. Portion of the customers were back feed after the feeder tripped. Faulty section Isolated and repairs carried out under AP Full Power restored at 17:32 | .
4321 |  | JE24018840 | BENNETT ST | Eastern | BENNETT ST | 2024-05-29 | 10:16 | 2024-05-29 | 14:09 | 0.068027 | 0.00029245 | 106 | 24657 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 9380/2 Protection flags (nil when none): E/F CAUSE: Trees through the HV Lines Location: Pole 876739 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Strong winds and rain. Follow up required (select advisory)? No Additional fault restoration comments: Trees brought HV Lines down. Repairs were completed under AP Full Power restored at 14:08 | .
4322 |  | JE24018841 | WAITAWHETA | Eastern | WAITAWHETA | 2024-05-29 | 10:17 | 2024-06-01 | 9:31 | 0.0075379 | 0.00013795 | 48 | 2732 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV Sec 9454 Protection flags (nil where none): A - B - C O/C E/F and Rec 9854 E/F 1 CAUSE: Trees through lines Poles broken in forestry. Can not access. Location: Temp generation (state details when used): Temp generation to transformers past Fuses 14562 PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: cursory Weather (wind/rain): high winds, Heavy rain LFI (Y/N + Comments): Nil Follow up Required (select advisory)? Yes, Check lines through forestry for clearances Additional fault restoration comments: 31/04/24 - Ferdi Two poles down and lines down. Job might take up to Tuesday to be complete. Lack of manpower 01/06/24 - Lines and pole repaired by James Brier 2 x poles replaced trees cut 02/06/24 - Cables re-connected, Generator removed and site livened by Mitchell West, before leaving site manager confirmed all supply fully restored. | .
4323 |  | JE24018842 | MANAIA COROMANDEL | Eastern | MANAIA COROMANDEL | 2024-05-29 | 10:17 | 2024-05-29 | 11:56 | 0.017005 | 0.00019589 | 71 | 6163 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | REGULATORY INFORMATION Voltage & Device ID: 11kV SEC 14439/2 Protection flags (nil where none): REC 13520/2 B Ø O/C CAUSE: Tree branch on O/H Line Location: Pole T1440 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Strong winds & rain. LFI (Y/N + Comments): Yes at Pole 268500 Follow up Required (select advisory)? No Additional fault restoration comments: Due to strong winds in the area, tree branch landed on O/H Lines at Pole T1440 and was then removed via Hotstick by the Field Switcher. Full Power restored at 11:55 | .
4324 |  | JE24018846 | PURIRI | Eastern | PURIRI | 2024-05-29 | 10:27 | 2024-05-29 | 11:09 | 0.020192 | 0.00048558 | 176 | 7319 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 9688 Protection flags (nil where none): B, C O/C CAUSE: Tree branch on the lines at pole 857033. Removed by hot stick Location: pole 857033 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): High wind, heavy Rain LFI (Y/N + Comments): 13587168 Follow up Required (select advisory)? No Additional fault restoration comments: | .
4325 |  | JE24018850 | KAIHERE | Eastern | KAIHERE | 2024-05-29 | 10:39 | 2024-05-29 | 13:26 | 0.0096705 | 5.7938e-05 | 21 | 3505 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Fuses FP1436 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 13:25 Cause: Lightning Weather (wind/rain): Rain Follow up required (select advisory)? No | .
4326 |  | JE24018855 | LINTON | Western | LINTON | 2024-05-29 | 10:51 | 2024-05-29 | 17:02 | 0.0092225 | 2.4831e-05 | 9 | 3343 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: H137 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 17:02 Cause: Unknown Weather (wind/rain): wind, rain Follow up required (select advisory)?n | .
4327 |  | JE24018885 | PIAKOITI RD | Eastern | PIAKOITI RD | 2024-05-29 | 12:19 | 2024-05-29 | 15:13 | 0.040178 | 0.00028141 | 102 | 14563 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 13640/2 Protection flags (nil where none): E/F CAUSE: Strong winds/deterioration. Location: Pole 388938 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Strong winds/rain. LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Broken binder on one phase. Repairs carried out and full Power on at 15:13 | .
4328 |  | JE24018892 | CLOTON RD SOUTH | Western | CLOTON RD SOUTH | 2024-05-29 | 12:24 | 2024-05-29 | 14:09 | 0.0089325 | 8.5528e-05 | 31 | 3238 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: Fuses 5562 No. Fuses: 2 Fuse Amp Size: 15A TIME CLOSED: 14:08 Cause: Weather Weather (wind/rain): Windy Follow up required (select advisory)? No | .
4329 |  | JE24018893 | WYUNA BAY | Eastern | WYUNA BAY | 2024-05-29 | 12:36 | 2024-05-29 | 14:18 | 0.020579 | 0.00057662 | 209 | 7459 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV rec RC07 Protection flags (nil where none): A O/C CAUSE: Line patrolled, unknown cause Location: Unkown Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): High winds, Heavy Rain, Lightning LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: | .
4330 |  | JE24018896 | APATA | Eastern | APATA | 2024-05-29 | 12:48 | 2024-05-29 | 16:33 | 0.019839 | 8.8287e-05 | 32 | 7191 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | REGULATORY INFORMATION Voltage & Device ID: 11kV Fuses SC2-057 Protection flags (nil where none): Fuses blown CAUSE: Very strong winds. Location: Pole 205 453 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Strong winds. LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: HV Lines down due to strong winds. Full Power restored at 16:33. | .
4331 |  | JE24018908 | WAIHI NORTH | Eastern | WAIHI NORTH | 2024-05-29 | 12:48 | 2024-05-29 | 12:54 | 0.00026587 | 3.8625e-05 | 14 | 96 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | REGULATORY INFORMATION Voltage & Device ID: 11kV Fuses FC2486 Protection flags (nil when none): Nil CAUSE: Strong winds Location: Pole P1126 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Strong winds & rain. Follow up required (select advisory)? No Additional fault restoration comments: Tree branch lying across HV O/H Lines Removed with hotstick. Full Power restored at 12:54 | .
4332 |  | JE24018910 | TOTARA | Eastern | TOTARA | 2024-05-29 | 13:39 | 2024-05-29 | 17:19 | 0.049924 | 0.00040833 | 148 | 18095 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kv Rec 9281 Protection flags (nil where none): B O/C, E/F CAUSE: patrolled, cause unknown Location: Unk Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: cursory Weather (wind/rain): High Wind, Heavy Rain LFI (Y/N + Comments): Nil Follow up Required (select advisory)? Additional fault restoration comments: | .
4333 |  | JE24018911 | PURIRI | Eastern | PURIRI | 2024-05-29 | 13:40 | 2024-05-30 | 15:58 | 0.080856 | 0.0013326 | 483 | 29307 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 3 Protection flags (nil where none): A,C O/C E/F CAUSE: Tree through the lines Matatoki Quarry Road. Location: Pole 425488 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: cursory Weather (wind/rain): High Wind, Heavy Rain LFI (Y/N + Comments): Nil Follow up Required (select advisory)? Additional fault restoration comments: Isolated at Fused ABS 14618 Gate locked & will return in the morning to remove trees & repair lines. Quarry notified & happy with this | .
4334 |  | JE24018912 | PYES PA | Eastern | PYES PA | 2024-05-29 | 13:25 | 2024-05-29 | 15:10 | 0.015701 | 0.00014898 | 54 | 5691 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | Fuses Location: Fuses SE3-017 No. Fuses: 2 Fuse Amp Size: 40A TIME CLOSED: 15:10 Cause: Branches in line Weather (wind/rain): Windy Follow up required (select advisory)? No | .
4335 |  | JE24018914 | MANGATARATA | Eastern | MANGATARATA | 2024-05-29 | 13:42 | 2024-05-31 | 18:31 | 0.07734 | 0.00080562 | 292 | 28032 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV RC24 Protection flags (nil where none): B O/C E/F CAUSE: Fault 1. Line down past fuses FP1167 Pole O4064 due to branch across the lines. Fault 2 Trees through the lines & broken Past fuses FP1009. Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: cursory Weather (wind/rain): High Wind, Heavy Rain LFI (Y/N + Comments): Nil Follow up Required (select advisory)? Additional fault restoration comments: Fault 2. Lines & Poles past fuses FP1009. Broken pole 855922 and broken transformer pole 855921 (TP165 ). Site has been made safe. This can not be repaired now, might be within 3 days. Due to the weather and the terrain. This was caused by a tree that has come down. FM will install a generator for the customer tomorrow morning. Have called and advised the customer of this, she is happy to be without power over night. Will need power by tomorrow as she has thousands of dollars worth of products that will be damaged with out power. 30/05 - gen connected to TP1809 at 13:00 31/05 Lines repaired and Transformer pole replaced | .
4336 |  | JE24018925 | OTAKEHO | Western | OTAKEHO | 2024-05-29 | 15:18 | 2024-05-29 | 16:47 | 0.011469 | 0.00012967 | 47 | 4157 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Outage Between ABS MA121 and ABS MA164 to replace king bolt at Pole 718285 On restoration ABS MA121 failed to close and arced. ABS is now left open with backfeeed in place. DNO 2405025 | .
4337 |  | JE24018934 | HIKUAI | Eastern | HIKUAI | 2024-05-29 | 14:32 | 2024-05-29 | 20:26 | 0.00097561 | 2.759e-06 | 1 | 354 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: TC5670 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 20:25 Cause: lightning Weather (wind/rain): Follow up required (select advisory)? | .
4338 |  | JE24018951 | KAIMAI DRIVE | Eastern | KAIMAI DRIVE | 2024-05-29 | 15:10 | 2024-05-29 | 16:20 | 0.049429 | 0.0013353 | 484 | 17916 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 9275/2 Protection flags (nil where none): A Ø O/C CAUSE: Wind blown debris/tree branch Location: TX TP3125 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Rain/wind LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Wind blown debris removed via hotstick. Full Power on at 16:19 | .
4339 |  | JE24018953 | MANGATEPARU | Eastern | MANGATEPARU | 2024-05-29 | 21:03 | 2024-05-30 | 17:01 | 0.0033035 | 2.759e-06 | 1 | 1197 | Unplanned | VEGETATION - OUTSIDE ZONE | tree through, pole down, lines out for night Fuses FC2401 open removed & tagged by Charlie @ 21:03Hrs Trees removed Power restored 17:00Hrs | .
4340 |  | JE24018960 | PATETONGA | Eastern | PATETONGA | 2024-05-29 | 16:11 | 2024-05-30 | 0:25 | 0.021793 | 4.4143e-05 | 16 | 7899 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV Fuses FP1322 Protection flags (nil where none): Fuses blown CAUSE: Tree fell over. Location: Poles K1173 & K1174 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Strong winds and rain LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: HV Lines down due to tree that fell over. Isolated at Fuses FP1322 LV isolated on TC261 awaiting morning inspection for potential LV / HV line clash 30/05/24 - Sean Walker - All inspections complete, full power restored to all properties - job complete | .
4341 |  | JE24018969 | WAIHI-WHANGAMATA 33KV | Eastern | WAIHI-WHANGAMATA 33KV | 2024-05-29 | 15:42 | 2024-05-29 | 15:54 | 0.03811 | 0.0078906 | 1430 | 13813 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Voltage & Device ID: 33kV CB 3252 Auto reclosed Protection flags (nil where none): B Ø E/F & Res E/F Weather (wind/rain): Strong winds and rain. Follow up required (select advisory): Yes, investigate BESS tripping please. LFI Activation: No This fault on the Network caused WGM BESS to trip out CB 1112 & CB 11 Protection: Grid UV/ frequency Unable to reset SMS alarm | .
4342 |  | JE24018971 | STATION RD | Eastern | STATION RD | 2024-05-29 | 15:44 | 2024-05-29 | 22:59 | 0.0036062 | 8.2769e-06 | 3 | 1307 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Fuses FC1407 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 22:59 Cause: Lightning Weather (wind/rain): Rain Follow up required (select advisory)? No Fuses Location: Transformer TC5261 No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 23:21 Cause: Lightning Weather (wind/rain): Rain Follow up required (select advisory)? No | .
4343 |  | JE24018972 | WAIHI NORTH | Eastern | WAIHI NORTH | 2024-05-29 | 15:44 | 2024-05-30 | 9:09 | 0.13683 | 0.00045523 | 165 | 49595 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 9604/2 Protection flags (nil where none): E/F CAUSE: Broken Jumper Location: Pole WHIWGM102 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Strong winds & rain LFI (Y/N + Comments): No Follow up Required (select advisory)? Additional fault restoration comments: Busy carrying out a Line Patrol. ABS IC213 was closed in to back feed customers. Could not complete patrol at night due to dangerous terrain - completed 30/05 and power restored | .
4344 |  | JE24018973 | MATAKANA RD | Eastern | MATAKANA RD | 2024-05-29 | 15:45 | 2024-05-30 | 11:06 | 0.26417 | 0.00024831 | 90 | 95749 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV SEC13216/2 Protection flags (nil where none): A, B Ø O/C & E/F CAUSE: Lines Down - unknown why Location: Pole 201957 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Weather (wind/rain): Strong winds & rain LFI (Y/N + Comments): Yes at Pole 202008 Follow up Required (select advisory)? Additional fault restoration comments: Ferry Not available till Tomorrow 30/05/24 Lines down repaired Power ON 11:05 | .
4345 |  | JE24018975 | HAURAKI RD | Eastern | HAURAKI RD | 2024-05-29 | 16:17 | 2024-05-29 | 16:30 | 0.012496 | 0.00097391 | 353 | 4529 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Lines down reported - was 400V lines down. Area isolated by control from Rec 9161 for safety. TX TC2890 isolated via LV fuses - Rec restored. No further HV impact. ETA Required - 10 MINUTES FC called F3984904 Recloser 9161 opened for safety. 400V fuses opened at Transformer TC2890 feeder relivened. 400V Line down. possible HV/LV clash TC2890 Isolated will be attending tomorrow. FM to ring back with TAG number and affected properties. Advised FM to also advise NC - NC advised all HV work has been completed. FM to ring back and give TAG info and affected ICP's FM can be completed off the 1R when the info has been received. 2R to be left open Power will be off over night No lines was not energized as feeder was dropped A41548 All off abbot road Across the road FM has advised customers affected - one customer not home. Will be rectified ASAP this week. Weather depending. 6 Abot road not home to inform TC2890 Tag Register Updated Retailer E-mailed Yes Iro Ezekiela called to say onsite 12:00 30/05/24 Iro closing job off - Replaced 2x insulators, 5m of conductor, 2x 100 amp fuses. Full power restored. This was nothing on the HV, all LV related here confirmed by the FM. MDP | .
4346 |  | JE24018998 | HIKUAI | Eastern | HIKUAI | 2024-05-29 | 21:46 | 2024-05-30 | 10:56 | 0.0021795 | 2.759e-06 | 1 | 790 | Unplanned | LIGHTNING - LIGHTNING STRIKE | FC4015 Close 21:45 1 fuse 3A Found transformer fuses had Operated again faulty transformer TC851 to be replaced tomorrow Difficult site access across rive may need GEN 30/05/2024 - Generator connected 10:55am SMC advised to send FM back under 2R to investigate why TX is no working Customer Contact: Garry Karl 027 918 0850 30/05/24 - 19:15 Brent Williams called and advised NES visited site and repaired generator and is back in service, was due to out of balance. Ben Edwards visited but was not able to resolve. generator CONNECTED 10:55 HrsTransformer replaced 31/05/24 Transformer Replaced .Power restored 13:15 Hrs, 31/05/24 Generator removed 13:20Hrs | .
4347 |  | JE24018999 | STRATHMORE | Western | STRATHMORE | 2024-05-29 | 13:24 | 2024-05-29 | 16:41 | 0.0059615 | 3.0349e-05 | 11 | 2161 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 5453 No. Fuses: 2 Fuse Amp Size: 8A TIME CLOSED: 1640 Cause: suspect line clash Weather (wind/rain): windy, heavy rain Follow up required (select advisory)? | .
4348 |  | JE24019020 | STATION RD | Eastern | STATION RD | 2024-05-29 | 18:47 | 2024-05-29 | 19:49 | 0.001378 | 2.2072e-05 | 8 | 499 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Replace cross arm at Pole G0466 Isolated at fuses FP947 Fuses FP947 closed after repairs @ 19:49 | .
4349 |  | JE24019021 | COROGLEN | Eastern | COROGLEN | 2024-05-29 | 16:56 | 2024-05-29 | 19:15 | 0.0011539 | 8.2769e-06 | 3 | 418 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: TC3173 No. Fuses: 2 Fuse Amp Size: 2 TIME CLOSED: 19:15 Cause: wind Weather (wind/rain): Follow up required (select advisory)? | .
4350 |  | JE24019044 | JE24019001 | Eastern | MANAIA COROMANDEL | 2024-05-29 | 16:23 | 2024-05-31 | 12:53 | 0.1318 | 0.0020002 | 349 | 47770 | Unplanned | LIGHTNING - LIGHTNING STRIKE | REGULATORY INFORMATION Voltage & Device ID: Recloser 13520 Protection flags (nil where none): EF CAUSE: Faulty Transformer TC5889 Location: Trf TC 5889 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): Check on completion JE24019087 & JE24019095 Transformer TC5889 to be replaced 31/05/24 - 1 Customer isolated - happy to be left off till tomorrow Transformer replaced, power restored 12:53 | .
4351 |  | JE24019076 | PARK RD | Western | PARK RD | 2024-05-29 | 19:18 | 2024-05-29 | 22:48 | 0.041153 | 0.00019589 | 71 | 14916 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | Fault branch removed pole 842083 Fuses 7606 2x 20A Fuses closed 22:47 Tree branch not found on first close attempt, 4 x20A fuses used in total | .
4352 |  | JE24019088 | COROGLEN | Eastern | COROGLEN | 2024-05-29 | 19:53 | 2024-05-30 | 9:01 | 0.010873 | 1.3795e-05 | 5 | 3941 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | Fuses Location: Fuses FC820 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 09:00 Cause: Tree Branch in Line Weather (wind/rain): Wind Follow up required (select advisory)? No | .
4353 |  | JE24019099 | SHAW AVE | Eastern | SHAW AVE | 2024-05-29 | 21:31 | 2024-05-29 | 23:48 | 0.10452 | 0.00099599 | 361 | 37883 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV POA CB 4 Protection flags (nil where none): B phase EF & Ground fault CAUSE: no fault found Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: operational Weather (wind/rain): wind & rain LFI (Y/N + Comments): sw/gear13535 indicating through switch gear Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4354 |  | JE24019103 | OWERA RD | Eastern | OWERA RD | 2024-05-29 | 22:20 | 2024-05-30 | 0:54 | 0.19773 | 0.0014126 | 512 | 71670 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV recloser RC15 Protection flags (nil where none): EF CAUSE: tree contact Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: No fault found but burnt tree branches found , faultman directed to use 2R to defect trees in area patrolled that may be problematic SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4355 |  | JE24019193 | KAIMAI DRIVE | Eastern | KAIMAI DRIVE | 2024-05-29 | 17:59 | 2024-05-30 | 17:11 | 0.007677 | 5.5179e-06 | 2 | 2783 | Unplanned | VEGETATION - INSIDE ZONE | Fuses Location: SE3-066 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 17:10 Cause: Trees contacting lines Weather (wind/rain): high winds & rain Follow up required (select advisory)? No Job actually for the 29/05/24, original job cancelled. Can not find it to link it to this job. | .
4356 |  | JE24012110 | 1022 TAUMATA ROAD OMANAWA TAURANGA | Eastern | PYES PA | 2024-05-28 | 9:00 | 2024-05-28 | 15:10 | 0.061299 | 0.00016554 | 60 | 22218 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV overhead conductors between Poles 217089 & 217097. And 217095 & 217099 with 2W Magpie. Remove 11kV ABS Temp022. | .
4357 |  | JE24012147 | 246 LONGBUSH ROAD HINAKURA MASTERTON | Western | COLOGNE ST | 2024-05-28 | 8:46 | 2024-05-28 | 14:22 | 0.040906 | 0.00012139 | 44 | 14827 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles hardware and resag 11kv lines past fuses 7383 | .
4358 |  | JE24012467 | 129 BURMA HILL ROAD RANGIWAEA WANGANUI | Western | PARAPARA | 2024-05-28 | 9:16 | 2024-05-28 | 16:21 | 0.018747 | 4.4143e-05 | 16 | 6795 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 2x poles 785237 & 785236. Remove TX X2254 and associated Xarms. | .
4359 |  | JE24013142 | 2198 SOUTH ROAD OKATO NEW PLYMOUTH | Western | INLAND COAST | 2024-05-28 | 9:31 | 2024-05-28 | 15:00 | 0.015438 | 4.6902e-05 | 17 | 5596 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Site 1: To install Travida recloser 12725 and replace pole 466560 | .
4360 |  | JE24015484 | 368 IRONWORKS ROAD HUNTERVILLE HUNTERVILLE | Western | HUNTERVILLE 22KV | 2024-05-28 | 8:45 | 2024-05-28 | 14:00 | 0.021711 | 6.8974e-05 | 25 | 7869 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 807659. Replace X-arms 807644, 807648, 807651, 807654, 807655, 807656. Replace Pole 807652 & Install new 30kVA TX (6593W) and replace pole 807660 & install new 30kVA Tx (6595W). Replace pole 807657 and remove Tx X262. Remove existing LV from poles 807652 to 807660 | .
4361 |  | JE24017078 | 62 PAHAUTEA ROAD KAHUTARA FEATHERSTON (DOWNER), 45 MURPHYS LINE FEATHERSTON ( POLTECH) | Western | SOUTH FEATHERSTON | 2024-05-28 | 8:31 | 2024-05-28 | 13:57 | 0.054966 | 0.0001683 | 61 | 19923 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Downer: Carry out 33kv ABS Maintenance on 3350,3139/1, 3140, S567, S568, S572, S1200,3141/1. Poltech: Replace existing pole 799982 with new 11m transformer structure and new 30KVA 3ph transformerT4690. | .
4362 |  | JE24018666 | STANLEY AVE | Eastern | STANLEY AVE | 2024-05-28 | 2:07 | 2024-05-31 | 11:10 | 0.15983 | 0.00060697 | 110 | 57933 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Fused/Sw FC711 Protection flags (nil where none): Fuses blown CAUSE: Insulation breakdown (deterioration) Location: HV Cable between Fused/Sw FC711 to Transformer TC4030 Temp generation (state details when used): Yes, Advisories selected: Generator connected at TX TP1029 at 09:50 Generator connected at TX TC4030 at 10:20 PERFORMANCE DETAIL DNO (number or state No): Yes 2405026 Circuit patrolled and type: Yes Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? Yes Additional fault restoration comments: Found Fused/Sw 711 Open after a No Power call. Replaced blown Fuses (3 x 31.5 Amp HRC Fuses ) under AP 8666-1 1st Attempt to Close Fused/Sw 711 at 05:47 and Fuses operated indicating a permanent fault. Under AP 8666-2 LV Breaks were made at Transformers TP1029 & TC4030 and then Generators at both Transformers were connected. (See times above) HV Cable is currently being disconnected from Fused/Sw 711 under AP 8666-2 and then a Test Permit will be taken to Test the HV Cable. Under Test Permit 8666-3 HV Cable fault was located. Both Transformer's will remain on Generator's until further notice. eMap & SCADA tile has been updated - BR SHARON advised Power is still flickering as the power is cutting off to the fascillaty. | .
4363 |  | JE24018743 | KIWITAHI | Eastern | KIWITAHI | 2024-05-28 | 15:34 | 2024-05-28 | 17:05 | 0.00025322 | 2.759e-06 | 1 | 92 | Unplanned | WILDLIFE - BIRD | Fuses Location: FP1119 No. Fuses: 2 Fuse Amp Size: 6 Amp TIME CLOSED: 17:05 Cause: Bird strike Weather (wind/rain): Calm Follow up required (select advisory)? No | .
4364 |  | JE24018750 | LEEDSTOWN 22KV | Western | LEEDSTOWN 22KV | 2024-05-28 | 15:54 | 2024-05-28 | 15:57 | 0.0016863 | 0.00052972 | 192 | 611 | Unplanned | THIRD PARTY INTERFERENCE - OVERHEAD CONTACT | REGULATORY INFORMATION Voltage & Device ID: 22kV CB1133 Protection flags (nil where none): C Phase O/C & E/F CAUSE: Excavator Hit Lines at New Pukepapa Substation worksite Location: New Pukepapa Substation worksite Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: No Glen Most rung in and reported incident & stated no Network Damage Weather (wind/rain): Fine LFI (Y/N + Comments): Nil Follow up Required (select advisory)? No Additional fault restoration comments: Safety Observer ? No CAC | .
4365 |  | JE24018758 | CLIMIE RD | Western | CLIMIE RD | 2024-05-28 | 17:03 | 2024-05-28 | 18:18 | 0.11514 | 0.001534 | 556 | 41734 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 33kV REC 3545 Protection flags (nil where none): A phase OC EF CAUSE: Blown insulator on Recloser 3545 Location: Recloser 3545 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): 2405024 Circuit patrolled and type: cursory Weather (wind/rain): fine LFI (Y/N + Comments): N Follow up Required (select advisory)? Additional fault restoration comments: One of the insulators on ABS 365 at CAR Sub looks defective. Crew will need a bucket truck to do a high level inspection before operating to energise the line SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Cardiff Circuit that tripped: Cardiff DTF (KM): N/A | .
4366 |  | JE24018760 | MOUNTAIN RD | Western | MOUNTAIN RD | 2024-05-28 | 17:20 | 2024-05-28 | 21:22 | 0.030622 | 0.00033108 | 107 | 11099 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11KV Rec12535 Protection flags (nil where none): B & C Phase O/C CAUSE: Blown Insulators Location: Pole 763140 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Wind & Rain LFI (Y/N + Comments): No Follow up Required (select advisory)? Additional fault restoration comments: Replaced 3 X Insulators and 1x crossarm Restored from initial trip, then saw an insulator glowing, isolated from Fuses 5547 to repair. | .
4367 |  | JE24018761 | KAIPI RD | Western | KAIPI RD | 2024-05-28 | 17:27 | 2024-05-28 | 20:55 | 0.09792 | 0.0013795 | 405 | 35492 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11KV CB6 Protection flags (nil where none): B Phase E/F CAUSE: Blown Insulator Location: Pole 747504 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Wind & Rain LFI (Y/N + Comments): Yes but not flashing Follow up Required (select advisory)? Additional fault restoration comments: Isolated at Links 12184 & 12025/4 And ABS 166 Back feed in At ABS 373 & Switch Gear 12026/3 replaced 1 X Pin & Insulator at Pole 747504 | .
4368 |  | JE24018783 | OPUNAKE | Western | OPUNAKE | 2024-05-28 | 23:22 | 2024-05-29 | 7:28 | 0.21288 | 0.0021382 | 775 | 77160 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Car v pole - Opened CB TA2 For safety Fire said pole about to fall over Feeder did not Trip Isolated at ABS TA206 ABS TA223 & TA112 Back feed put in at ABS 6681 Reliven Rest of Feeder from CB TA2 Replaced Pole Complete with Crossarms ETC Relivened HV with a small section of LV still to restore NDR to follow | .
4369 |  | JE24019829 | KETEMARAE RD | Western | KETEMARAE RD | 2024-05-28 | 9:51 | 2024-05-28 | 11:51 | 0.00066031 | 5.5179e-06 | 2 | 239 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation from W5323 TX fuses. Replaced 3 x Lightning Arrestors, 2 x Fuse Barrels & 3x3A Fuses at transformer W5323 Related to JE24018680 single phase outage from Fuses WH806 | .
4370 |  | JE24015558 | 50 CARDIFF ROAD CARDIFF STRATFORD | Western | CARDIFF RD | 2024-05-27 | 9:46 | 2024-05-27 | 18:20 | 0.092087 | 0.00017933 | 65 | 33378 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace pole 737608 and install new 33kv recloser 3545 & remove ABS 366 commissioning will be happening during the shutdown there will be no WA required as we intend on Workshop commisioning prior to outages | .
4371 |  | JE24015855 | 108 KAIWHAIKI ROAD KAIWHAIKI WANGANUI | Western | MAKIRIKIRI | 2024-05-27 | 9:07 | 2024-05-27 | 16:01 | 0.16574 | 0.00040005 | 145 | 60075 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace multiple 11KV Defected poles & X-Arms & Tree Cutting between poles 784800 & 784737 | .
4372 |  | JE24018505 | BRUNSWICK | Western | BRUNSWICK | 2024-05-27 | 4:32 | 2024-05-27 | 7:51 | 0.064222 | 0.00097667 | 354 | 23278 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 6 Protection flags (nil where none): A ph E/F CAUSE: Insulator Location: 782211 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: cursory Weather (wind/rain): calm LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Line was isolated at ABS's 1025, 1107 & Fuses 608 to replace insulator | .
4373 |  | JE24018511 | WAITUNA | Western | WAITUNA | 2024-05-27 | 5:55 | 2024-05-27 | 10:49 | 0.10757 | 0.0018926 | 686 | 38990 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: CB 7 Protection flags (nil where none): E/F CAUSE: 2 Lines Down due to Faulty insulator Location: pole P08658 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Fine LFI (Y/N + Comments): Nil Follow up Required (select advisory)? No Additional fault restoration comments: Crossarm replaced as a hole burnt into it. | .
4374 |  | JE24018520 | APITI | Western | APITI | 2024-05-27 | 8:12 | 2024-05-27 | 13:08 | 0.072182 | 0.00074768 | 271 | 26163 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 10002 Protection flags (nil where none): A O/C, E/F CAUSE: Faulty insulator Location: P03571 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Fine LFI (Y/N + Comments): Rec P61 Follow up Required (select advisory)? Additional fault restoration comments: Rec P61 LFI's activated but Rec P61 didn't record anything. Fault past ABS P54. | .
4375 |  | JE24018527 | LEPPERTON | Western | LEPPERTON | 2024-05-27 | 8:42 | 2024-05-27 | 10:09 | 0.0014437 | 1.6554e-05 | 6 | 523 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 8160 No. Fuses: 2 Fuse Amp Size: 3 amp TIME CLOSED: 10:08 Cause: Unknown Weather (wind/rain): Wind Follow up required (select advisory)? No | .
4376 |  | JE24018540 | COONOOR | Western | COONOOR | 2024-05-27 | 9:53 | 2024-05-27 | 14:16 | 0.0058027 | 2.2072e-05 | 8 | 2103 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Truck versus Pole Isolated at Fuses T44 to allow repairs Pole P419174 broken, Fuses at T44 had blown on arrival | .
4377 |  | JE24018633 | MOUNT BRUCE | Western | MOUNT BRUCE | 2024-05-27 | 15:53 | 2024-05-27 | 17:00 | 0.00036992 | 5.5179e-06 | 2 | 134 | Unplanned | WILDLIFE - OTHER | Fuses Location: 7960 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 17:00 Cause: stock rubbing against pole causing line clash Weather (wind/rain): Fine Follow up required (select advisory)? No | .
4378 |  | JE24018643 | APITI | Western | APITI | 2024-05-27 | 16:46 | 2024-05-27 | 19:27 | 0.04989 | 0.00074768 | 271 | 18083 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 10002 Protection flags (nil where none): A O/C, E/F CAUSE: Blown Insulator Location: Pole P03573 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments :Repaired line at Pole due to Burning | .
4379 |  | JE24018416 | ROADS | Eastern | ROADS | 2024-05-26 | 1:40 | 2024-05-26 | 7:26 | 0.13789 | 0.00069526 | 252 | 49980 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: Recloser 9146 Protection flags (nil where none): Ph A O/C CAUSE: lines down due to trees Location: Pole 223752 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4380 |  | JE24018421 | MOAWHANGO | Western | MOAWHANGO | 2024-05-26 | 6:46 | 2024-05-26 | 13:08 | 0.046511 | 0.00036418 | 61 | 16858 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11KV Rec4230 Protection flags (nil where none): E/F CAUSE: Floating Conductor Location: Pole 371846 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Wind & Rain LFI (Y/N + Comments): Yes But was over 2 Hours until they got there Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4381 |  | JE24018430 | COLVILLE | Eastern | COLVILLE | 2024-05-26 | 9:39 | 2024-05-29 | 13:35 | 0.0024323 | 2.759e-05 | 5 | 882 | Unplanned | VEGETATION - OUTSIDE ZONE | LV lines down HV fuses At TC1454 removed & re-instated after cutting LV line break at pole 389983 A tree that has been poisoned snapped off and went through the LV lines bringing them down & making one pole on 45 & and another on 30 degree angle Generation is being installed at 3 premises Poles affected V 13297 851118, 316971 & 389933 Generators installed at 1459, 1473 & 1479 Port Charles Rd at 17:30 27/05/24 - 1476, 1447C Port Charles Road - Left off due to nobody home for acces, Retailers informed 1451 Port Charles Road - Emailed AI team for support finding correct ICP for address so we can inform their retailer. 28/05/2024 - Customer from number 1447C has called up, not happy with the delay in having power back on. This is a batch and she has food in the freezer and have a client arriving today that will require power. Have spoken to Andrew King. Trees is still being cleared, lines to be reinstated tomorrow. Have called and advised the customer of this, she will try sort things with her client, but is not happy at all. MDP 29/05/2024 All LV Lines have been repaired and Generators have been removed. HV supply was restored on 26/05, but ICPs still had an LV outage, another short HV outage on 29/05 to finalise repairs and remove gen. | .
4382 |  | JE24018431 | TAWHITI RD | Western | TAWHITI RD | 2024-05-26 | 8:07 | 2024-05-26 | 10:55 | 0.0051036 | 4.1384e-05 | 15 | 1850 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Found 2 Blown Fuse at CA 405 at 08:50 Found 3 Blown Fuses at CA 432 at 09:31 Relived CA405 2X 8 Amp At 09:54 Protlled line and Found Nothing Reliven CA432 3X6 Amp at 10:55 Very windy | .
4383 |  | JE24018459 | FERTILISER WORKS | Eastern | FERTILISER WORKS | 2024-05-26 | 11:45 | 2024-05-26 | 11:49 | 1.1036e-05 | 2.759e-06 | 1 | 4 | Unplanned | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | Triton CB tripped with no SCADA alarms tripped via Ballance Gen intertrip Closed CB with Ballance on line | .
4384 |  | JE24018468 | AUROA | Western | AUROA | 2024-05-26 | 14:04 | 2024-05-26 | 16:26 | 0.00078171 | 5.5179e-06 | 2 | 283 | Unplanned | VEGETATION - OUTSIDE ZONE | Isolated at Fuses 6223 Tree hit lines Cut trees and pulled up conductors | .
4385 |  | JE24018474 | BRUNSWICK | Western | BRUNSWICK | 2024-05-26 | 14:09 | 2024-05-26 | 15:15 | 0.00036412 | 5.5179e-06 | 2 | 132 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: 2882 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 15:15 Cause: Wind Weather (wind/rain): Wind Follow up required (select advisory)? | .
4386 |  | JE24018476 | WAITARA RD | Western | WAITARA RD | 2024-05-26 | 14:22 | 2024-05-26 | 17:45 | 0.040063 | 0.0003697 | 134 | 14521 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Sec12235 Protection flags (nil where none): C Phase E/F O/C CAUSE: Lines down - broken insulator Location: Pole 745020 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Wind LFI (Y/N + Comments): No Follow up Required (select advisory)? Additional fault restoration comments :Replace Complete Crossarm as it was not in good state | .
4387 |  | JE24018490 | JUNCTION RD | Western | JUNCTION RD | 2024-05-26 | 21:13 | 2024-05-26 | 22:46 | 0.0094119 | 0.00010208 | 37 | 3411 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Faultman found a line down at pole 747018 due to the wind, line was isolated at ABS's 299 & 548 to repair the lines. | .
4388 |  | JE24018493 | KEENAN RD | Eastern | KEENAN RD | 2024-05-26 | 19:48 | 2024-05-26 | 20:23 | 0.0073253 | 0.00021244 | 77 | 2655 | Unplanned | THIRD PARTY INTERFERENCE - OVERHEAD CONTACT | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 14447/2 Protection flags (nil where none): E/F, O/C. CAUSE: Human error - third party OH contact Location: Intersection of SH 29 & Belk Rd Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4 / Not patrolled Weather (wind/rain): Windy LFI (Y/N + Comments): No activation Follow up Required (select advisory)? NDR to follow Additional fault restoration comments: Intersection of SH29 and Belk Rd contractor lifted a lighting tower and broke clearance to the lines. Mast lowered and lines inspected. No damage caused. | .
4389 |  | JE24018350 | 1403A 1, MARTON, MARTON, 4787 | Western | LEEDSTOWN 22KV | 2024-05-25 | 2:36 | 2024-05-25 | 7:31 | 0.018809 | 0.00020968 | 76 | 6818 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Car V Pole at 1403 State Highway 1, Marton F3982299 Isolate between ABS 16085 and ABS 796 to replace Pole 460165 No Tripping No Flags Backfeed in at MABS 539 Replaced 1 X Pole complete | .
4390 |  | JE24018391 | IRIRANGI | Western | IRIRANGI | 2024-05-25 | 16:44 | 2024-05-25 | 20:23 | 0.079757 | 0.00092701 | 188 | 28908 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | REGULATORY INFORMATION Voltage & Device ID: 11kV Recloser 142 Protection flags (nil where none): A & B Phase ???? CAUSE: small branch on line Location: 785656 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: op Weather (wind/rain): wind, rain LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: branch removed with hotstick, full power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4391 |  | JE24018396 | 964 SOUTH ROAD, HAWERA | Western | MANAWAPOU RD | 2024-05-25 | 19:10 | 2024-05-25 | 20:04 | 0.0053419 | 9.9323e-05 | 36 | 1936 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Faulty joint/Jumper at Pole 728364 Back feed put in place Isolated at ABS WH106, WH108 & Links 12290/4 Jumper/joint replaced, full power restored | .
4392 |  | JE24018408 | LINDERMANN RD | Eastern | LINDERMANN RD | 2024-05-25 | 20:24 | 2024-05-25 | 21:26 | 0.067382 | 0.001316 | 477 | 24423 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | REGULATORY INFORMATION Voltage & Device ID: GMCB 13021/3 Protection flags (nil where none): Ph BC O/C CAUSE: Branch on lines Location: Pole 204645 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y + Comments): Follow up Required (select advisory)? No Additional fault restoration comments: Removed branch with Hot Stick & restored power OPENED GMCB 13021/3 FOR 23 SECONDS TO CLOSE ABS 14274. (Requested by Field Switcher for safety) | .
4393 |  | JE24015637 | 333 HARBOUR DRIVE EAST MATARANGI WHITIANGA | Eastern | OWERA RD | 2024-05-24 | 9:50 | 2024-05-24 | 10:05 | 0.0019037 | 0.00012691 | 46 | 690 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Tap change TP1583 down one tap due to PV issues Transformer voltages L - N before tapping (Tap 4) R Ø - 247V W Ø - 248V B Ø - 243V After tapping ( Tap 3) R Ø - 240V W Ø - 240V B Ø - 239V At 118 Taupata Way - @ mains 239V, Service fuses 240V At 333 Harbour Drive - @ mains 241V, Service fuses 239V | .
4394 |  | JE24015640 | 159 RANGIORA CRESCENT MATARANGI WHITIANGA | Eastern | OWERA RD | 2024-05-24 | 11:45 | 2024-05-24 | 12:03 | 0.0045731 | 0.00025382 | 92 | 1658 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Tap change TP1584 down one tap due to PV issues Before tapping (Tap 4) R Ø - 244V, B Ø - 244V, W Ø - 243V After tapping (Tap 3) R Ø - 237V, B Ø - 238V, W Ø - 238V | .
4395 |  | JE24015871 | 17 TE ARAKURA ROAD FEILDING FEILDING | Western | TE ARAKURA | 2024-05-24 | 10:56 | 2024-05-24 | 12:43 | 0.016522 | 0.0001545 | 56 | 5989 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Secionalizer 10249-2 Maintenance | .
4396 |  | JE24017666 | 1507 OPAKI KAIPARORO ROAD MAURICEVILLE MASTERTON | Western | IHURAUA | 2024-05-24 | 10:30 | 2024-05-24 | 14:09 | 0.024105 | 0.00011036 | 40 | 8737 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To repair and restring 11kv conductor between poles P15828 and 374789 after being brought down by trees. | .
4397 |  | JE24017682 | 133 CENTRAL ROAD NORTH WAITAKARURU THAMES | Eastern | MANGATARATA | 2024-05-24 | 9:33 | 2024-05-24 | 12:48 | 0.00053749 | 2.759e-06 | 1 | 195 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV G/M Transformer TP1994 | .
4398 |  | JE24018239 | GORDON ST | Western | GORDON ST | 2024-05-24 | 8:30 | 2024-05-24 | 14:50 | 0.0010487 | 2.759e-06 | 1 | 380 | Unplanned | OTHER | Customer is part of HV NAPA 110724, they are supplied by T1971. LV open point at pole 862298. Notified AI team to update TX Attended by Thomas Wilson, not on site due to system issues | .
4399 |  | JE24018274 | KIWITAHI | Eastern | KIWITAHI | 2024-05-24 | 12:02 | 2024-05-24 | 13:38 | 0.00053101 | 5.5179e-06 | 2 | 192 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: FC2318 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 13:38 Cause: Unknown Weather (wind/rain): Fine Follow up required (select advisory)?N | .
4400 |  | JE24018281 | TE POI | Eastern | TE POI | 2024-05-24 | 12:45 | 2024-05-24 | 14:20 | 0.00026199 | 2.759e-06 | 1 | 95 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: FC786 No. Fuses: 2 Fuse Amp Size: 2 Amp TIME CLOSED: 14:20hrs Cause: Unk Weather (wind/rain): Calm Follow up required (select advisory)? | .
4401 |  | JE24018296 | CLOTON RD SOUTH | Western | CLOTON RD SOUTH | 2024-05-24 | 15:02 | 2024-05-24 | 15:59 | 0.00093052 | 1.6554e-05 | 6 | 337 | Unplanned | THIRD PARTY INTERFERENCE - TREES | Fuses Location: 6243 No. Fuses: 2 Fuse Amp Size: 8 Amp TIME CLOSED: 15:58 Cause: Customer cutting trees. Tree fell and brushed HV lines on way down causing them to clash and blow fuses at Pole 740027. Weather (wind/rain): Calm Follow up required (select advisory)? NDR to follow | .
4402 |  | JE24018329 | BEACH RD WAIHI BEACH | Eastern | BEACH RD WAIHI BEACH | 2024-05-24 | 18:30 | 2024-05-24 | 20:59 | 0.0061108 | 4.1384e-05 | 15 | 2215 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: FABS IC292 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 20:58 Cause: WIND Weather (wind/rain): WINDY Follow up required (select advisory)? NO | .
4403 |  | JE24018344 | KAIHERE | Eastern | KAIHERE | 2024-05-24 | 20:22 | 2024-05-24 | 21:41 | 0.0030439 | 3.8625e-05 | 14 | 1103 | Unplanned | WILDLIFE - BIRD | Please check to make sure JE24018345 is fed from this TX. 165 Puhunga Island Road Fuses Location: Fuses FC823 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 21:40 Cause: Bird strike Weather (wind/rain): Calm Follow up required (select advisory)? No | .
4404 |  | JE24018347 | MOUNT BRUCE | Western | MOUNT BRUCE | 2024-05-24 | 21:05 | 2024-05-24 | 23:23 | 0.027359 | 0.00019865 | 72 | 9916 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: Recloser C223 Protection flags (nil where none): EF, Phase B Fault CAUSE: Bird Strike -Lines Down Location: Pole 834244 Temp generation (state details when used): One conductor on the deck, restringed..Power restored 23:23Hrs PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4405 |  | JE24012447 | 100 WHAKARUA ROAD HINAKURA MASTERTON | Western | COLOGNE ST | 2024-05-23 | 9:25 | 2024-05-23 | 13:10 | 0.0099735 | 4.4143e-05 | 16 | 3615 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles and hardware past fuses 7379 Poles 817122,817140,817138,817119,817118 and 377586 to be worked on Job was started late as Downer had a big safety meeting after incident in P/North. and had problems with comms in the area. | .
4406 |  | JE24012451 | 172 MANGAREWA ROAD RAETIHI OHAKUNE | Western | RAETIHI | 2024-05-23 | 9:20 | 2024-05-23 | 14:56 | 0.0018554 | 5.5179e-06 | 2 | 673 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Transformer X4044 and LV Xarms. Also upgrade earthing. | .
4407 |  | JE24012455 | 175 POREWA ROAD MARTON MARTON | Western | PUTORINO | 2024-05-23 | 9:17 | 2024-05-23 | 14:37 | 0.0079479 | 2.4831e-05 | 9 | 2881 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace TX Pole X2850 - 805759 | .
4408 |  | JE24015315 | 68 Ranginui Road Welcome bay | Eastern | WELCOME BAY | 2024-05-23 | 8:59 | 2024-05-23 | 17:29 | 0.22925 | 0.00045247 | 164 | 83093 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Poles 215409 and 215410, Reconductor from Pole 268846 to pole 215410.Install new links 14832 at Pole 215409 and remove 11KV fuses SD4-155. Install new switch gear 14849 with new 3C 300mm cable to new links 14832. Cut and cup cable at Transformer TD4-536 from 11KV Link box SD4-174 and install new 3C 185mm cable from 14849-2 to Transformer TD4-536. Remove Link box SD4-174 and existing cables | .
4409 |  | JE24015578 | 142 TREMAINE AVENUE WESTBROOK PALMERSTON NORTH | Western | TREMAINE AVE | 2024-05-23 | 3:16 | 2024-05-23 | 4:28 | 0.059776 | 0.00081941 | 297 | 21666 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Magnefix maintenance 199, 200, 201 | .
4410 |  | JE24016169 | 187 main st, 12 cook st, 50 cook st, 278 church street Palmerston North | Western | THE SQUARE | 2024-05-23 | 23:07 | 2024-05-24 | 0:15 | 0.010919 | 0.00016002 | 58 | 3958 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Magnefix maintenance G9, G133, G149, G236 Switching started, power off, work cancelled due to outage affecting traffic lights on state hwy and numerous customer complaints about no notification. | .
4411 |  | JE24016671 | 45A HEATH ROAD WAIHI WAIHI | Eastern | WAIHI-WHANGAMATA 33KV | 2024-05-23 | 7:01 | 2024-05-23 | 19:30 | 3.9908 | 0.010705 | 3118 | 1446492 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles WHIWHM004, P13757, WHIWGM006, 853594, 853598, R13096 . Downer to repair defect pole WHIWGM124 & WHIWGM125 . Temp generation installed on TC4848 - Outside work area . Temp generation installed on TP3928 ( Golf Club - 1 ICP ) - Outside work area . See linked related job for details of associated unplanned event due to BESS/battery failing after planned outage was underway. | .
4412 |  | JE24017193 | 1310 WAIHI VALLEY ROAD PONGAROA PONGAROA | Western | HOROEKA | 2024-05-23 | 9:48 | 2024-05-23 | 12:07 | 0.026025 | 0.00018761 | 68 | 9433 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace pole P06283. | .
4413 |  | JE24018028 | COLOGNE ST | Western | COLOGNE ST | 2024-05-23 | 2:26 | 2024-05-23 | 4:55 | 0.0065881 | 4.4143e-05 | 16 | 2388 | Unplanned | WILDLIFE - BIRD | Fuses Location: 7379 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 04:55 Cause: Duck Weather (wind/rain): Windy Follow up required (select advisory)? | .
4414 |  | JE24018030 | OMO Sub - CB 6 Fuse/ Sw_13900/2 | Eastern | PLUMMERS POINT | 2024-05-23 | 9:21 | 2024-05-23 | 9:33 | 0.00024161 | 1.9313e-05 | 7 | 88 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: Fuse/Sw 13900/2 Protection flags (nil where none): None CAUSE: Location: Trees brushing onto lines Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? No Additional fault restoration comments: Repalced 3 x 6.3 A 11kV Fuses in Sw/Gear 13900/2. Power Restored 09:33 Customer advised to get arborists and trim down trees SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4415 |  | JE24018033 | HETHERINGTON RD | Eastern | HETHERINGTON RD | 2024-05-23 | 6:25 | 2024-05-23 | 18:27 | 0.57131 | 0.014049 | 2586 | 207076 | Unplanned | HUMAN ERROR - LOAD SHEDDING - NETWORK LOAD | Multiple trips/BESS failures during planned outage NAPA 109958. BESS could not support load, so multiple outages throughout the planned switching process. Initially the planned switching was to have the Battery & generation running together which Raises the protection setting on CB 1122 to 201amps & would have supported both CB 11 & CB 5. Battery & Generator could not be run together, the setting on CB 1122 was 100 amps. CB 11 & 5 were supported by Generation only for the plannned outage. The first unplanned outage for CB 11 & 5 was caused from the load going over 100amps momentarily. Beyond sect 13503 was left off & patrolled as there were flags from this device at the time of the fault. Next unplanned outage was from the evening peak due to the shutdown running over time. CB 11 was restored after the tripping & part of CB 5 only. | .
4416 |  | JE24018037 | OKAIAWA | Western | OKAIAWA | 2024-05-23 | 9:15 | 2024-05-23 | 13:35 | 0.021535 | 8.2769e-05 | 30 | 7806 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV, CB 7 (Auto reclosing only) Protection flags (nil where none): E/F, B phase CAUSE: Insulator shorting to pole Location: 721439 Isolation: ABS MA411 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Yes / Operational Weather (wind/rain): Calm / Light Rain LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: 11kV Crossarm & all hardware replaced Isolation from ABS MA411 and Sec 12436 | .
4417 |  | JE24018042 | PUT Sub - CB 7 - REC 13232 | Eastern | LICHFIELD | 2024-05-23 | 6:38 | 2024-05-23 | 9:32 | 0.035922 | 0.0002759 | 100 | 13020 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV, Rec 13232 Protection flags (nil where none): o/C C phase CAUSE: Unk Location: Unk Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Yes / Cursory Weather (wind/rain): Calm / Light Rain LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4418 |  | JE24018081 | PUKETIRO | Western | PUKETIRO | 2024-05-23 | 9:13 | 2024-05-23 | 10:41 | 0.0079316 | 9.1046e-05 | 33 | 2875 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses 7639 - Replace Fuses for correct size - assign Thomas Wilson Faultman replaced Fuses 7639 to 50 amps to the correct fuse size. As had 1x 50 amp, 1x 30 amp & 1 x20 amp. Incorrect fuse sizes were found after attending a part power job last week. | .
4419 |  | JE24018091 | PRINCESS ST | Western | PRINCESS ST | 2024-05-23 | 9:48 | 2024-05-23 | 9:57 | 0.020187 | 0.002083 | 755 | 7317 | Unplanned | HUMAN ERROR - POTENTIAL SWITCHING ERROR | Power was lost during switching for planned outage under NAPA 110813. This was because the long term back feed that was in place when the switching was written, had been removed. This was missed by the NOC Operator working the desk, as his morning checks were interrupted by other feeder fault trippings, and were not completed fully. Upon realisation of the outage, Network checks were carried out, and a back feed installed remotely by SCADA via Recloser 12383/2 | .
4420 |  | JE24018112 | RAETIHI | Western | RAETIHI | 2024-05-23 | 10:38 | 2024-05-23 | 17:08 | 0.43376 | 0.0028969 | 1050 | 157218 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 2 Protection flags (nil where none): E/F CAUSE: Tree through lines & lines down Location: pole 776484 & ABS 652 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): N Follow up Required (select advisory)? Additional fault restoration comments: Faultman was advised by customer that there was a tree through the lines, Faultman also found lines down at ABS 652 and at pole 776515, line was isolated at ABS 652. Appears tree may have been purposely cut down, with the culprit then doing a runner. NDR to follow | .
4421 |  | JE24018131 | PAREWANUI | Western | PAREWANUI | 2024-05-23 | 12:34 | 2024-05-23 | 17:02 | 0.002951 | 1.1036e-05 | 4 | 1070 | Unplanned | THIRD PARTY INTERFERENCE - OVERHEAD CONTACT | Location: Tfr X2467 No: Fuses: 3 Size Fuses: 3 amp Time: 17:01 Cause: Digger hit lines. | .
4422 |  | JE24018146 | 295 Roberts Road, Maungatautari, 3494 | Eastern | CAMBRIDGE RD TIRAU | 2024-05-23 | 17:06 | 2024-05-23 | 19:28 | 0.012541 | 8.8287e-05 | 32 | 4546 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV ABS 850 section Protection flags (nil where none): nil CAUSE: Rotten crossarm failed Location: Pole D12673 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Customer rung in low lines job. Isolation from ABS 850. | .
4423 |  | JE24018153 | WAVERLEY | Western | WAVERLEY | 2024-05-23 | 14:33 | 2024-05-23 | 16:43 | 0.000718 | 5.5179e-06 | 2 | 260 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 2630 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 16:43 Cause: Suspect bird strike Weather (wind/rain): wind Follow up required (select advisory)?n | .
4424 |  | JE24018203 | PASCAL ST 12 | Western | PASCAL ST 12 | 2024-05-23 | 23:07 | 2024-05-24 | 0:15 | 0.00018825 | 2.759e-06 | 1 | 68 | Unplanned | OTHER | Customer is part of a planned outage under NAPA 109676 but is listed on the wrong transformer. This customer is actually fed from Transformer G236 Planned outage restored 00:15 24/05/24 | .
4425 |  | JE24012381 | 432 STATE HIGHWAY 1 BULLS BULLS | Western | CROFTON | 2024-05-22 | 9:17 | 2024-05-22 | 12:28 | 0.00052954 | 2.759e-06 | 1 | 192 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace TX Pole 809985/4388W & move site forward one pole to 809984 | .
4426 |  | JE24012417 | 1472 NAPIER ROAD ASHHURST ASHHURST | Western | AOKAUTERE | 2024-05-22 | 8:45 | 2024-05-22 | 15:08 | 0.021125 | 5.5179e-05 | 20 | 7657 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | reconductor 11kv between P01314 and Abs E74 Advised by onsite crew there has been an incident involving a fall from height. | .
4427 |  | JE24014681 | 3 PALAZZO DRIVE PAPAMOA BEACH TAURANGA | Eastern | PALM SPRINGS | 2024-05-22 | 9:01 | 2024-05-22 | 15:04 | 0.29592 | 0.00081389 | 295 | 107257 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install / remove generator at "BestStart" Daycare - pillar 167551 (0630-0700 & 1600-1630). Replace 11Kv coupling and minor corrosion repairs at SD switchgear S6165>6171 (0900-1530) | .
4428 |  | JE24015135 | 61 TANGITERORIA LANE PAUANUI HIKUAI | Eastern | PAUANUI | 2024-05-22 | 8:46 | 2024-05-22 | 18:12 | 0.057864 | 0.0001076 | 38 | 20973 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv overhead conductors between poles 383718 & 382626 . Install surge diverters on pole 382626 Isolation's IC1205 and Links temp 97 | .
4429 |  | JE24015459 | 368 IRONWORKS ROAD HUNTERVILLE HUNTERVILLE | Western | LEEDSTOWN 22KV | 2024-05-22 | 8:46 | 2024-05-22 | 12:51 | 0.016916 | 6.8974e-05 | 25 | 6131 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Stage 2: Replace pole 807630, 807631, 807632, 807633, 807643. Replace X-arms 807629. Upgrade Tx X210 at pole 807633 from 10kVA to 15-11-3, Keeping same asset number. | .
4430 |  | JE24015476 | 8 David Street, 27 Willis Street Palmerston North | Western | PASCAL ST 8 | 2024-05-22 | 23:00 | 2024-05-23 | 1:30 | 0.021106 | 0.00014071 | 51 | 7650 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Magnefix maintenance G188, G37 | .
4431 |  | JE24015849 | Rata Sub, Off Puturino Rd, Hunterville. | Western | ARAHINA 33KV | 2024-05-22 | 8:39 | 2024-05-22 | 13:21 | 0.001556 | 5.5179e-06 | 2 | 564 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Maintenance of 33kv and 11Kv Abs at Rata Sub | .
4432 |  | JE24016635 | 21 DARLINGTON STREET NGATEA NGATEA | Eastern | KAIHERE | 2024-05-22 | 9:01 | 2024-05-22 | 10:49 | 0.012211 | 0.00011312 | 41 | 4426 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Dig up and repair 400volt cable fault out of TC5631 CT 2, which is located in front of Transformer, Note there is No 11kV guard cover | .
4433 |  | JE24017530 | 114 THE DRIVE WHANGAMATA WHANGAMATA | Eastern | OTAHU RD | 2024-05-22 | 9:30 | 2024-05-22 | 16:24 | 0.07815 | 0.00031728 | 115 | 28326 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Switch 9112/3 LV break at TC3697 LV generator installed at TC3697 Replace Switch 9112/3 under AP1 on completion leave switch SW9112/3 in earthed position. Liven switch 9112. Take AP 2 to remove generator and remake LV jumpers and liven TC3697. FUSE SWITCH 9112/3 IS A SEPERATE SINGLE UNIT CONNECTED TO CFC 9112. | .
4434 |  | JE24017860 | PUNGAREHU | Western | PUNGAREHU | 2024-05-22 | 14:07 | 2024-05-22 | 16:10 | 0.01791 | 0.00014623 | 53 | 6492 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Jumper at Transformer 5051 broken. Customer happy for repairs to be done in morning FM organising team to repair under 2R. 2R left open Fuses PU302 could not be opened, jammed shut Isolated at Fuses 5555 DDO's replaced (Fuses PU302), jumper repaired at TFR 5051E, Full power restored | .
4435 |  | JE24017868 | PORTLAND QUAY | Western | PORTLAND QUAY | 2024-05-22 | 0:56 | 2024-05-22 | 2:58 | 0.064763 | 0.00072285 | 262 | 23474 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Blown Jumper found at Pole 842664 Isolated at ABS's LI677, LI672, & LI227. Back Feed installed via ABS LI615 Cause age | .
4436 |  | JE24017871 | PYES PA | Eastern | PYES PA | 2024-05-22 | 0:26 | 2024-05-22 | 3:10 | 0.024504 | 0.00014898 | 54 | 8882 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: SE3-017 line fuses No. Fuses: 2 Fuse Amp Size: 40A TIME CLOSED: 03:10 Cause: unknown Weather (wind/rain): Follow up required (select advisory)? | .
4437 |  | JE24017876 | ELTHAM TOWN NORTH | Western | ELTHAM TOWN NORTH | 2024-05-22 | 3:23 | 2024-05-22 | 8:29 | 0.17222 | 0.0015202 | 415 | 62422 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV ELT R21 Protection flags (nil where none): C Phase Fault & EF CAUSE: broken insulator/burnt up cross arm Location: Pole 732497 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): wind LFI (Y/N + Comments): N/A Follow up Required (select advisory)? n Additional fault restoration comments: Isolated at ABS 6199, 6191 & 6059, cross arm and hardware replaced, full power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4438 |  | JE24017881 | CAMBRIDGE RD TIRAU | Eastern | CAMBRIDGE RD TIRAU | 2024-05-22 | 7:15 | 2024-05-22 | 11:30 | 0.0049127 | 1.9313e-05 | 7 | 1781 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: FP666 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 11:29 Cause: Line patrolled past Fuses FP666, no fault found Weather (wind/rain): Wind, Rain, Lightning Follow up required (select advisory)?n | .
4439 |  | JE24017890 | TE POI | Eastern | TE POI | 2024-05-22 | 14:00 | 2024-05-22 | 17:49 | 0.0018906 | 8.2769e-06 | 3 | 685 | Unplanned | LIGHTNING - LIGHTNING STRIKE | 2R Y - What is the timeframe for repairs? When approved FM are ready to go. 22/05/2024 or 23/05/2024 Additional Info: TX needs to be replaced today Waiting to get termination cables and TX TC5194 Power not yet restored TFR TC5194 has lightning damage Isolated at Fuses FC4192 TFR Replaced, Full power restored 3 x ICP , will liven 2 , 1 is left off. FM has issued a tag /A39410. Can not ID which ICP. The customer will apply for reconnection when all internal faults are repaired. Have not entered into the STR | .
4440 |  | JE24017954 | OLD COACH RD | Eastern | OLD COACH RD | 2024-05-22 | 12:19 | 2024-05-22 | 16:21 | 0.034568 | 0.0003697 | 134 | 12529 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: Recloser 9875 Protection flags (nil where none): EF CAUSE: Lines Down due to vegetation Location: Pole 493926 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): Windy LFI (Y/N + Comments): Yes at Pole 494398 Follow up Required (select advisory)? No Additional fault restoration comments: Cleared lines down, Power restored Fuses FP2114 @ 16:20Hrs SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4441 |  | JE24017983 | HARRIS BLOCK | Eastern | HARRIS BLOCK | 2024-05-22 | 15:33 | 2024-05-22 | 17:11 | 0.00027055 | 2.759e-06 | 1 | 98 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: FC851 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 17:10 Cause: lightning Weather (wind/rain): wind, rain, lightning Follow up required (select advisory)?n Faultman has restored full power to the main switch, but said no power to the meter, unable to get hold of customer | .
4442 |  | JE24017989 | ROTOEHU | Eastern | ROTOEHU | 2024-05-22 | 21:30 | 2024-05-24 | 16:17 | 0.014162 | 5.5179e-06 | 2 | 5133 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: Fuses SF7-020 Protection flags (nil where none): None CAUSE: Trees on lines Location: Pole 228495 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: 23/05/24 Tree removal and pole replacement in progress. Transformer TF7-038 feeds irrigation pump. Farmer Ok with having no power during the time repairs are being done ETR 24/05/24: Lines repaired by NPE under Access Permit and relivened at 16:16 Customer called saying that faultman called him telling him he wont be returning tomorrow 24/05/24. The Line is a private Line so will need to be repaired by the customer using a powerco approved contractor. Advised the customer of this. Customer is not happy but was going to sort this | .
4443 |  | JE24017997 | AUROA | Western | AUROA | 2024-05-22 | 18:39 | 2024-05-22 | 21:28 | 0.0028045 | 1.6554e-05 | 6 | 1017 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Fuses TA804 Protection flags (nil where none): Nil CAUSE: Strong winds Location: Pole 371 269 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Strong winds LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: HV Lines down beyond Fuses TA804 One HV Line was still "'energized" on the ground. Field Switcher carried out switching to make the area safe and Isolated at Fuses TA804. Repairs were made under Access Permit 7997-01 HV Lines were pulled up and repaired. Full Power was restored at 21:28 Field Switcher confirmed that Power has been restored to all the Transformers. | .
4444 |  | JE24018012 | OHAKEA | Western | OHAKEA | 2024-05-22 | 20:22 | 2024-05-22 | 22:40 | 0.080183 | 0.0021492 | 779 | 29063 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV SAN CB9 Protection flags (nil where none): E/F , Neutral , B Ø O/C CAUSE: Unknown Location: Unknown Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Rain LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: HV Feeder fault - Field crew dispatched. REC 10748/2 was opened and then a back feed was put in place via REC L10/2 from SAN6. Field Switcher busy with a Line Patrol. Line Patrol was carried out from SAN S/S CB9 up to REC 10748/2 and nothing abnormal was found. Network was restored section by section and Full Power was restored at 22:40 No fault found. | .
4445 |  | JE24018014 | PUKETIRO | Western | PUKETIRO | 2024-05-22 | 20:43 | 2024-05-22 | 22:30 | 0.0097587 | 9.1046e-05 | 33 | 3537 | Unplanned | WILDLIFE - BIRD | Fuses Location: 7639 No. Fuses: 3 Fuse Amp Size: 50 Amp TIME CLOSED: 22:30 Cause: Duck Strike Weather (wind/rain): Calm Light Rain Follow up required (select advisory)? No | .
4446 |  | JE24012359 | 524 STATE HIGHWAY 3 KAITOKE WANGANUI | Western | UNION LINE | 2024-05-21 | 9:01 | 2024-05-21 | 14:12 | 0.08725 | 0.00028417 | 103 | 31624 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 793204, and X arms on poles 793205, 793086, 793066 | .
4447 |  | JE24015445 | 61 TANGITERORIA LANE PAUANUI HIKUAI | Eastern | PAUANUI | 2024-05-21 | 9:03 | 2024-05-21 | 15:09 | 0.037432 | 0.0001076 | 38 | 13567 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv pole 248654 and ABS IC2138. Isolation's IC1205 and Links temp 97 | .
4448 |  | JE24015461 | 18 Chaytor Street, 84 Linton Street, 150 Park Road Palmerston North | Western | FITZHERBERT AVE | 2024-05-21 | 23:00 | 2024-05-22 | 4:42 | 0.096631 | 0.00066767 | 242 | 35025 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Magnefix maintenance G63, G64, G80 | .
4449 |  | JE24017561 | WAIHI NORTH | Eastern | WAIHI NORTH | 2024-05-21 | 0:03 | 2024-05-21 | 9:06 | 0.12293 | 0.00022623 | 82 | 44558 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | 11kV sectionaliser 1377 tripped on EF, Rec 9604 A/R partial patrol of FC 2344 patrol of Golden Valley Road up until area of road closure, faultman then called off for safety due to fog and to attend Waihi CB 10 fault Tree Branches & vine removed from Transformer TC4822 using hot stick in daylight hours. Weather: Heavy Rain / Windy | .
4450 |  | JE24017564 | MATAKANA RD | Eastern | MATAKANA RD | 2024-05-21 | 0:21 | 2024-05-21 | 19:35 | 0.19354 | 0.00025382 | 92 | 70149 | Unplanned | VEGETATION - OUTSIDE ZONE | Fault Isolated by 11kV sectionaliser 13216 Fault passage indicators AT ABS SC3-008 indicating on 2 phases Pole 202008 Sectionaliser 13216 Protection A B & C phase OC Line down tree had taken out pole, not able to get team out for repairs until first ferry crossing TX TC3-008 broken LV pole, repaired and restored in the afternoon | .
4451 |  | JE24017570 | OLD TAURANGA RD | Eastern | OLD TAURANGA RD | 2024-05-21 | 0:39 | 2024-05-21 | 13:47 | 0.21576 | 0.00073113 | 265 | 78203 | Unplanned | VEGETATION - INSIDE ZONE | Voltage & Device ID: Waihi CB10 Protection flags (nil where none): A & B phase & EF Weather (wind/rain): wind rain possibly lightning Follow up required (select advisory): LFI Activation: Y/N Yes IC247 Pole P12399 2 phase lit up 11kV recloser 14703 & sectionaliser 13005 both tripped to lock out while WHI CB 10 cycled Sectionaliser 13005 was manually reclosed & Recloser 14705 was closed after ABS IC247 was opened by field staff. Location: Between Poles 493516-494290 Cause: Broken tree branch sitting on lines and bought line down. Isolations: IC247, IC1223, IC200 Back Fed: Via ABS IC233 NDR: To follow NOTE: Links 14901 were also installed during shutdown, as trees which caused outage are a known problem spot. | .
4452 |  | JE24017571 | TIROHIA-KARANGAHAKE | Eastern | TIROHIA-KARANGAHAKE | 2024-05-21 | 0:37 | 2024-05-21 | 4:36 | 0.058142 | 0.0011698 | 424 | 21074 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV POA CB 3 Protection flags (nil where none): CAUSE: B & C OC Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: cursory Weather (wind/rain): wind & rain LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: LFI @ ABS IC505 lit up on 3 phases pole 876695 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): trip of POA CB 3 B & C phase OC LFI activated at Pole 876695 on 2 phases ABR scheme opened and back fed past recloser 13420 via recloser 13699 Recloser RC 33 tripped via ABR but scheme is needs work in works under NAPA , manual close of recloser 9953 to back feed up to REC RC33 | .
4453 |  | JE24017575 | KAITEMAKO RD | Eastern | KAITEMAKO RD | 2024-05-21 | 1:15 | 2024-05-21 | 9:10 | 0.017878 | 4.1384e-05 | 15 | 6480 | Unplanned | VEGETATION - INSIDE ZONE | Fuses Location: Fuses SD4-444 No. Fuses: 2 Fuse Amp Size: 10 Amps TIME CLOSED: 09:09 Cause: Tree branches touched the line. Weather (wind/rain): Wind & Rain. Follow up required (select advisory)? No | .
4454 |  | JE24017579 | SPRINGDALE | Eastern | SPRINGDALE | 2024-05-21 | 2:52 | 2024-05-21 | 5:35 | 0.0009038 | 5.5179e-06 | 2 | 328 | Unplanned | VEGETATION - INSIDE ZONE | 11kV Fuses FC4233 2 blown on arrival, tree on fire when faultman arrived pulled remaining fuse *take first call time Isolated @ Fuses FC4223 , engaged tree cutters to clear trees back from line 2x6A Fuses replaced 0535 | .
4455 |  | JE24017583 | RUAPEHU | Western | RUAPEHU | 2024-05-21 | 3:55 | 2024-05-21 | 5:20 | 0.081091 | 0.0010429 | 378 | 29392 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: CB 6 Protection flags (nil where none): B Phase E/F CAUSE: Unknown Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Patrolled Nothing Found Weather (wind/rain): Fine still LFI (Y/N + Comments): Yes and not Flashing Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4456 |  | JE24017587 | TE POI | Eastern | TE POI | 2024-05-21 | 5:12 | 2024-05-21 | 11:18 | 0.0050484 | 1.3795e-05 | 5 | 1830 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: TX TC2347 (incorrect location given when called in) No. Fuses: 3 Fuse Amp Size: 3 Amp TIME CLOSED: 11:18 Cause: Lightning Weather (wind/rain): Wind/Rain Follow up required (select advisory)? No | .
4457 |  | JE24017590 | TE POI | Eastern | TE POI | 2024-05-21 | 5:33 | 2024-05-21 | 15:27 | 0.011464 | 1.9313e-05 | 7 | 4155 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: TC1288 No. Fuses: 2 & holder Fuse Amp Size: 6 TIME CLOSED: 15:26 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? | .
4458 |  | JE24017595 | MOWBRAY RD | Eastern | MOWBRAY RD | 2024-05-21 | 5:55 | 2024-05-21 | 15:52 | 0.10821 | 0.00042764 | 155 | 39222 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 13115/2 Protection flags (nil where none): Nil. (Opened by NOC) CAUSE: Car vs Pole Location: Pole F0526 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Windy & Rain LFI (Y/N + Comments): No Follow up Required (select advisory)? Yes Additional fault restoration comments: Recloser 13115 Opened for safety car vs pole report person reported trapped past ABS IC 723 between transformers TC 325 & TC 3071 ETA 1 hour. Advised feeder is dropped. Person should not move until FM arrive onsite. MDP 4min away Person still in car Field Switcher arrived on site and confirmed Car vs Pole at Pole F0526. Person removed from car safely and paramedics were on site. Isolation carried out at ABS IC723 & ABS IC1330 REC 13115/2 NOC Closed in at 07:56 and Power restored to the healthy part of the network. Pole is being replaced under Access Permit 7595-01 ETA= Several hours due to HV & LV that need to be repaired on the Pole. SAFETY MANAGER | .
4459 |  | JE24017597 | HARRIS BLOCK | Eastern | HARRIS BLOCK | 2024-05-21 | 5:58 | 2024-05-21 | 9:24 | 0.050729 | 0.00040005 | 145 | 18387 | Unplanned | LIGHTNING - LIGHTNING STRIKE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 9198/2 Protection flags (nil where none): E/F CAUSE: Lightning Location: FusedABS 1297 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: cursory Weather (wind/rain): Lightning LFI (Y/N + Comments): Y at Pole 392831 Follow up Required (select advisory)? n Additional fault restoration comments: 2 transformers were found with fuses hanging due to the lightning and were reloaded and closed. Tfr 1: TC791 3 X 3 amp fuses Time: 08:30 Cause: lightning Tfr 2: TC3136 2 X 3 amp fuses Time : 09:15 Cause: lightning | .
4460 |  | JE24017600 | TE POI | Eastern | TE POI | 2024-05-21 | 6:11 | 2024-05-21 | 12:45 | 0.002173 | 5.5179e-06 | 2 | 788 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: TC2278 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 12:44 Cause: Lightning Weather (wind/rain): Lightning / rain Follow up required (select advisory)?n | .
4461 |  | JE24017601 | KEENAN RD | Eastern | KEENAN RD | 2024-05-21 | 9:27 | 2024-05-21 | 11:02 | 0.00072919 | 8.2769e-06 | 3 | 264 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: Lead off main line @ Pole 212211 Weather (wind/rain): High wind & rain Isolation from Fuses S4731 | .
4462 |  | JE24017603 | LICHFIELD | Eastern | LICHFIELD | 2024-05-21 | 6:13 | 2024-05-21 | 15:00 | 0.0043613 | 8.2769e-06 | 3 | 1581 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Tc1992 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 15:00 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? | .
4463 |  | JE24017607 | OKOROIRE | Eastern | OKOROIRE | 2024-05-21 | 6:20 | 2024-05-21 | 15:04 | 0.010118 | 1.9313e-05 | 7 | 3667 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: TC969 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 15:04 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? | .
4464 |  | JE24017621 | PAPANUI ST | Eastern | PAPANUI ST | 2024-05-21 | 7:04 | 2024-05-21 | 12:02 | 0.004114 | 1.3795e-05 | 5 | 1491 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: FC1448 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 12:02 Cause: Lightning Weather (wind/rain): Lightning / rain Follow up required (select advisory)?n | .
4465 |  | JE24017623 | WAITAWHETA | Eastern | WAITAWHETA | 2024-05-21 | 11:41 | 2024-05-21 | 23:00 | 0.0098052 | 9.9323e-05 | 21 | 3554 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faulty transformer TC582 Additional Info: Generator is installed 18:25. Returning tomorrow to carry on repairs Generator Connected TC582 23:00 The faultman found some trees on the LV lines and some twisted LV lines when they attempted to start generator it tripped out, after clearing LV faults generator in service. There is an issue in this region of the network with over grown trees the faultman cut back any they could see where branches were on fire. I have asked the faultman to use the 2R and document their findings and to take pictures so that we can get tree cutters in to clear the trees back from the line. There has been issues of low voltage at the end of the line experienced by some customers and it may be worth having the line patrolled with infra red camera looking for trouble spot connections LV fault cleared, Gen OFF 11:30 Hrs, Normal Power restored 11:40Hrs | .
4466 |  | JE24017633 | TE POI | Eastern | TE POI | 2024-05-21 | 7:25 | 2024-05-21 | 12:21 | 0.0024514 | 8.2769e-06 | 3 | 889 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: TC2784 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 12:20 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n | .
4467 |  | JE24017640 | KAIMAI DRIVE | Eastern | KAIMAI DRIVE | 2024-05-21 | 7:45 | 2024-05-21 | 13:45 | 0.00099516 | 2.759e-06 | 1 | 361 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Fuses S5284 No. Fuses: 2 Fuse Amp Size: 6 Amp TIME CLOSED: 13:45 Cause: Lightning Weather (wind/rain): Rain & wind Follow up required (select advisory)? No | .
4468 |  | JE24017644 | APATA | Eastern | APATA | 2024-05-21 | 9:45 | 2024-05-21 | 20:15 | 0.008688 | 1.3795e-05 | 5 | 3149 | Unplanned | VEGETATION - OUTSIDE ZONE | Transformer & pole brought down by tree Pole & transformer TC2-145 replaced Fuses SC2-129 closed 20:15 | .
4469 |  | JE24017649 | GORDON | Eastern | GORDON | 2024-05-21 | 8:05 | 2024-05-21 | 11:48 | 0.0024674 | 1.1036e-05 | 4 | 894 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: TC4654 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 11:48 Cause: Lightning Weather (wind/rain): Lightning / rain Follow up required (select advisory) Job was at REF JE24017733 | .
4470 |  | JE24017651 | YOUNG RD | Eastern | YOUNG RD | 2024-05-21 | 8:11 | 2024-05-21 | 9:20 | 0.011072 | 0.00024555 | 89 | 4013 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11 kV REC 13282 Protection flags (nil where none): O/C & C Phase CAUSE: No fault found Location: N/A Temp generation (state details when used): N/A PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Curs Patrol Weather (wind/rain): High Wind LFI (Y/N + Comments): Follow up Required (select advisory)? N Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4471 |  | JE24017686 | OKOROIRE | Eastern | OKOROIRE | 2024-05-21 | 9:13 | 2024-05-21 | 15:20 | 0.0010142 | 2.759e-06 | 1 | 368 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: TC3549 No. Fuses: 2 Fuse Amp Size: 2 TIME CLOSED: 15:20 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? | .
4472 |  | JE24017713 | HARRIS BLOCK | Eastern | HARRIS BLOCK | 2024-05-21 | 11:16 | 2024-05-21 | 15:31 | 0.0063364 | 2.4831e-05 | 9 | 2297 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: TC1626 CAUSE: Lightning Temp generation (stage details when used): n PERFORMANCE DETAIL DNO (number or state no): n Circuit patrolled & type: n/a Weather (wind/rain): Lightning Follow up required (select advisory)?y Additional fault restoration comments: Transformer TC1626 replaced under 2R, hit by lightning | .
4473 |  | JE24017731 | PAPANUI ST | Eastern | PAPANUI ST | 2024-05-21 | 7:26 | 2024-05-21 | 12:50 | 0.0022356 | 1.3795e-05 | 5 | 810 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: TC1644 No. Fuses: 3 Fuse Amp Size: 3 TIME CLOSED: 12:49 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?Jobs on JE24017634 are all fed off this transformer TC1644 | .
4474 |  | JE24017732 | MATAPIHI RD | Eastern | MATAPIHI RD | 2024-05-21 | 16:00 | 2024-05-21 | 16:46 | 0.00025263 | 5.5179e-06 | 2 | 92 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Suspect Cable Failed (confirmed , has been replaced) Generator Connected to TD4-251 16:45 21/05/24 27/05/24 - New 11KV cable being put in starting today. The generator should be off Thursday - as per SMC 4/06/24 Cable replaced and liven then generator removed Power off Generator 14:18, restored via LV Fuses 1421 | .
4475 |  | JE24017734 | CAMBRIDGE RD TIRAU | Eastern | CAMBRIDGE RD TIRAU | 2024-05-21 | 13:45 | 2024-05-21 | 20:24 | 0.0010994 | 2.759e-06 | 1 | 399 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Isolation: TX fuses CAUSE: Lightning Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): n Circuit patrolled & type: cursory Weather (wind/rain): Lightning Follow up required (select advisory)? Additional fault restoration comments: Transformer TC7274 replaced, fuses closed 20:23 | .
4476 |  | JE24017741 | OPOUTERE | Eastern | OPOUTERE | 2024-05-21 | 6:30 | 2024-05-21 | 10:43 | 0.0098724 | 4.1384e-05 | 15 | 3578 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: FC2339 No. Fuses: 2 Fuse Amp Size: 10Amp TIME CLOSED: 10:42hrs Cause: Lightning Weather (wind/rain): Lightning / Heavy Rain Follow up required (select advisory)? | .
4477 |  | JE24017742 | LICHFIELD | Eastern | LICHFIELD | 2024-05-21 | 11:07 | 2024-05-21 | 14:20 | 0.0026597 | 1.3795e-05 | 5 | 964 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: TC348 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 14:20 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? | .
4478 |  | JE24017760 | PLUMMERS POINT | Eastern | PLUMMERS POINT | 2024-05-21 | 12:02 | 2024-05-21 | 19:26 | 0.011021 | 2.4831e-05 | 9 | 3995 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: TC3-048 No. Fuses: 3 Fuse Amp Size: TIME CLOSED: 19:25 Cause: TC3-048 failed & was replaced Weather (wind/rain): Follow up required (select advisory)? | .
4479 |  | JE24017769 | RUAPEHU | Western | RUAPEHU | 2024-05-21 | 12:37 | 2024-05-21 | 13:50 | 0.0016193 | 2.2072e-05 | 8 | 587 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Faultman found blown jumper at FusedABS 1265, line was isolated at Links 1038 , when Faultman went to repair the jumper found insulator had been blown off, ABS part of the FusedABS was bypassed, ABS has been DNO'd (2405018), Faultman will arrange with FRM to put in a NAPA to replace insulators. | .
4480 |  | JE24017770 | TAUMANGI RD | Eastern | TAUMANGI RD | 2024-05-21 | 12:45 | 2024-05-22 | 10:14 | 0.0035556 | 2.759e-06 | 1 | 1289 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: TC397 No. Fuses: 3 Fuse Amp Size: 2 TIME CLOSED: 10:14 Cause: Lightning Weather (wind/rain): Rain, wind, lightning Follow up required (select advisory)?n TFR TC397 was found to be missing its earthing, TFR could not be restored until earthing had been replaced. | .
4481 |  | JE24017781 | TE POI | Eastern | TE POI | 2024-05-21 | 13:28 | 2024-05-21 | 13:37 | 4.7756e-05 | 5.5179e-06 | 2 | 17 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: TX TC1441 No. Fuses: 2 Fuse Amp Size: 2 Amp TIME CLOSED: 13:36 Cause: Lightning Weather (wind/rain): Rain & wind. Follow up required (select advisory)? No Hub need to put Malcolm on site. I have asked - BR | .
4482 |  | JE24017787 | HETHERINGTON RD | Eastern | HETHERINGTON RD | 2024-05-21 | 13:26 | 2024-05-21 | 13:36 | 0.003045 | 0.00030349 | 110 | 1104 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Equipment de enegised to allow Tap Setting to be lowered as per Powerco request, then power restored | .
4483 |  | JE24017793 | WAOTU | Eastern | WAOTU | 2024-05-21 | 14:00 | 2024-05-22 | 9:44 | 0.006533 | 5.5179e-06 | 2 | 2368 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: FP1231 No. Fuses: 3 Fuse Amp Size: 3 TIME CLOSED: 09:43 Cause: Lightning Weather (wind/rain): wind, rain & lightning Follow up required (select advisory)?n | .
4484 |  | JE24017804 | HARRIS BLOCK | Eastern | HARRIS BLOCK | 2024-05-21 | 14:54 | 2024-05-22 | 6:22 | 0.0050902 | 5.5179e-06 | 2 | 1845 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses TC5060 1x 2A 06:21 Fuses TC4954 3 x 3A 06:10 | .
4485 |  | JE24017805 | TE POI | Eastern | TE POI | 2024-05-21 | 14:56 | 2024-05-21 | 18:10 | 0.0021381 | 1.1036e-05 | 4 | 775 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: FP15 No. Fuses: 3 Fuse Amp Size: 8 TIME CLOSED: 18:10 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)?n | .
4486 |  | JE24017813 | LICHFIELD | Eastern | LICHFIELD | 2024-05-21 | 15:54 | 2024-05-22 | 12:16 | 0.0067417 | 5.5179e-06 | 2 | 2444 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: TC4336 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 12:16 Cause: lightning Weather (wind/rain): rain, windy, lightning Follow up required (select advisory)?n | .
4487 |  | JE24017849 | TE POI | Eastern | TE POI | 2024-05-21 | 18:00 | 2024-05-21 | 21:25 | 0.0016974 | 8.2769e-06 | 3 | 615 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: TC2684 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 21:24 Cause: Weather (wind/rain): Follow up required (select advisory)? | .
4488 |  | JE24017858 | MANGATARATA | Eastern | MANGATARATA | 2024-05-21 | 19:09 | 2024-05-21 | 21:12 | 0.0010165 | 8.2769e-06 | 3 | 368 | Unplanned | WILDLIFE - BIRD | Fuses Location: FP1130 No. Fuses: 3 Fuse Amp Size: 6 TIME CLOSED: 21:11 Cause: bird Weather (wind/rain): Follow up required (select advisory)? | .
4489 |  | JE24017863 | LICHFIELD | Eastern | LICHFIELD | 2024-05-21 | 21:02 | 2024-05-22 | 10:49 | 0.006844 | 8.2769e-06 | 3 | 2481 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: TC2834 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 10:49 Cause: lightning Weather (wind/rain): wind, rain, lightning Follow up required (select advisory)?n | .
4490 |  | JE24012196 | 8 Otaranoho Rd Raetihi | Western | RAETIHI | 2024-05-20 | 9:30 | 2024-05-20 | 14:29 | 0.018109 | 6.0697e-05 | 22 | 6564 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 777837 & 777835. It was reported the LV service line from transformer X1693 goes through a whole lot of gorse and will need to be removed. The line is private owned, the Faulman indicated that the line will be isolated on 21/05, to cut the gorse away in conjunction with the owner and their electrician. For further info contact James Prime from Taihape area. | .
4491 |  | JE24012400 | 1213 FITZHERBERT EAST ROAD AOKAUTERE PALMERSTON NORTH | Western | AOKAUTERE | 2024-05-20 | 8:46 | 2024-05-20 | 15:18 | 0.024238 | 0.00017106 | 42 | 8785 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | reconductor between pole P01350 and P01314 | .
4492 |  | JE24017470 | WAITUNA | Western | WAITUNA | 2024-05-20 | 10:31 | 2024-05-20 | 11:46 | 0.00020472 | 2.759e-06 | 1 | 74 | Unplanned | WILDLIFE - BIRD | Fuses Location: P23 No. Fuses: 2 Fuse Amp Size: 10 Amp TIME CLOSED: 11:45 Cause: Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? N | .
4493 |  | JE24017552 | POOLES RD | Eastern | POOLES RD | 2024-05-20 | 20:35 | 2024-05-21 | 23:12 | 0.23917 | 0.0029383 | 984 | 86689 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 11kV recloser 9690 on TGA 20 back feeding TGA 21 via sectionaliser 9832 up to ABS SD4-310 due to DNO tripped C phase OC & EF Fault isolated to cable disconnected at pole 268903 supplying switch gear 13018 Cable disconnect & left earthed at sw/gear 13018/1 Transformer TD4-583 is 750kVA but some sites past it are shut down, area is commercial & industrial FRM advised, and will deal with customers in morning as required It was found that switch gear 13018 was faulty and it was changed out. Generation was connected to transformer TD4-583 08:46 & removed 22:00 | .
4494 |  | JE24017556 | WARDVILLE | Eastern | WARDVILLE | 2024-05-20 | 22:36 | 2024-05-21 | 8:24 | 0.085794 | 0.00040833 | 108 | 31097 | Unplanned | ADVERSE WEATHER - WIND-BLOWN DEBRIS (NOT TREES) | REGULATORY INFORMATION Voltage & Device ID: 11kV REC RC25/2 Protection flags (nil where none): E/F CAUSE: Wire found bridging Conductor to stay-wire. Location: Pole 468868 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Windy & Rain LFI (Y/N + Comments): Yes, LFI @ H0569 Comms offline. Follow up Required (select advisory)? Yes, investigate why LFI's are offline please. Additional fault restoration comments: 11kV recloser RC 25 tripped on E/F LFI at pole H0569 not working on SCADA but indicating on site towards ABS 700 LFI at IC1099 were not indicating and when back feed put in place via ABS IP584 tripped MIK CB 4 recloser RC 11 Second patrol of IP584 to IC 1099 did not find a fault left out for day light hours patrol 21/05/2024 Field Switcher to carry out a Line Patrol from ABS IC1099 to ABS IP584 - Matthew Mculloch is on site. After carrying out the Line Patrol and not finding anything at the time. ABS IC1099 was closed in at 08:23 successfully. Upon checking if all Power had been restored, Field Switcher found 1 x HV Fuse blown at Fuses FC1428. Patrolled past those Fuses and it was not easy to see from ground level but found loose wire bridging HV Conductor & stay-wire at Pole 468868. Removed via ho | .
4495 |  | JE24014697 | 206 JELLICOE CRESCENT THAMES THAMES | Eastern | TOTARA | 2024-05-19 | 9:15 | 2024-05-19 | 15:29 | 0.0082445 | 2.2072e-05 | 8 | 2988 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Pole T12602 and HV Crucifix | .
4496 |  | JE24017380 | BROOKLANDS | Western | BROOKLANDS | 2024-05-19 | 10:51 | 2024-05-19 | 13:04 | 0.014075 | 0.00044143 | 160 | 5101 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Live 11kV Line found on ground at pole Feeder de-energised at CB 10405/2 Isolated at ABS I27 CB 10405/2 Closed 11:04 Line repaired and power restored 13:03 Cause age Location pole P10787 FM to defect pole and conductor | .
4497 |  | JE24017392 | MARTON | Western | MARTON | 2024-05-19 | 14:38 | 2024-05-19 | 17:20 | 0.31726 | 0.003617 | 1311 | 114994 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 7 Protection flags (nil where none): O/C CAUSE: Line down Location: Pole 802695 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Isolated at ABS 930Lines repaired SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4498 |  | JE24017396 | JAMES LINE | Western | JAMES LINE | 2024-05-19 | 15:51 | 2024-05-19 | 17:52 | 0.00099861 | 8.2769e-06 | 3 | 362 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuse found blown at Fuses E58 Transformer T6/673 found to be faulty Isolated at Fuses E58 Transformer replaced, Power restored 17:51 | .
4499 |  | JE24017404 | KUMENGA | Western | KUMENGA | 2024-05-19 | 18:56 | 2024-05-19 | 20:36 | 0.0010947 | 1.1036e-05 | 4 | 397 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 7043 No. Fuses: 2 Fuse Amp Size: 8A TIME CLOSED: 20:35 Cause: Unknown, patrolled Weather (wind/rain): calm Follow up required (select advisory)? No | .
4500 |  | JE24017307 | RIVERLEA | Western | RIVERLEA | 2024-05-18 | 3:31 | 2024-05-18 | 14:02 | 0.065333 | 0.00040005 | 145 | 23680 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 12258/2 Protection flags (nil where none): B & C ph E/F CAUSE: Car vs Pole Location: 941698 (Tfr 3060T) Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: n Weather (wind/rain): LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Received call from Fire Comms(F3977659) of car vs pole. Line was isolated at ABS's 5968, 6000, 12258/1 & Links 12258/6 TAG REG Updated Yes Riverlea Hall 1767 Eltham Road - TAG A41684 Retailer e-mailed Yes 1779 Eltham Road - TAG A41686 - Retailer e-mailed Yes 1790 Eltham Road - TAG A41685 - Retailer e-mailed Yes | .
4501 |  | JE24017333 | DAIRY FACTORY | Western | DAIRY FACTORY | 2024-05-18 | 13:05 | 2024-05-18 | 14:30 | 0.020483 | 0.00024279 | 88 | 7424 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kv recloser 11169 Protection flags (nil where none): EF A &B phase CAUSE: birds Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Performance Additional fault restoration comments: Farmer states number of swans so large that they wake him at 6 am as they fly in , his property is near the river **Field staff requested** LFI @ poles 815 457 & 468 191 These 2 locations will speed fault finding by reducing the areas needed to be patrolled. | .
4502 |  | JE24017356 | 340 HARWOODS ROAD, TAPAPA, TIRAU, 3485 | Eastern | RANGITANUKU RD | 2024-05-18 | 19:40 | 2024-05-19 | 3:05 | 0.10431 | 0.00023451 | 85 | 37809 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 1 Protection flags (nil where none): None CAUSE: Car accident Location: Pole 878908 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4, either side of the accident scene Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Check JE24017358 reported no power 11m pole replaced 1 x double HV pin arm complete assembly 1 x double LV pin arm complete assembly NDR to follow SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4503 |  | JE24017366 | FORDELL | Western | FORDELL | 2024-05-18 | 23:04 | 2024-05-19 | 13:36 | 0.15422 | 0.00034487 | 125 | 55899 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 4200/2 Protection flags (nil where none): E/F CAUSE: Lines down Location: Between poles 791191 & 791184 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: cursory Weather (wind/rain): calm LFI (Y/N + Comments): N Follow up Required (select advisory)? n Additional fault restoration comments: Line isolated at ABS 251, crews will return in first day light as lines cross river and thick bush area. 19/05/2024 Lines repaired power restored 13:35 | .
4504 |  | JE24011806 | 1022 TAUMATA ROAD OMANAWA TAURANGA | Eastern | PYES PA | 2024-05-17 | 9:23 | 2024-05-17 | 16:06 | 0.066588 | 0.00016554 | 60 | 24135 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV overhead conductors between Poles 493697 & 216961 with 2W Ferret. | .
4505 |  | JE24012098 | 62 NGA TAWA ROAD MARTON MARTON | Western | NGATAWA | 2024-05-17 | 9:00 | 2024-05-17 | 12:46 | 0.011215 | 4.9661e-05 | 18 | 4065 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11KV Defected X-Arms & TX at pole 802772/X1099 | .
4506 |  | JE24012399 | 1152 FITZHERBERT EAST ROAD AOKAUTERE PALMERSTON NORTH | Western | AOKAUTERE | 2024-05-17 | 9:16 | 2024-05-17 | 15:02 | 0.021261 | 0.00017106 | 42 | 7706 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | reconductor between P35424 and P35414 | .
4507 |  | JE24015350 | 368 IRONWORKS ROAD HUNTERVILLE HUNTERVILLE | Western | HUNTERVILLE 22KV | 2024-05-17 | 8:33 | 2024-05-17 | 13:26 | 0.025888 | 8.8287e-05 | 32 | 9383 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV poles 807603, 807604, 807628, 807640. Replace X-arms 807626, 807627, 807636, 807637, 807638, 807639. Remove LV Conductor: 807630, 807634, 807635. Relocate Transformer X1414 from 807639 to 807640. | .
4508 |  | JE24016799 | MCCABE ROAD | Eastern | MCCABE ROAD | 2024-05-17 | 9:46 | 2024-05-17 | 11:13 | 0.0091108 | 0.00010484 | 38 | 3302 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE DAMAGED 11kV POLE 499654. | .
4509 |  | JE24017065 | BUFFALO BEACH | Eastern | BUFFALO BEACH | 2024-05-17 | 11:01 | 2024-05-17 | 12:08 | 0.01023 | 0.00015174 | 55 | 3708 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Cause: Overheating due to faulty connection What was replaced? LV disconnector Where was it replaced (pole/TX/pillar box)? TP888 Is 2R required? Y 2R Y - What is the timeframe for repairs? Tomorrow - 17/05/2024 Additional Info: Isolation via Fuse/Sw 9089/2 Advertised under E00125 on 16/05 at 15:25, outage is unplanned. | .
4510 |  | JE24017196 | TURAKINA | Western | TURAKINA | 2024-05-17 | 9:57 | 2024-05-17 | 11:30 | 0.0002559 | 2.759e-06 | 1 | 93 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 2977 No. Fuses: 2 Fuse Amp Size: 2Amp TIME CLOSED: 11:30 hrs Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)? | .
4511 |  | JE24017197 | KAIHERE | Eastern | KAIHERE | 2024-05-17 | 10:09 | 2024-05-17 | 11:15 | 0.00090551 | 1.3795e-05 | 5 | 328 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses FC762 No. Fuses: 2 Fuse Amp Size: 25A TIME CLOSED: 11:14 Cause: Unknown Weather (wind/rain): windy Follow up required (select advisory)? No | .
4512 |  | JE24017199 | OTAHU RD | Eastern | OTAHU RD | 2024-05-17 | 10:14 | 2024-05-17 | 19:06 | 0.331 | 0.0031507 | 1142 | 119971 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 7 Protection flags (nil where none): O/C E/F A Ø CAUSE: the bus coupler failed on the switchgear 9112/3 Location: Sw/Gear 9112/3 Temp generation (state details when used): Yes -19:05 Hrs PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: No trip flags on Rec 9813/2, Opened and back fed via WGM 9 Sec 9476/2 Closed. Generator connected at TC3697, ON 19:05Hrs DNO 2405016 (2405017 was a duplicate) | .
4513 |  | JE24017275 | TUTURUMURI | Western | TUTURUMURI | 2024-05-17 | 15:58 | 2024-05-18 | 12:15 | 0.0033598 | 2.759e-06 | 1 | 1218 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Cause: Transformer T3059 faulty What was replaced? yes Is 2R required? Y/NY 2R Y - What is the timeframe for repairs? Additional Info: FM have spoken to the customer, transformer has blown, will need replacing, will return in the morning in daylight to replace. Customer is happy with this outcome. Sam is onsite - as per NC Replaced 18/05/24 | .
4514 |  | JE24017277 | MAURICEVILLE | Western | MAURICEVILLE | 2024-05-17 | 16:03 | 2024-05-17 | 21:00 | 0.031592 | 0.00011036 | 40 | 11451 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC U39 Protection flags (nil where none): A, B & C ph O/C CAUSE: Tree through lines in gully Location: between poles P15828 & 374789 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: cursory Weather (wind/rain): wind LFI (Y/N + Comments): N Follow up Required (select advisory)? Y Additional fault restoration comments: Faultman cut 2 Temp Line Breaks at poles P15828 & 374789, will return on Monday 20/05 with tree cutters to cut remaining trees and repair the lines under the 2R Work is going to be done under NAPA 111468 on 24/05/24, to repair the lines and close the 2 line breaks. | .
4515 |  | JE24017297 | CLOTON RD SOUTH | Western | CLOTON RD SOUTH | 2024-05-17 | 19:33 | 2024-05-17 | 21:54 | 0.00038958 | 2.759e-06 | 1 | 141 | Unplanned | WILDLIFE - POSSUM | Fuses Location: 12322 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 21:54 Cause: Possum Weather (wind/rain): calm Follow up required (select advisory)?n | .
4516 |  | JE24011790 | 790 TAUMATA ROAD OMANAWA TAURANGA | Eastern | PYES PA | 2024-05-16 | 8:59 | 2024-05-16 | 14:36 | 0.055814 | 0.00016554 | 60 | 20230 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV overhead conductors between Poles 217046 & 493697 with 3W Ferret. | .
4517 |  | JE24012025 | 211 BRANDON HALL ROAD BULLS BULLS | Western | PAREWANUI | 2024-05-16 | 9:15 | 2024-05-16 | 13:19 | 0.038324 | 0.00015726 | 57 | 13891 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles and crossarms between poles 809320 & 809230. | .
4518 |  | JE24012832 | 609 KENT ROAD KORITO NEW PLYMOUTH | Western | JUNCTION RD | 2024-05-16 | 9:45 | 2024-05-16 | 12:40 | 0.008699 | 4.9661e-05 | 18 | 3153 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | to replace all xarms on pole 752413 in bad state, | .
4519 |  | JE24014578 | 79 THAMES STREET MORRINSVILLE MORRINSVILLE | Eastern | LORNE ST | 2024-05-16 | 21:00 | 2024-05-16 | 23:39 | 0.0022 | 1.3795e-05 | 5 | 797 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9472-1/2/3 | .
4520 |  | JE24014693 | 281 DEVON STREET WEST NEW PLYMOUTH NEW PLYMOUTH | Western | BREAKWATER RD | 2024-05-16 | 0:04 | 2024-05-16 | 2:23 | 0.024429 | 0.00017657 | 64 | 8854 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | DNO 2402008 - Cable to be in service. Clean Magnefix 411 and cable terms to re-test cable before attempt relivening. | .
4521 |  | JE24015048 | 124 WOODSIDE ROAD WOODSIDE GREYTOWN | Western | WEST ST | 2024-05-16 | 9:00 | 2024-05-16 | 15:01 | 0.16028 | 0.00044419 | 161 | 58094 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles and hardware a multiple sites past C430/2 | .
4522 |  | JE24015085 | 839 OTARAOA ROAD TIKORANGI WAITARA | Western | OTARAOA RD | 2024-05-16 | 9:22 | 2024-05-16 | 16:01 | 0.056055 | 0.00014071 | 51 | 20318 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install New Tavrida 12698 Recloser/Abs/Links/Tx structure near pole 760931 | .
4523 |  | JE24015371 | 265 TOKO ROAD TOKO STRATFORD | Western | TOKO | 2024-05-16 | 8:31 | 2024-05-16 | 13:17 | 0.072731 | 0.00027038 | 98 | 26362 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace hv red tag pole 740228 for clearance and replace hv pin arm 740485 | .
4524 |  | JE24016677 | 91 MATAKOKIRI DRIVE TAURIKO TAURANGA | Eastern | MATAKOKIRI DR | 2024-05-16 | 23:28 | 2024-05-17 | 3:00 | 0.0040885 | 1.9313e-05 | 7 | 1482 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace a leaking transformer. | .
4525 |  | JE24017030 | UNION LINE | Western | UNION LINE | 2024-05-16 | 0:41 | 2024-05-16 | 2:40 | 0.0022899 | 1.9313e-05 | 7 | 830 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 2894 No. Fuses: 2 Fuse Amp Size: 30 TIME CLOSED: 02:39 Cause: unknown Weather (wind/rain): fog Follow up required (select advisory)?y Network improvement remove fuses 2894 from pole 793308 & install fuses at pole 79330, this pole is the last pole before the line goes into a forestry block, we have no access past a locked gate, end TFR feeds a Gas site | .
4526 |  | JE24017031 | APATA | Eastern | APATA | 2024-05-16 | 5:31 | 2024-05-16 | 7:57 | 0.005617 | 3.8625e-05 | 14 | 2036 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: S6014 No. Fuses: 2 Fuse Amp Size: 8A TIME CLOSED: 07:56 Cause: UNKNOWN Weather (wind/rain): RAIN Follow up required (select advisory)?NO | .
4527 |  | JE24017068 | PAHOIA | Eastern | PAHOIA | 2024-05-16 | 12:33 | 2024-05-16 | 15:12 | 0.052527 | 0.00033108 | 120 | 19039 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 13206/2 (NOC opened) Protection flags (nil where none): Nil CAUSE: Tree on lines Location: Pole 209008 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: F1/F4, No patrolled. Weather (wind/rain): Rain LFI (Y/N + Comments): Not activated Follow up Required (select advisory)? No Additional fault restoration comments: AOR valley Central Emailed AI Team and network connections about no AOR details ETA 20 min. Rec 13206/2 Opened by NOC for safety Tree removed from lines at pole 209008 NDR to follow | .
4528 |  | JE24017072 | TURAKINA | Western | TURAKINA | 2024-05-16 | 10:44 | 2024-05-16 | 13:22 | 0.00087395 | 5.5179e-06 | 2 | 317 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 2708 No. Fuses: 2 Fuse Amp Size: 15 TIME CLOSED: 13:22 Cause: Unknown, Patrolled Weather (wind/rain): Fine Follow up required (select advisory)? No | .
4529 |  | JE24017075 | GULLIVER RD | Eastern | GULLIVER RD | 2024-05-16 | 11:11 | 2024-05-16 | 13:41 | 0.0012414 | 8.2769e-06 | 3 | 450 | Unplanned | WILDLIFE - BIRD | Fuses Location: FP894 No. Fuses: 2 Fuse Amp Size: 8 amps TIME CLOSED: 13:40 Cause: bird strike Weather (wind/rain): calm Follow up required (select advisory)? | .
4530 |  | JE24017104 | COUNTY WATER | Eastern | COUNTY WATER | 2024-05-16 | 13:35 | 2024-05-16 | 15:02 | 0.083717 | 0.0021382 | 775 | 30343 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 4 Protection flags (nil where none): O/C INST, B - C Ø CAUSE: Unknown, lines patrolled. Location: Unknown Temp generation (state details when used): N/A PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F1/F4, cursory patrolled. Weather (wind/rain): rain/windy LFI (Y/N + Comments): No LFIs activated Follow up Required (select advisory)? No Additional fault restoration comments: CB 4 was back feeding CB 1(DNO 2405001) at the time of the tripping. David Spellman informed me that CB 1 had repairs done and could be normalized which was done with the fault switching. The rest of CB 4 was patrolled and no fault was found. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4531 |  | JE24017127 | PONATAHI | Western | PONATAHI | 2024-05-16 | 14:50 | 2024-05-16 | 16:19 | 0.00043892 | 5.5179e-06 | 2 | 159 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 11103 & T2196 No. Fuses: 2 & 3 Fuse Amp Size: 8 amps & 2 amps TIME CLOSED: 16:00 & 16:18 Cause: unknown Weather (wind/rain): calm Follow up required (select advisory)?Job was not at Transformer T3158 that is the customers home Tfr. fault was at Fuses 11103 & Tfr T2196. Transformer T2196 has only a abandoned house on it and the LV fuses are removed. | .
4532 |  | JE24017137 | TATUANUI | Eastern | TATUANUI | 2024-05-16 | 16:50 | 2024-05-16 | 18:23 | 0.0066999 | 7.1733e-05 | 26 | 2428 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Replace broken fuse bases at TP1950 Isolation between ABS IC626 and IC639 replaced fuse cross arm complete assembly 3 x 6A fuses Repaired jumper connections on the main line to fuses. | .
4533 |  | JE24017149 | WESTMERE GLADSTONE | Western | WESTMERE GLADSTONE | 2024-05-16 | 21:15 | 2024-05-16 | 22:29 | 0.00040419 | 5.5179e-06 | 2 | 147 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Replaced jumper at Transformer T4089, and restored power. | .
4534 |  | JE24010630 | 86 AVENUE ROAD NORTH MORRINSVILLE MORRINSVILLE | Eastern | LORNE ST | 2024-05-15 | 23:30 | 2024-05-16 | 4:26 | 0.037521 | 0.00012691 | 46 | 13600 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance 9184-1/2/3/4 | .
4535 |  | JE24011657 | 21 WILLIAMS ROAD SOUTH PYES PA TAURANGA | Eastern | PYES PA | 2024-05-15 | 8:01 | 2024-05-15 | 10:09 | 0.019139 | 0.00014898 | 54 | 6937 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | install 11kV LFI's smart navigator 2.0 LFIs at Pole 216656 | .
4536 |  | JE24012144 | 1464A MASTERTON STRONVAR ROAD WAINUIORU MASTERTON | Western | WERAITI | 2024-05-15 | 8:45 | 2024-05-15 | 12:30 | 0.00062021 | 2.759e-06 | 1 | 225 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re conductor from fuses 11462 to T1737 | .
4537 |  | JE24012189 | 1152 FITZHERBERT EAST ROAD AOKAUTERE PALMERSTON NORTH | Western | AOKAUTERE | 2024-05-15 | 9:15 | 2024-05-15 | 15:17 | 0.022207 | 0.00017106 | 42 | 8049 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | reconductor between pole 367024 and P35424 | .
4538 |  | JE24014516 | 339 KAIRANGA BUNNYTHORPE ROAD BUNNYTHORPE PALMERSTON NORTH | Western | BUNNYTHORPE | 2024-05-15 | 9:30 | 2024-05-15 | 15:30 | 0.064608 | 0.00017933 | 65 | 23417 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Drop HV and LV lines for Asplundh to cut trees between poles P42258, P42259 and P42260 | .
4539 |  | JE24015327 | 13 WAIREKA ROAD PAPAITI WANGANUI | Western | MAKIRIKIRI | 2024-05-15 | 9:00 | 2024-05-15 | 12:55 | 0.089575 | 0.00038074 | 138 | 32467 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Move Fuses 586 to pole 784521 & install a 3m Trem arm. Move pole 784519 back to river side | .
4540 |  | JE24016183 | 1822 SOUTH ROAD TATARAIMAKA NEW PLYMOUTH | Western | INLAND COAST | 2024-05-15 | 9:30 | 2024-05-15 | 10:21 | 0.0039179 | 7.7251e-05 | 28 | 1420 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace red defect x- arm on pole 756924 and replace king with nut unwound on it | .
4541 |  | JE24016888 | BRUCE RD | Eastern | BRUCE RD | 2024-05-15 | 4:34 | 2024-05-15 | 5:41 | 0.04783 | 0.0015699 | 392 | 17336 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 14727 Protection flags (nil where none): B Phase O/C E/F CAUSE: Small Pine Tree Branch on ABS IP598 Location: ABS IP598, Tree only 1M away from ABS!! Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Sec Weather (wind/rain): Wind Rain LFI (Y/N + Comments): Yes Pole 485340 Indicated the fault was behind it. Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4542 |  | JE24016890 | ROADS | Eastern | ROADS | 2024-05-15 | 5:46 | 2024-05-15 | 7:21 | 0.047825 | 0.00069526 | 252 | 17334 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: Recloser 9146 Protection flags (nil where none): EF CAUSE: Tree branch Location: Pole 223713 trf TP3273 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Removed tree branch at Pole 223713 | .
4543 |  | JE24016892 | MOEHAU ST | Eastern | MOEHAU ST | 2024-05-15 | 8:46 | 2024-05-15 | 10:54 | 0.097949 | 0.0019175 | 695 | 35502 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: CB 5 Protection flags (nil where none): EF , Phase A Fault CAUSE: Cracked insulator Location: Pole 222606 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): Rain LFI (Y/N + Comments): No Follow up Required (select advisory)? Additional fault restoration comments: Replaced cross arm and insulator at pole 222606 CB 5 Tripped while already started isolating faulty area hence mixed sequence on switching sheet TE5-054 not in outage area | .
4544 |  | JE24016898 | RICHMOND ST | Eastern | RICHMOND ST | 2024-05-15 | 7:57 | 2024-05-15 | 12:43 | 0.27692 | 0.0015781 | 572 | 100373 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: Recloser 13585 Protection flags (nil where none): Phase OC CAUSE: Tres on Lines Location: Poles 484646 & 484475 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Yes Weather (wind/rain): Rain LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Trees removed from lines SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4545 |  | JE24016904 | PAPANUI ST | Eastern | PAPANUI ST | 2024-05-15 | 10:17 | 2024-05-15 | 11:30 | 0.0011966 | 1.6554e-05 | 6 | 434 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: Lightning What was replaced? Removed 3x faulted lightning arrestors at Transformer TC174 & bypassed. Where was it replaced (pole/TX/pillar box)? 380240 Additional Info: Also replaced 2x 10A HV fuse links at Fuses 13441 (found blown) TC174 will be defected for lightning arrestors to be replaced. | .
4546 |  | JE24016911 | TAIRUA NORTH | Eastern | TAIRUA NORTH | 2024-05-15 | 8:51 | 2024-05-15 | 10:56 | 0.00034533 | 2.759e-06 | 1 | 125 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Transformer TC5164 No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 10:55 Cause: Lightning Weather (wind/rain): Lightning Follow up required (select advisory)? No | .
4547 |  | JE24016928 | POHANGINA | Western | POHANGINA | 2024-05-15 | 10:55 | 2024-05-15 | 12:41 | 0.00029135 | 2.759e-06 | 1 | 106 | Unplanned | THIRD PARTY INTERFERENCE - VANDALISM/THEFT | Faultman found earthing had been cut away from transformer T2/262, transformer T2/262 was isolated and the earthing replaced. | .
4548 |  | JE24016932 | MEREMERE | Western | MEREMERE | 2024-05-15 | 10:35 | 2024-05-15 | 13:36 | 0.00099847 | 5.5179e-06 | 2 | 362 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: Aged / Rotten Cross Arm What was replaced? Cross Arm & All Hardware replaced. Wire pulled up. Where was it replaced (pole/TX/pillar box)? Pole 725383 Isolation: Fuses WH234 Weather: Windy / Heavy Rain Additional Info: | .
4549 |  | JE24016967 | CAMBRIA LS | Western | CAMBRIA LS | 2024-05-15 | 13:50 | 2024-05-15 | 15:29 | 0.024553 | 0.00024831 | 90 | 8900 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: Aged / Broken dead-end Isolation: CA463 What was replaced? 6x 35mm cu. dead-ends Where was it replaced (pole/TX/pillar box)? Pole 364164 Weather: Light Rain / Windy Additional Info: FM noticed low hanging HV line whilst carrying out other duties , so called into NOC Control to make urgent repairs | .
4550 |  | JE24016988 | WAIMAPU | Eastern | WAIMAPU | 2024-05-15 | 16:20 | 2024-05-15 | 23:50 | 0.0048127 | 1.1036e-05 | 4 | 1744 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses SF4-003 blown, incorrectly rated. TX TF4-023 blown due to lightning, TX replaced. | .
4551 |  | JE24016996 | TE MIRO RD | Eastern | TE MIRO RD | 2024-05-15 | 18:16 | 2024-05-15 | 22:56 | 0.024787 | 8.8287e-05 | 32 | 8984 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kv Pole I2676 Protection flags (nil where none): Rec 9121 A/R CAUSE: Car Location: I2676 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Suspected HV Contact, Customers off DTX TC2859 Instal checked. All OK No tripping, Rec 9121 A/R | .
4552 |  | JE24017026 | APATA | Eastern | APATA | 2024-05-15 | 23:18 | 2024-05-16 | 1:22 | 0.011009 | 8.8287e-05 | 32 | 3990 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses SC2-126 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 01:22 Cause: Pukekeho, Swampie Weather (wind/rain): wind Rain Follow up required (select advisory)? | .
4553 |  | JE24011764 | 1943 Pyes PA road | Eastern | PYES PA | 2024-05-14 | 8:57 | 2024-05-14 | 14:20 | 0.0017831 | 5.5179e-06 | 2 | 646 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV Poles, 217095, 217098, 217099, 217097. Replace 11kV Crossarms at Poles, 217093, 217094, 217096. | .
4554 |  | JE24011768 | 63 PREECES POINT ROAD PREECE POINT COROMANDEL | Eastern | MANAIA COROMANDEL | 2024-05-14 | 9:01 | 2024-05-14 | 16:59 | 0.021109 | 4.4143e-05 | 16 | 7651 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace xarms at poles V0187,V0188,V0189,and restrain | .
4555 |  | JE24011991 | 29 HIPANGO TERRACE DURIE HILL WANGANUI | Western | DURIE HILL | 2024-05-14 | 9:30 | 2024-05-14 | 12:28 | 0.033429 | 0.00018761 | 68 | 12116 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace old glass stain insulators and termination X arm Pole 767724 | .
4556 |  | JE24011995 | 54 TE ARAKURA ROAD FEILDING FEILDING | Western | TE ARAKURA | 2024-05-14 | 8:31 | 2024-05-14 | 13:39 | 0.022103 | 7.1733e-05 | 26 | 8011 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles and cross-arms between poles P39760 and P39124 | .
4557 |  | JE24012758 | 246 KORITO ROAD KORITO NEW PLYMOUTH | Western | JUNCTION RD | 2024-05-14 | 9:46 | 2024-05-14 | 12:30 | 0.022302 | 0.00013519 | 49 | 8083 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace all xarms on pole 752360 in bad state. | .
4558 |  | JE24014432 | 481 OTARAOA ROAD TIKORANGI WAITARA | Western | PRINCESS ST | 2024-05-14 | 11:07 | 2024-05-14 | 15:25 | 0.069147 | 0.0002759 | 100 | 25063 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Abs 5166 pole 764094 with Double 11m pole with new 12707-2 Entec Sw + - 4 links & 1kva Tx | .
4559 |  | JE24014641 | 1 MARKET STREET PUTARURU PUTARURU | Eastern | KENNEDY DRIVE | 2024-05-14 | 23:00 | 2024-05-15 | 3:36 | 0.031978 | 0.00011588 | 42 | 11591 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance IC3160/IC3127/IC3121/14657 | .
4560 |  | JE24014644 | 664 WANGANUI ROAD TURAKINA MARTON | Western | TURAKINA | 2024-05-14 | 8:30 | 2024-05-14 | 15:22 | 0.070478 | 0.00017106 | 62 | 25545 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | vegetation cutting on Wanganui road. site 1 between 802504 to 802503, site 2 between 359232 to 359256, site 3 between 358768 to 802435. | .
4561 |  | JE24016313 | 106 JOHNSTONE DRIVE FITZHERBERT PALMERSTON NORTH | Western | SUMMERHILL | 2024-05-14 | 9:10 | 2024-05-14 | 13:41 | 0.027627 | 0.00010208 | 37 | 10013 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | 7554P leaky bushing. Will swap out transformer like for like to remedy and bring faulty tx back for repair. | .
4562 |  | JE24016767 | 465 OEO ROAD, AUROA, HAWERA, 4678 | Western | PIHAMA | 2024-05-14 | 9:26 | 2024-05-14 | 10:19 | 0.0051946 | 9.9323e-05 | 36 | 1883 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Low Line at Pole 717181 (Fuses TA833), missing nut and insulator pulled out of cross arm Isolated at ABS TA813 & TA840 Strain insulator replaced, line pulled up, full power restored | .
4563 |  | JE24016777 | WINDFARM | Western | WINDFARM | 2024-05-14 | 9:48 | 2024-05-14 | 11:00 | 0.00019911 | 2.759e-06 | 1 | 72 | Unplanned | DEFECTIVE EQUIPMENT - ZONE SUBSTATION | Protection testing on CB C971 ( DNO 2405006) to check that protection will operate correctly. Tested and protection will operate but operation of the CB is only available at the operating handle. | .
4564 |  | JE24016875 | TUTURUMURI | Western | TUTURUMURI | 2024-05-14 | 19:10 | 2024-05-15 | 18:58 | 0.13302 | 0.00029245 | 106 | 48214 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec C632 Protection flags (nil where none): B, Phase Earth Fault CAUSE: 2 Faults found: (F1) Defective DDO on transformer T3059 and (F2) Cable clamp at Fuses 7168 all rusted and arcing on the cross arm. Location:(F1) Tfr T3059 & (F2) Fuses 7168 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: Operational Weather (wind/rain): rain LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Line isolated at Fuses 8064 to replace defective DDO's at T3059, when reliving Fuses 8064 Faultman saw arcing at Fuses 7168, line was isolated at Fuses 7168 to replace clamp and re-terminate cable. all 3 replaced | .
4565 |  | JE24012179 | 977 FITZHERBERT EAST ROAD AOKAUTERE PALMERSTON NORTH | Western | AOKAUTERE | 2024-05-13 | 9:00 | 2024-05-13 | 15:35 | 0.020754 | 0.00018209 | 66 | 7522 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | reconductor between P35448 to pole 367024 replacing robin to dog | .
4566 |  | JE24012665 | 118 WHITE ROCK ROAD MARTINBOROUGH MARTINBOROUGH | Western | WINDFARM | 2024-05-13 | 8:22 | 2024-05-13 | 15:54 | 0.0012452 | 2.759e-06 | 1 | 451 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Tree removal under and beside 33kV and 11kV lines "Switching Required to Open wind farm CB's 3178/2 & C971" | .
4567 |  | JE24016632 | CITY No 1 33kV | Western | CITY No 1 33kV | 2024-05-13 | 7:59 | 2024-05-13 | 8:05 | 0.026562 | 0.0046875 | 1699 | 9628 | Unplanned | HUMAN ERROR - POTENTIAL SWITCHING ERROR | During Planned NAPA 110296 for Transformer T1 offload at City sub, the bus coupler & Incomer were opened in error. once mistake realised, Bus coupler closed to restore power. | .
4568 |  | JE24016675 | 2076 WESTERN LAKE ROAD, FEATHERSTON | Western | REVANS ST | 2024-05-13 | 12:30 | 2024-05-13 | 13:05 | 0.0001923 | 5.5179e-06 | 2 | 70 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Broken binder, floating conductor Isolated at Fuses 7273 Binder replaced, full power restored | .
4569 |  | JE24016676 | MARTINBOROUGH SUB - CB C893 | Western | TAWAHA | 2024-05-13 | 12:00 | 2024-05-13 | 15:23 | 0.030865 | 0.00036142 | 131 | 11187 | Unplanned | THIRD PARTY INTERFERENCE - OVERHEAD CONTACT | REGULATORY INFORMATION Voltage & Device ID: CB C893 Protection flags (nil where none): EF CAUSE: digger working under CAC 89805 hit the lines and has brought them down in multiple sites Location: Pole 815283 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: ETA 20min Given to Fire Comms | .
4570 |  | JE24016710 | TAWAHA | Western | TAWAHA | 2024-05-13 | 15:42 | 2024-05-13 | 16:29 | 0.017116 | 0.00036142 | 131 | 6204 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: CB C893 Protection flags (nil where none): EF CAUSE: loose binder hanging on the line touching the cross arm. Suspect this was a secondary fault related to a digger hitting the lines earlier. Location: Pole 815283 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4571 |  | JE24016543 | ROTOEHU | Eastern | ROTOEHU | 2024-05-12 | 3:28 | 2024-05-12 | 8:48 | 0.068061 | 0.00042212 | 153 | 24669 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 9556 Protection flags (nil where none): É/F CAUSE: Line over tight broke on cold day, All Lines resaged, backed off eye bolts on strains Location: Pole 228246 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Frost ish LFI (Y/N + Comments): nil Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4572 |  | JE24016560 | WHIRITOA | Eastern | WHIRITOA | 2024-05-12 | 9:35 | 2024-05-12 | 11:05 | 0.0017362 | 1.9313e-05 | 7 | 629 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: DTX No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 11:05 Cause: LV Shackel Bolt Rusted out and gave way, Causing LV line Clash & blowing 2 x 2A HV Fuses Weather (wind/rain): Slight wind Follow up required (select advisory)? | .
4573 |  | JE24016582 | BROOKLANDS 7 | Western | BROOKLANDS 7 | 2024-05-12 | 13:19 | 2024-05-12 | 14:40 | 0.00045015 | 5.5179e-06 | 2 | 163 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 8446 No. Fuses: 2 Fuse Amp Size: 2 Amp TIME CLOSED: 14:40 Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)? N | .
4574 |  | JE24016592 | PEAT ST 33KV | Western | PEAT ST 33KV | 2024-05-12 | 14:43 | 2024-05-12 | 14:51 | 0.11319 | 0.018725 | 6787 | 41025 | Unplanned | HUMAN ERROR - PROTECTION SETTINGS - INCORRECT/ERROR | REGULATORY INFORMATION Voltage & Device ID: 33kV CB 3092 Protection flags (nil where none): A, B, C, Ph O/C CAUSE: Possible inrush load on restoring Load control Location: Peat St Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: N/A Weather (wind/rain): Calm LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Peat St, Kai Iwi, Castlecliff (momentary due to auto changeover) Circuit that tripped: CB 3092 DTF (KM): N/A | .
4575 |  | JE24016611 | COLVILLE | Eastern | COLVILLE | 2024-05-12 | 21:41 | 2024-05-13 | 1:27 | 0.016209 | 7.1733e-05 | 26 | 5875 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 9927/6 No. Fuses: 1 Fuse Amp Size: 8 TIME CLOSED: 01:27 Cause: Possible possum Weather (wind/rain): Fine Follow up required (select advisory)? No TC680 & Recloser 9927/6 Fuse Blown line is single phase so total loss of power (hence 2 or more phases selected for reporting purposes). TC680 Fuse replaced 01:25 Recloser 9927/6 Fuse replaced 01:27 (power on time) Recloser is bypassed in field & /6 would normally be links not a Fuse Faultman contacted customer power is on after fuse reload Faultman suspects opossum as cause as many out on this night | .
4576 |  | JE24012360 | 204 JELLICOE CRESCENT THAMES THAMES | Eastern | QUEEN ST | 2024-05-11 | 9:00 | 2024-05-11 | 11:32 | 0.018099 | 0.00012139 | 44 | 6560 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install 33kv post insulators on top circuit 11kv. Lower bottom circuit 11kv xarms 1 hole to maintain 1200mm seperation between circuits | .
4577 |  | JE24016474 | 177 MEREMERE ROAD, HAWERA, 4672 | Western | MEREMERE | 2024-05-11 | 9:34 | 2024-05-11 | 13:31 | 0.018308 | 7.7251e-05 | 28 | 6636 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Transformer W2390 to be changed 11/05/23, on 2R left open 11/05/2024 Isolated at ABS 6439 & Links 12282/4, 12266/4 & 12294 Back feed installed Via ABS 6537 & Sw/Gear 12276/3 Transformer changed | .
4578 |  | JE24016522 | OHAUITI RD | Eastern | OHAUITI RD | 2024-05-11 | 14:11 | 2024-05-11 | 18:29 | 0.020858 | 0.00030073 | 109 | 7560 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Sec 13135, Rec 9209 A/R Protection flags (nil where none): E/F O/C CAUSE: Cable fault found Location: Fuses SE4-66 Temp generation (state details when used): Yes, 25kVa PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: F3/F4 Cursory patrolled Weather (wind/rain): Fine LFI (Y/N + Comments): No Follow up Required (select advisory)? Yes Additional fault restoration comments: Found faulty cable past Fuses SE4-066 LV break made on 230V tails of TE4-209 & GEN connected. Cable Repaired Power Restored 13/05/24 @ 15:01 | .
4579 |  | JE24016962 | NGATAWA | Western | NGATAWA | 2024-05-11 | 9:02 | 2024-05-11 | 9:06 | 0.00093317 | 0.0002014 | 73 | 338 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kv CB 9 during isolation switching for NAPA 109205 Protection flags (nil where none): CAUSE: Faulty ABS 1409 Location: Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): 2405010 Circuit patrolled and type: No Weather (wind/rain): Calm LFI (Y/N + Comments): Nil Follow up Required (select advisory)? No Additional fault restoration comments: | .
4580 |  | JE24011648 | 376 MINDEN ROAD TE PUNA TAURANGA | Eastern | WAIPUNA | 2024-05-10 | 9:30 | 2024-05-10 | 9:59 | 0.0079687 | 0.00028141 | 102 | 2888 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | install 11kV LFI's smart navigator 2.0 LFIs at Pole 213162 | .
4581 |  | JE24011704 | 26 KESTREL AVENUE WELCOME BAY TAURANGA | Eastern | VICTORY STREET | 2024-05-10 | 8:31 | 2024-05-10 | 12:35 | 0.047245 | 0.00019313 | 70 | 17124 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace cable-box compartment dividers at SD switchgear 9128 | .
4582 |  | JE24011781 | 82 CENTENNIAL AVENUE TE AROHA TE AROHA | Eastern | STANLEY AVE | 2024-05-10 | 9:00 | 2024-05-10 | 11:56 | 0.039783 | 0.00022623 | 82 | 14420 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance 9455-1/2/3 | .
4583 |  | JE24011883 | 452 KAI IWI VALLEY ROAD KAI IWI WANGANUI | Western | MISSION RD | 2024-05-10 | 9:51 | 2024-05-10 | 11:39 | 0.00060063 | 5.5179e-06 | 2 | 218 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Lightning Arrestors on X920 | .
4584 |  | JE24011893 | 13 BROADVIEW HEIGHTS KAI IWI WANGANUI | Western | MISSION RD | 2024-05-10 | 9:15 | 2024-05-10 | 11:09 | 0.0037665 | 3.3108e-05 | 12 | 1365 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Lightning Arrestors on X3193 | .
4585 |  | JE24011975 | 6253 STATE HIGHWAY 1 MANGAWEKA MANGAWEKA | Western | MANGAWEKA | 2024-05-10 | 9:19 | 2024-05-10 | 14:06 | 0.0079053 | 2.759e-05 | 10 | 2865 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Transformer X1641 and Xarm. | .
4586 |  | JE24014402 | 279 CROSS ROAD HUIRANGI NEW PLYMOUTH | Western | WAITARA RD | 2024-05-10 | 9:15 | 2024-05-10 | 11:56 | 0.0013271 | 8.2769e-06 | 3 | 481 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Safety isolation Hv fuses TX 518 to carry LV crossarm changes between 11kV poles 742447 and 742441. | .
4587 |  | JE24016379 | BUFFALO BEACH | Eastern | BUFFALO BEACH | 2024-05-10 | 11:03 | 2024-05-13 | 14:37 | 0.064456 | 1.9313e-05 | 7 | 23362 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Transformer TC4196 Faulty , by negotiation with farmer to be replaced Sunday or Monday Isolation for safety reasons will need to be Fuses FC2214 The other transformer affected will be TC3902 which supplies PCO Maungatawhiri Repeater. Replaced 13/05/24 | .
4588 |  | JE24016429 | PROSPECT ST | Eastern | PROSPECT ST | 2024-05-10 | 12:51 | 2024-05-10 | 13:31 | 0.0083231 | 0.00020416 | 74 | 3017 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Faulty Fuse boxes/holders found on the LV side of TFR TC3713, due to old age Isolated at Sw/Gear IC3070 & 13749/3 LV fuse holders replaced, full power restored | .
4589 |  | JE24011175 | 57 RITCHIE STREET TE AROHA TE AROHA | Eastern | STANLEY AVE | 2024-05-09 | 9:14 | 2024-05-09 | 12:33 | 0.033088 | 0.00016554 | 60 | 11993 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance 9179-1/2/3 | .
4590 |  | JE24011184 | 1022 TAUMATA ROAD OMANAWA TAURANGA | Eastern | PYES PA | 2024-05-09 | 8:58 | 2024-05-09 | 15:10 | 0.042121 | 0.00011312 | 41 | 15267 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV Poles 217087, 217089, 217090, 217092. Replace 11kV cross arms at Poles 217084,217085, 217086, 217088, 217091. Replace 11kV and LV conductors with Ferret & PVC Ferret. | .
4591 |  | JE24011670 | 163 TE PUNA ROAD TE PUNA | Eastern | PLUMMERS POINT | 2024-05-09 | 9:32 | 2024-05-09 | 17:26 | 0.0091594 | 1.9313e-05 | 7 | 3320 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 200708, remove ABS SD3-073 and replace with with ENTEC LBS 14828, remove LFI's. Replace pole 393253 | .
4592 |  | JE24011677 | 2883A MANGAMAHU ROAD KAKATAHI WANGANUI | Western | FORDELL | 2024-05-09 | 9:05 | 2024-05-09 | 14:16 | 0.049788 | 0.00016002 | 58 | 18046 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Red Tagged 11KV Pole 791179 | .
4593 |  | JE24011714 | 1591 STATE HIGHWAY 56 TIAKITAHUNA PALMERSTON NORTH | Western | BAINESSE | 2024-05-09 | 8:47 | 2024-05-09 | 12:46 | 0.00066146 | 2.759e-06 | 1 | 240 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace multiple 11kV crossarms between poles P45298 and P45006. Re-use transformer T2/606. | .
4594 |  | JE24011848 | 1450 NAPIER ROAD ASHHURST ASHHURST | Western | AOKAUTERE | 2024-05-09 | 9:31 | 2024-05-09 | 14:22 | 0.062395 | 0.0002152 | 78 | 22615 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | install new pole between P15393 and P01318 and move Abs E74 to new pole. | .
4595 |  | JE24012729 | 754 PLYMOUTH ROAD KORU NEW PLYMOUTH | Western | PIONEER RD | 2024-05-09 | 9:00 | 2024-05-09 | 14:52 | 0.085482 | 0.00024279 | 88 | 30983 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Worksite - String 14 x span of Squirrel conductor from pole 755291-755278 | .
4596 |  | JE24012746 | 1086 JUNCTION ROAD EGMONT VILLAGE INGLEWOOD | Western | JUNCTION RD | 2024-05-09 | 9:30 | 2024-05-09 | 14:30 | 0.0033148 | 1.1036e-05 | 4 | 1201 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To Replace Tx structure 678 and leaking 30kva TX | .
4597 |  | JE24013581 | 1108 AUROA ROAD AUROA HAWERA | Western | RIVERLEA | 2024-05-09 | 9:45 | 2024-05-09 | 13:26 | 0.0012208 | 5.5179e-06 | 2 | 443 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | unbind poles 942681 to 942685 and resag the whole spur line at tx pole. | .
4598 |  | JE24014393 | 368 IRONWORKS ROAD HUNTERVILLE HUNTERVILLE | Western | HUNTERVILLE 22KV | 2024-05-09 | 9:01 | 2024-05-09 | 15:41 | 0.027588 | 6.8974e-05 | 25 | 10000 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Reconductoring 11kV line between poles 807675 & 807706. Relocate Fuses 2855 from pole 807675 to 850108 Weather caused a delay in the reconductoring | .
4599 |  | JE24014564 | 1464A MASTERTON STRONVAR ROAD WAINUIORU MASTERTON | Western | WERAITI | 2024-05-09 | 8:45 | 2024-05-09 | 13:13 | 0.070991 | 0.00026486 | 96 | 25731 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles 827463,464,465,466,467,and 462 installing new fuses on this site | .
4600 |  | JE24016201 | PIHAMA | Western | PIHAMA | 2024-05-09 | 3:22 | 2024-05-09 | 8:49 | 0.075165 | 0.00066215 | 120 | 27244 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: REC 12194/2 found tripped Protection flags (nil where none): E/F, O/C B CAUSE: Broken binder, floating conductor Location: 718171 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): windy LFI (Y/N + Comments): n Follow up Required (select advisory)? Is there a reason why we do not have comms to REC 12194? There is comms to REC 12345 a few poles away. Having comss would reduce outage times and increase response times. Additional fault restoration comments: Isolated at ABS TA815 & 8831/1 faulty binder replaced, full power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4601 |  | JE24016207 | KUMENGA | Western | KUMENGA | 2024-05-09 | 9:06 | 2024-05-09 | 12:19 | 0.0037293 | 1.9313e-05 | 7 | 1352 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | Faultman found branch on lines at pole 798791, line was isolated at Fuses 11226 to remove the branch and resag the lines. | .
4602 |  | JE24016214 | MANAIA | Western | MANAIA | 2024-05-09 | 14:59 | 2024-05-09 | 16:25 | 0.0073826 | 9.3805e-05 | 34 | 2676 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faulty DDO's to TFR M4275, due to old age, holder will not hold the barrel in place, barrel keeps falling out Isolated at ABS 6711, 8762/1 & Links 8762/6 1 x set of DDO's replaced, full power restored | .
4603 |  | JE24016218 | RUAWHATA | Western | RUAWHATA | 2024-05-09 | 8:36 | 2024-05-09 | 9:49 | 0.017687 | 0.00024279 | 88 | 6411 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faultman found broken DDO at Fuses Q47, line was isolated at ABS's Q46 & Q52 to replace the full set of DDO's and replace the cross arm and this was due to deuteriation. | .
4604 |  | JE24016225 | KATERE 8 | Western | KATERE 8 | 2024-05-09 | 8:43 | 2024-05-09 | 10:46 | 0.27033 | 0.0048668 | 1764 | 97981 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: CB 8 Protection flags (nil where none): E/F CAUSE: Faulty Deadend due to age Location: 749991 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): windy LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: line down reported, faultman isolated faulted section of line, back feed put in place for line past ABS 51 from BLK15, inrush current tripped Rec 8765, device Auto reclosed Isolated at Sw/Gear 454/3 & ABS 51 Deadends and insulators replaced, full power restored | .
4605 |  | JE24016300 | OKAIAWA | Western | OKAIAWA | 2024-05-09 | 14:41 | 2024-05-09 | 18:49 | 0.006249 | 4.9661e-05 | 18 | 2265 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Broken DDO's to TFR M3108, DDO broken in half due to old age Isolated at ABS's MA415 & MA579 1 x set of DDO'S replaced, full power restored | .
4606 |  | JE24016314 | ASHHURST | Western | ASHHURST | 2024-05-09 | 9:31 | 2024-05-09 | 14:22 | 0.00080258 | 2.759e-06 | 1 | 291 | Unplanned | OTHER | Cause: Customer turned off their Switch. IS 2R required? N Additional Info: HV NAPA 109595 Was related to aHV NAPA in the area - Customer turned of his main switch and forgot to turn it back on again. (ICP not advertised so outage is unplanned) | .
4607 |  | JE24011157 | 26A TAIHOA SOUTH ROAD MATAMATA MATAMATA | Eastern | TAIHOA | 2024-05-08 | 9:26 | 2024-05-08 | 14:07 | 0.0054275 | 1.9313e-05 | 7 | 1967 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace crossarms on 11kV Pole F12882 (TC2412). | .
4608 |  | JE24011697 | 43 HAYBITTLE STREET FEILDING FEILDING | Western | DENBIGH | 2024-05-08 | 5:00 | 2024-05-08 | 6:04 | 0.063837 | 0.00099599 | 361 | 23138 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Repair earthing between cable screen and main ABS earth. | .
4609 |  | JE24011961 | 973 FITZHERBERT EAST ROAD AOKAUTERE PALMERSTON NORTH | Western | AOKAUTERE | 2024-05-08 | 9:30 | 2024-05-08 | 16:50 | 0.023631 | 0.00018209 | 66 | 8565 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Make line break P34779 then replace 11KV line from Rec 10367 to P35448 Close line break | .
4610 |  | JE24012819 | 25 MOORHOUSE STREET MORRINSVILLE MORRINSVILLE | Eastern | LORNE ST | 2024-05-08 | 8:50 | 2024-05-08 | 11:34 | 0.00045123 | 2.759e-06 | 1 | 164 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance 9785-1/2/3 Rewrite of NAPA 106121 - SW/Gear IC1505 re numbered to 14805/1 . Advertising under NAPA 106121 | .
4611 |  | JE24014093 | 281 CENTENNIAL DRIVE OMATA NEW PLYMOUTH | Western | NGAMOTU RD | 2024-05-08 | 9:31 | 2024-05-08 | 10:43 | 0.0010004 | 1.3795e-05 | 5 | 363 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Red Defect repairs on Defective hotspot ABS 553 | .
4612 |  | JE24014567 | 385 MAUNGATAPU ROAD MAUNGATAPU TAURANGA | Eastern | MATAPIHI RD | 2024-05-08 | 10:15 | 2024-05-08 | 15:24 | 0.067407 | 0.00021796 | 79 | 24432 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace a faulty RMU unit. | .
4613 |  | JE24015579 | 636 NGATIRA ROAD NGATIRA PUTARURU | Eastern | LICHFIELD | 2024-05-08 | 10:01 | 2024-05-08 | 12:41 | 0.0013249 | 8.2769e-06 | 3 | 480 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE POLE 878926 FOR 11M, REPLACE CROSS-ARM ON POLE 878927 | .
4614 |  | JE24016083 | SPRINGDALE | Eastern | SPRINGDALE | 2024-05-08 | 3:49 | 2024-05-08 | 6:25 | 0.00086 | 5.5179e-06 | 2 | 312 | Unplanned | WILDLIFE - BIRD | Fuses Location: FC4233 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 06:25 Cause: Bird strike Weather (wind/rain): calm Follow up required (select advisory)? | .
4615 |  | JE24016117 | RANGIWAHIA | Western | RANGIWAHIA | 2024-05-08 | 13:10 | 2024-05-08 | 14:55 | 0.0011639 | 1.1036e-05 | 4 | 422 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Broken DDO Fuse holder to TFR T5/40, Pole P05203, due to old age Isolated at Fuses N14 2 X DDO's Replaced, Full power restored | .
4616 |  | JE24016119 | CAMBRIDGE RD TIRAU | Eastern | CAMBRIDGE RD TIRAU | 2024-05-08 | 9:47 | 2024-05-08 | 12:03 | 0.0026185 | 1.9313e-05 | 7 | 949 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses FP666 No. Fuses: 2 Fuse Amp Size: 6 Amp TIME CLOSED: 12:02 Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)? No | .
4617 |  | JE24016168 | OAKURA | Western | OAKURA | 2024-05-08 | 15:55 | 2024-05-08 | 17:45 | 0.010574 | 9.6564e-05 | 35 | 3833 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Fuses 8497 Protection flags (nil where none): 1 x HV Fuse was blown due to Line down on the ground. CAUSE: Corrosion (16mm Copper wire) Coastal area. Location: Pole 756 124 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Clear LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: HAZARD - Report of Lines down causing Part Power. Field Switcher found one HV Line down on the ground and the HV Fuses at 8497 had operated/blown. Isolation then carried out at Fuses 8497 and repairs are being carried out under AP 6168-01. Repair HV Conductor & replace burnt cross-arm. All repairs completed and full Power restored at 17:44 | .
4618 |  | JE24011035 | 1022 TAUMATA ROAD OMANAWA TAURANGA | Eastern | PYES PA | 2024-05-07 | 9:16 | 2024-05-07 | 15:50 | 0.065288 | 0.00016554 | 60 | 23664 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | NAPA#:109028 Replace 11kv/400vt poles,216966, 216967, 217082, 216968, 217083. Isolation point @ Temp 22: Issuers earths @ pole 216964 (216965 side). | .
4619 |  | JE24011143 | 32 SAPPHIRE DRIVE HAIRINI TAURANGA | Eastern | POIKE | 2024-05-07 | 8:30 | 2024-05-07 | 14:32 | 0.12265 | 0.00033935 | 123 | 44456 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace fuse-switch (S4523) SDAF base unit, corrosion due to soil ingress into transformer (T4514) HV cable-box. | .
4620 |  | JE24011155 | 43 STANLEY AVENUE TE AROHA TE AROHA | Eastern | STANLEY AVE | 2024-05-07 | 9:31 | 2024-05-07 | 10:09 | 0.0048929 | 0.00012967 | 47 | 1773 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance 9279-1/2/3 Job cancelled, due to school in the outage area not advertised (switching used, power off to ICPs for ~1 hour) | .
4621 |  | JE24011632 | 5 GUMTREE RISE OTAMATEA WANGANUI | Western | ST JOHNS | 2024-05-07 | 8:31 | 2024-05-07 | 9:04 | 0.01048 | 0.00031176 | 113 | 3799 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Top transformer X3153 up with oil via oil valve at base | .
4622 |  | JE24011636 | 108 KAIMATIRA ROAD OKOIA WANGANUI | Western | NO 3 LINE | 2024-05-07 | 9:02 | 2024-05-07 | 15:28 | 0.0010645 | 2.759e-06 | 1 | 386 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace TX Pole X4257 - 790740 | .
4623 |  | JE24011638 | 1591 STATE HIGHWAY 56 TIAKITAHUNA PALMERSTON NORTH | Western | BAINESSE | 2024-05-07 | 8:49 | 2024-05-07 | 12:35 | 0.052984 | 0.00023451 | 85 | 19204 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace HV & LV crossarms and poles between P43036 and P43039 including 30kVA Transformer T2/258. | .
4624 |  | JE24011799 | 68 SEAFORTH ROAD WAIHI BEACH WAIHI BEACH | Eastern | SEAFORTH RD | 2024-05-07 | 9:04 | 2024-05-07 | 12:24 | 0.084143 | 0.00042212 | 153 | 30498 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Rotate 11kv links 14580/4 180'degrees so that when opened the links will open towards the sectionaliser. | .
4625 |  | JE24012609 | 762 PAIERAU ROAD OPAKI MASTERTON | Western | MOUNT BRUCE | 2024-05-07 | 9:30 | 2024-05-07 | 14:35 | 0.015114 | 4.9661e-05 | 18 | 5478 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Vegetation cutting between poles 831994 and 449270 | .
4626 |  | JE24012622 | 3458 RAWHITIROA ROAD MATEMATEAONGA ELTHAM | Western | RAWHITIROA | 2024-05-07 | 10:15 | 2024-05-07 | 15:16 | 0.0049711 | 1.6554e-05 | 6 | 1802 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Asplundh to cut trees between poles 736398 to 736406 | .
4627 |  | JE24012629 | 754 PLYMOUTH ROAD KORU NEW PLYMOUTH | Western | PIONEER RD | 2024-05-07 | 9:00 | 2024-05-07 | 13:00 | 0.010589 | 4.4143e-05 | 16 | 3838 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Worksite - Crew 1: Replace poles 755286, 755287, and 755288 (Digger operator needed) Crew 2: Replace poles 755299, 755300, and 755301 Crew 3: Replace poles 755302â€¦...... Crew 4: Replace poles 755313, 755314, and 755315 | .
4628 |  | JE24012706 | 1660 MOKAU ROAD URUTI URENUI | Western | MAIN RD MOTONUI | 2024-05-07 | 9:33 | 2024-05-07 | 12:10 | 0.0013061 | 8.2769e-06 | 3 | 473 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Isolation of Hv tx 2672 to carry out lv works | .
4629 |  | JE24012763 | 368 IRONWORKS ROAD HUNTERVILLE HUNTERVILLE | Western | HUNTERVILLE 22KV | 2024-05-07 | 8:45 | 2024-05-07 | 15:11 | 0.0095718 | 2.4831e-05 | 9 | 3469 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV Poles 807702, 807704, 807705, 807706. | .
4630 |  | JE24013810 | 67 RACECOURSE ROAD AWAPUNI PALMERSTON NORTH | Western | PASCAL ST 9 | 2024-05-07 | 10:01 | 2024-05-07 | 13:41 | 0.017008 | 7.7251e-05 | 28 | 6165 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace defect ABS A25 â€“ Vertical fused 11kv ABS at pole 318375 | .
4631 |  | JE24015134 | 316A KAHUTARA ROAD KAHUTARA FEATHERSTON | Western | DAIRY FACTORY | 2024-05-07 | 9:06 | 2024-05-07 | 10:00 | 0.0026867 | 4.9661e-05 | 18 | 974 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace broken 33kv insulators at poles 812558, 812563, 812568, 812553, 799601 | .
4632 |  | JE24015939 | MOROA | Western | MOROA | 2024-05-07 | 7:32 | 2024-05-07 | 8:35 | 0.0008751 | 1.3795e-05 | 5 | 317 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: 7504 No. Fuses: 2 Fuse Amp Size: 8 TIME CLOSED: 08:35 Cause: unknown Weather (wind/rain): overcast & cold Follow up required (select advisory)?n | .
4633 |  | JE24015982 | OTAKEHO | Western | OTAKEHO | 2024-05-07 | 10:13 | 2024-05-07 | 11:40 | 0.00048219 | 5.5179e-06 | 2 | 175 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: TX M2227 No. Fuses: 3 Fuse Amp Size: 3 Amp TIME CLOSED: 11:40 Cause: Corrosion Weather (wind/rain): Clear Follow up required (select advisory)? No Customer's Electrician reported fluctuating Power. At the Transformer the Voltage readings are within limits as per Peter Northcott Under investigation. LV testing for 2R Overloading on customers side. Advise the share the load or to upgrade TX | .
4634 |  | JE24015986 | OAONUI | Western | OAONUI | 2024-05-07 | 12:41 | 2024-05-07 | 14:23 | 0.0076603 | 7.4492e-05 | 27 | 2777 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Fuses TA718 Protection flags (nil where none): Nil CAUSE: Corrosion Location: Pole 713 623 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Windy LFI (Y/N + Comments): Nil Follow up Required (select advisory)? No Additional fault restoration comments: King bolt nut rusted off & HV cross-arm is lying on the LV arm. Isolation at Fuses TA718 Field Switcher is busy with repairs under AP 5986-01 Material used: King Bolt including washers, nut & two new binders. Full Power restored at 14:23 | .
4635 |  | JE24016010 | PLUMMERS POINT | Eastern | PLUMMERS POINT | 2024-05-07 | 14:24 | 2024-05-07 | 15:38 | 0.00061362 | 8.2769e-06 | 3 | 222 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses FP1091 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 15:38 Cause: Birds Weather (wind/rain): Calm Follow up required (select advisory)? No | .
4636 |  | JE24016020 | WAIHI NORTH | Eastern | WAIHI NORTH | 2024-05-07 | 16:22 | 2024-05-07 | 17:14 | 0.0068719 | 0.00013243 | 48 | 2491 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: Recloser 9604 Protection flags (nil where none): None CAUSE: Broken Dead End Location: Pole P13386 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Dead End replaced SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4637 |  | JE24016036 | PONATAHI | Western | PONATAHI | 2024-05-07 | 17:49 | 2024-05-07 | 18:42 | 0.021343 | 0.00039729 | 144 | 7736 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Blown Jumper at Pole 819019 (ABS S379) Backfeed put in place Isolated at ABS S344, S378 & CB C955 Jumper repaired, Full Power restored | .
4638 |  | JE24016074 | COROGLEN | Eastern | COROGLEN | 2024-05-07 | 22:58 | 2024-05-08 | 0:07 | 0.038386 | 0.00055179 | 200 | 13913 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faultman found burning connection from O/H line to transformer TC5541 on pole W1463, line was isolated at ABS 2703 to repair the connection. | .
4639 |  | JE24016077 | PAPANUI ST | Eastern | PAPANUI ST | 2024-05-07 | 22:23 | 2024-05-07 | 23:28 | 0.00088858 | 1.3795e-05 | 5 | 322 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: FC1441 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 23:27 Cause: unknown Weather (wind/rain): windy Follow up required (select advisory)?n | .
4640 |  | JE24010800 | 555 MILL CREEK ROAD KAIMARAMA WHITIANGA | Eastern | COROGLEN | 2024-05-06 | 9:02 | 2024-05-06 | 14:43 | 0.032056 | 9.3805e-05 | 34 | 11619 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV Pole W12654. Replace 11kV Transformer TC3507 and all hardware. | .
4641 |  | JE24011026 | 8 LEYLAND ROAD WHAKAMARAMA | Eastern | WHAKAMARAMA | 2024-05-06 | 8:47 | 2024-05-06 | 13:00 | 0.099327 | 0.00039177 | 142 | 36002 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | install 11kV LFI's with smart navigator 2.0 LFIs at Pole 210133 & 210117 | .
4642 |  | JE24012422 | 188 GOVETT AVENUE FRANKLEIGH PARK NEW PLYMOUTH | Western | BROOKLANDS 6 | 2024-05-06 | 8:30 | 2024-05-06 | 16:09 | 0.31993 | 0.002014 | 525 | 115961 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Existing site tx leaking and has Magnefix (1325) in enclosure. Site not viable for new equipment. Outage to disconnect existing equipment and systematically change to new location. Switchgear 1325 and TX 1325 to retain same numbers, new configuration. | .
4643 |  | JE24012760 | 368 IRONWORKS ROAD HUNTERVILLE HUNTERVILLE | Western | HUNTERVILLE 22KV | 2024-05-06 | 8:46 | 2024-05-06 | 15:11 | 0.0095503 | 2.4831e-05 | 9 | 3462 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 807695, 807697, 807698, 807700, 850116. Replace X-Arms 850111, 850112, 850113, 850114, 850115, 851073, 850103, 850104, 850105 | .
4644 |  | JE24013967 | 13 HARVARD WAY MOUNT MAUNGANUI TAURANGA | Eastern | AERODROME | 2024-05-06 | 19:31 | 2024-05-06 | 21:38 | 0.0021153 | 1.6554e-05 | 6 | 767 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace leaking G/M transformer TC4-379. | .
4645 |  | JE24015840 | GULLIVER RD | Eastern | GULLIVER RD | 2024-05-06 | 10:42 | 2024-05-06 | 16:19 | 0.011242 | 4.6902e-05 | 17 | 4075 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: Trf TE6-135 No. Fuses: 1 Fuse Amp Size: TIME CLOSED: Cause: Weather (wind/rain): Follow up required (select advisory)? yes No successful reload Blowing Fuses on Re Load, To change Transformer JE24015876 is a child of this job. Fuses FP1109 were opened because of MADs. (SAFETY) .On same pole as Trf TE6-135, Fuses Pole 485518 TRF TE6-135 Fuses ORT @ 10:42 - Transformer TE6-135 replaced, Fuses Closed @ 16:18 Fuses FP1109 ORT @ 12:56 - Closed @ 16:15 New Transformer is 50kVA from 30kVA | .
4646 |  | JE24015873 | IHAIA RD | Western | IHAIA RD | 2024-05-06 | 16:45 | 2024-05-06 | 19:22 | 0.0091967 | 0.00012691 | 25 | 3333 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV ABS TA108 changed to ABS TA106 & ABS TA122 Protection flags (nil where none): Nil CAUSE: Deterioration Location: Poles 715 696 & 715 705 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Change Cross-arms at both sites as per above. Due to the original Isolation at ABS TA108 which failed due to the B Ø not opening all the way. Isolation area had to be increased and include more ICP's for this fault. New Isolation points are at ABS TA106 & ABS TA122 DNO 240 5004 created for ABS TA108 | .
4647 |  | JE24015877 | LEEDSTOWN 22KV | Western | LEEDSTOWN 22KV | 2024-05-06 | 13:21 | 2024-05-06 | 13:24 | 1.7014e-05 | 5.5179e-06 | 2 | 6 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 2708 No. Fuses: 2 Fuse Amp Size: 15 Amp TIME CLOSED: 13:23 Cause: Suspect ducks near the pond. Weather (wind/rain): Overcast Follow up required (select advisory)? No | .
4648 |  | JE24015886 | 477 LANGDALE ROAD, MANGAPAKEHA, MASTERTON, 5872 | Western | LANGDALE | 2024-05-06 | 15:36 | 2024-05-06 | 16:00 | 6.6629e-05 | 2.759e-06 | 1 | 24 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Voltage checked at 246V Transformer is set to Tap 3, next transformer up and down the feeder are both set to Tap 2. Outage to tap DTX T103 down to Tap 2 and voltage now 239V | .
4649 |  | JE24015917 | IRIRANGI | Western | IRIRANGI | 2024-05-06 | 17:17 | 2024-05-06 | 22:14 | 0.022899 | 7.7251e-05 | 28 | 8300 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 2601 No. Fuses: 2 Fuse Amp Size: 8 Amp TIME CLOSED: 22:13 Cause: Unknown Weather (wind/rain): Calm, Light Rain Follow up required (select advisory)? N | .
4650 |  | JE24015919 | CAMBRIDGE RD TIRAU | Eastern | CAMBRIDGE RD TIRAU | 2024-05-06 | 18:08 | 2024-05-06 | 21:25 | 0.10907 | 0.00074492 | 270 | 39534 | Unplanned | WILDLIFE - POSSUM | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 9773/2 Protection flags (nil where none): E/F CAUSE: Opossum Location: Pole D1106 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: cursory Weather (wind/rain): calm LFI (Y/N + Comments): Yes, LFI at Pole D12657 is offline & LFI at Pole D12618 did not operate. Follow up Required (select advisory)? Yes Additional fault restoration comments: Opossum removed from lines with hot line sticks. | .
4651 |  | JE24015756 | PIHAMA | Western | PIHAMA | 2024-05-05 | 0:09 | 2024-05-05 | 1:58 | 0.0035844 | 3.3108e-05 | 12 | 1299 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: TA805 No. Fuses: 2 Fuse Amp Size: 10 Amp TIME CLOSED: 01:57 Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)? N | .
4652 |  | JE24015765 | CLOTON RD NORTH | Western | CLOTON RD NORTH | 2024-05-05 | 6:39 | 2024-05-05 | 8:44 | 0.014858 | 0.00011864 | 43 | 5385 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: FABS 5539 No. Fuses: 2 Fuse Amp Size: 25A TIME CLOSED: 0844 Cause: Unknown Weather (wind/rain): fine Follow up required (select advisory)? | .
4653 |  | JE24015766 | DAIRY FACTORY | Western | DAIRY FACTORY | 2024-05-05 | 8:14 | 2024-05-05 | 9:46 | 0.0022785 | 2.4831e-05 | 9 | 826 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses 7236 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 09:45 Cause: Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? No | .
4654 |  | JE24015774 | 2704 OPUNAKE ROAD, OPUNAKE, 4682 | Western | IHAIA RD | 2024-05-05 | 12:07 | 2024-05-05 | 13:19 | 0.0003949 | 5.5179e-06 | 2 | 143 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Replace cross arm at Pole 714664. Isolation via unnumbered fuses on same pole | .
4655 |  | JE24015788 | OAKURA | Western | OAKURA | 2024-05-05 | 15:37 | 2024-05-05 | 17:16 | 0.0021731 | 2.2072e-05 | 8 | 788 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 6432 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 1715 Cause: Unknown Weather (wind/rain): fine Follow up required (select advisory)? | .
4656 |  | JE24014129 | 46 Reta Crescent, Kerepehi 3671 | Eastern | NGATEA | 2024-05-04 | 9:05 | 2024-05-04 | 11:23 | 0.0095188 | 6.8974e-05 | 25 | 3450 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole O3050 | .
4657 |  | JE24015714 | SOUTH RD NGARIKI | Western | SOUTH RD NGARIKI | 2024-05-04 | 9:10 | 2024-05-04 | 9:48 | 0.00041844 | 1.1036e-05 | 4 | 152 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Jumper out at Transformer N3340 Isolated at Fuses NG380 Repaired jumper all Good Power Off at 09:09 Power on at 09:47 | .
4658 |  | JE24015718 | COUNTY WATER | Eastern | COUNTY WATER | 2024-05-04 | 7:49 | 2024-05-04 | 10:45 | 0.0047952 | 3.8625e-05 | 14 | 1738 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses FC823 No. Fuses: 2 Fuse Amp Size: 8A TIME CLOSED: 10:45 Cause: Ducks Weather (wind/rain): Calm Follow up required (select advisory)?No | .
4659 |  | JE24015719 | RANGIWAHIA | Western | RANGIWAHIA | 2024-05-04 | 8:53 | 2024-05-04 | 10:49 | 0.0003206 | 2.759e-06 | 1 | 116 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: N27 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 10:48 Cause: Unknown Weather (wind/rain): Fine Follow up required (select advisory)? | .
4660 |  | JE24015735 | IHAIA RD | Western | IHAIA RD | 2024-05-04 | 16:19 | 2024-05-04 | 17:13 | 0.0023587 | 4.4143e-05 | 16 | 855 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Split crossarm at Pole 714313 Isolated at Fuses TA191 Power off at 16:19 Power on at 17:12 | .
4661 |  | JE24015755 | OAONUI | Western | OAONUI | 2024-05-04 | 22:15 | 2024-05-05 | 0:58 | 0.022212 | 0.00051869 | 188 | 8051 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV CB TA7 Protection flags (nil where none): DefT E/F CAUSE: Line Down Location: Pole 713629 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4662 |  | JE24011115 | 19 PHILLIPS ROAD NGATEA NGATEA | Eastern | COUNTY WATER | 2024-05-03 | 9:30 | 2024-05-03 | 14:14 | 0.053582 | 0.00019037 | 69 | 19421 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE POLE O750 AND INSTALL NEW REC NOJA 14813/2 & 14813/4. FOR FUTURE FEEDER KPE7. COMMs NOJA SWITCH TECH WILL BE WORKING UNDER OUR AP USING INVERTER APPLY AC V TO UNIT FOR TESTING. | .
4663 |  | JE24011225 | 368 RAUMAI ROAD BULLS BULLS | Western | LAKE ALICE | 2024-05-03 | 9:43 | 2024-05-03 | 12:32 | 0.00093418 | 5.5179e-06 | 2 | 339 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Upgrade TX X1105 from 15KVA to 30KVA | .
4664 |  | JE24011606 | 303 BAINESSE ROAD GLEN OROUA PALMERSTON NORTH | Western | BAINESSE | 2024-05-03 | 8:30 | 2024-05-03 | 12:48 | 0.018502 | 7.1733e-05 | 26 | 6706 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Access Permit to replace multiple poles and arms | .
4665 |  | JE24011617 | 595 WARDS LINE MORRISONS BUSH GREYTOWN | Western | TAWAHA | 2024-05-03 | 9:30 | 2024-05-03 | 13:13 | 0.004922 | 2.2072e-05 | 8 | 1784 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Straighten T2358 and pole 799946 and re sag 11kv lines between poles | .
4666 |  | JE24011621 | 1250A TE WHITI ROAD GLADSTONE MASTERTON | Western | PUKETIRO | 2024-05-03 | 9:45 | 2024-05-03 | 11:07 | 0.0011278 | 1.3795e-05 | 5 | 409 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv fuse arm at T951 live line | .
4667 |  | JE24011720 | 200 PARIHAKA ROAD PUNGAREHU OPUNAKE | Western | PARIHAKA | 2024-05-03 | 9:31 | 2024-05-03 | 12:15 | 0.0031628 | 1.9313e-05 | 7 | 1146 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To change defective crossarm and straighten pole 710469 | .
4668 |  | JE24012145 | 1159 FITZHERBERT EAST ROAD AOKAUTERE PALMERSTON NORTH | Western | AOKAUTERE | 2024-05-03 | 9:00 | 2024-05-03 | 14:16 | 0.019431 | 0.00017106 | 42 | 7043 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11Xarms between Temp 086 & Pole P35416. | .
4669 |  | JE24012756 | 449 BRUNSWICK ROAD BRUNSWICK WANGANUI | Western | BRUNSWICK | 2024-05-03 | 9:15 | 2024-05-03 | 11:54 | 0.0074669 | 4.6902e-05 | 17 | 2706 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 33KV Sleeves at pole 706710 & replace 11KV poles & X-Arms between 706710 & 782728 | .
4670 |  | JE24015357 | 2 BRUCE ROAD TOKO STRATFORD | Western | TOKO | 2024-05-03 | 9:15 | 2024-05-03 | 11:05 | 0.0054545 | 4.9661e-05 | 18 | 1977 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace badly rotten LV fuse arms at pole 740061 | .
4671 |  | JE24015546 | PAREWANUI | Western | PAREWANUI | 2024-05-03 | 6:51 | 2024-05-03 | 8:32 | 0.0011141 | 1.1036e-05 | 4 | 404 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: 4946 No. Fuses: 2 Fuse Amp Size: 8 TIME CLOSED: 08:31 Cause: Unknown Weather (wind/rain): calm Follow up required (select advisory)?n | .
4672 |  | JE24015553 | OTAKEHO | Western | OTAKEHO | 2024-05-03 | 7:39 | 2024-05-03 | 9:31 | 0.0083213 | 7.4492e-05 | 27 | 3016 | Unplanned | WILDLIFE - BIRD | Fuses Location: MA233 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 09:30 Cause: Bird strike at Pole 717868 Weather (wind/rain): calm Follow up required (select advisory)?n | .
4673 |  | JE24015556 | TE PUKE QUARRY RD | Eastern | TE PUKE QUARRY RD | 2024-05-03 | 8:07 | 2024-05-03 | 8:38 | 0.050528 | 0.0030349 | 1100 | 18314 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 33kV KMO 2182 Protection flags (nil where none): 2182 Auto-reclosed until lock out no flags, flags on SEC 3227 OC A & C phase CAUSE: Tree fire under lines possible cause being load causing lines to droop. Location: Between ABS 3165 to ABS 2007 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: - Cursory Weather (wind/rain): clear LFI (Y/N + Comments): SAP 13736939 vicinity of ABS 2007 3 phase lit up towards ABS 2007 (correct indication) Follow up Required (select advisory)? yes Additional fault restoration comments: Planned NAPA 110279 placed ATU from TMI over to KMO GXP. Bush fire started under lines that had been energised previously with no load. Suspect line droop caused lines to touch tree and cause bush fire. Major voltage drop at ATU sub when moved from TMI to KMO Circuit approx 300A @ 33kV. T7 dropped down to 10.1 kV and wasn't tapping, manually tapped up to tap 13 , placed in auto on tap 13 @ 10.8KV, T7 then tapped to tap 14. During restoration not able to back feed all of ATU due to high loads and risk of tripping donor. A close of CB2 @ ATU failed due to suspected circulating current trying to place load on TPV with TPV down to one bank. Make before break switching to rest | .
4674 |  | JE24015562 | MAIN RD MOTONUI | Western | MAIN RD MOTONUI | 2024-05-03 | 10:22 | 2024-05-03 | 12:03 | 0.0092518 | 9.1046e-05 | 33 | 3353 | Unplanned | WILDLIFE - BIRD | Line clash due to Bird strike Mid span Past Pole 764804, broken strands in conductors Isolated at Fuses 5301 Faulty conductor Fixed, Full power restored also replaced 1 x Barrel & 3 Fuses | .
4675 |  | JE24015569 | RAHOTU | Western | RAHOTU | 2024-05-03 | 9:27 | 2024-05-03 | 10:37 | 0.0084855 | 0.00012139 | 44 | 3076 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Broken binder found at Pole 712030, O/H Line hanging from jumper HV/LV line clash, customers isolated at service fuses Isolated at ABS NG248 & NG237 Binder replaced, full power restored Customers inspected, Customers at 387 & 397 OK power restored, Old shed for address 425 Mid Kahui Rd, ICP 0043751602PCC3B, service isolated due to meter damage, Tag A47164 Retailer e-mailed Tag Reg Updated | .
4676 |  | JE24015571 | PARK RD | Western | PARK RD | 2024-05-03 | 8:32 | 2024-05-03 | 10:39 | 0.00035043 | 2.759e-06 | 1 | 127 | Unplanned | WILDLIFE - BIRD | Fuses Location: 7598 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 10:38 Cause: Goose Weather (wind/rain): Fine Follow up required (select advisory)? | .
4677 |  | JE24015593 | BAINESSE | Western | BAINESSE | 2024-05-03 | 8:30 | 2024-05-03 | 12:48 | 0.00071163 | 2.759e-06 | 1 | 258 | Unplanned | OTHER | Cause: Part of Planned shut 109695 What was replaced? FM confirmed that property is fed from TX T1/442 Where was it replaced (pole/TX/pillar box)? Is 2R required? N 2R Y - What is the timeframe for repairs? Planned Shut Additional Info: Part of Shut TX T1/442 Not fed From TX T1/303 AI team e-mailed Yes This ICP not advertised, outage is unplanned. | .
4678 |  | JE24015599 | NEW ROAD, STRATFORD, 4392 | Western | TOKO | 2024-05-03 | 14:00 | 2024-05-03 | 15:15 | 0.0016576 | 2.2072e-05 | 8 | 601 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Burnt cross arm at Pole 740246 & fault cross arm and faulty insulator at pole 740249 Isolated at Fuses 4966 Cross arms and hardware replaced at poles 740246 & 740249, Full power restored | .
4679 |  | JE24015677 | 220 OHAWE ROAD, OHAWE, HAWERA, 4671 | Western | KETEMARAE RD | 2024-05-03 | 17:48 | 2024-05-03 | 19:10 | 0.00022725 | 2.759e-06 | 1 | 82 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Leaking TFR 5496E Fuses Isolated at TFR 5496E Fuses TFR Replaced, Full Power restored | .
4680 |  | JE24015696 | TAITIMU | Eastern | TAITIMU | 2024-05-03 | 18:57 | 2024-05-03 | 22:01 | 0.00049768 | 5.5179e-06 | 1 | 180 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Fused/Sw 13686/4 opened 1 X blown fuse the cable and transformer were tested, 3 x 63A HV HRC Fuses replaced and re-livened, installation tested ok. | .
4681 |  | JE24015700 | pole_219699 | Eastern | BRUCE RD | 2024-05-03 | 21:26 | 2024-05-03 | 22:30 | 0.032058 | 0.0012471 | 452 | 11619 | Unplanned | WILDLIFE - POSSUM | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 5 Protection flags (nil where none): E/F B Ø CAUSE: Possum Location: Pole 219699 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F4, Cursory patrolled. Weather (wind/rain): Calm LFI (Y/N + Comments): None installed Follow up Required (select advisory)? No Additional fault restoration comments: Dead possum found at pole 219699 base, no damage caused. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4682 |  | JE24015703 | MALEME EXPRESS | Eastern | MALEME EXPRESS | 2024-05-03 | 23:34 | 2024-05-04 | 1:25 | 0.043431 | 0.00050213 | 182 | 15742 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 21 Protection flags (nil where none): E/F B Ø CAUSE: Burnt contacts and flickers Location: ABS SD4-310 Temp generation (state details when used): no PERFORMANCE DETAIL DNO (number or state No): DNO 2405003 Circuit patrolled and type: F2/F3 cursory patrolled Weather (wind/rain): Calm LFI (Y/N + Comments): Yes Follow up Required (select advisory)? Yes, repairs need to be made to the ABS Additional fault restoration comments: Pole on Fire reported by Fire services. Event # F3968112 ETA required ABS SD4-310 contact & flickers damaged due to the ABS handle coming loose causing the ABS to partially open under load. ABS SD4-310 has been Opened and tagged and back fed via TGA 20 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4683 |  | JE24010984 | 1022 TAUMATA ROAD OMANAWA TAURANGA | Eastern | PYES PA | 2024-05-02 | 8:48 | 2024-05-02 | 15:05 | 0.062286 | 0.00016554 | 60 | 22576 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | NAPA# 109026 : Replace 11kv/400vt poles, 216960, 216961, 216962, 216964, 216965. Replace 11kv/400vt cross arms @ poles 249383, 216963. Isolation point Temp 22: Issuers earths @ pole 216958 (249383 side). | .
4684 |  | JE24010986 | 654A STATE HIGHWAY 3 KAI IWI WANGANUI | Western | MISSION RD | 2024-05-02 | 9:08 | 2024-05-02 | 13:53 | 0.037634 | 0.00013243 | 48 | 13641 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Defected 11KV X-Arm on pole 782838, Replace TX Pole X46 -782833 & Replace Red Tag Pole 782791 | .
4685 |  | JE24011013 | 72 CENTENNIAL AVENUE TE AROHA TE AROHA | Eastern | STANLEY AVE | 2024-05-02 | 8:30 | 2024-05-02 | 12:32 | 0.082683 | 0.00034211 | 124 | 29969 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance IC3412-IC2086-IC3150-FC3135 | .
4686 |  | JE24011087 | 372 RANGIOTU ROAD RANGIOTU PALMERSTON NORTH | Western | BAINESSE | 2024-05-02 | 9:45 | 2024-05-02 | 11:30 | 0.00057736 | 5.5179e-06 | 2 | 209 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replacing damaged 11kv Insulators P29664 | .
4687 |  | JE24011096 | 446 NORTH ROAD EKETAHUNA EKETAHUNA | Western | EKETAHUNA | 2024-05-02 | 8:33 | 2024-05-02 | 11:15 | 0.0076083 | 4.6902e-05 | 17 | 2758 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 30 kVA transformer T8/56, replace multiple 11kV crossarms and replace 400V pole P15554. | .
4688 |  | JE24011646 | 326 WORTLEY ROAD WAIONGANA INGLEWOOD | Western | LEPPERTON | 2024-05-02 | 9:16 | 2024-05-02 | 13:00 | 0.0018531 | 8.2769e-06 | 3 | 672 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Asplundh Vegetation clearance in between poles 745163 - 745164 | .
4689 |  | JE24011651 | 671 KIWI ROAD URUTI URENUI | Western | MAIN RD MOTONUI | 2024-05-02 | 9:45 | 2024-05-02 | 13:23 | 0.0042115 | 1.9313e-05 | 7 | 1526 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | to replace 11kv red tagged poles 764924,764937 and 764947 on kiwi rd | .
4690 |  | JE24011841 | 1522 NAPIER ROAD ASHHURST ASHHURST | Western | AOKAUTERE | 2024-05-02 | 9:15 | 2024-05-02 | 15:27 | 0.020546 | 5.5179e-05 | 20 | 7447 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11KV poles & Xarms between ABS E74 to Temp083 | .
4691 |  | JE24012541 | 754 PLYMOUTH ROAD KORU NEW PLYMOUTH | Western | PIONEER RD | 2024-05-02 | 9:00 | 2024-05-02 | 15:14 | 0.090791 | 0.00024279 | 88 | 32908 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Worksite - Crew 1: Replace pole 755278, and 755279 Crew 2: Replace pole 755281, 755282, and 755283 (Digger operator needed) Crew 3: Replace poles 755284, 755285, and 755289 Crew 4: Replace pole 755316 (Double Tx Pole) | .
4692 |  | JE24014888 | 963 FRANKLEY ROAD HURWORTH NEW PLYMOUTH | Western | BROOKLANDS 7 | 2024-05-02 | 10:00 | 2024-05-02 | 11:53 | 0.0037367 | 3.3108e-05 | 12 | 1354 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace cracked Pole 702127 and restrain Hv wires Tree NDR | .
4693 |  | JE24015397 | WAIHI NORTH | Eastern | WAIHI NORTH | 2024-05-02 | 0:01 | 2024-05-02 | 1:47 | 0.018766 | 0.00022623 | 82 | 6802 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Sect. 13777/2 Protection flags (nil where none): REC. 9604/2 - E/F CAUSE: Unknown - tripped when it was raining hard Location: ?? Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: Cursory Weather (wind/rain): hard rain LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: S | .
4694 |  | JE24015399 | PAHAUTEA 33KV TIE | Western | PAHAUTEA 33KV TIE | 2024-05-02 | 2:58 | 2024-05-02 | 3:23 | 0.062486 | 0.0027672 | 1003 | 22648 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 33kV REC. 3139/2 & 3141/2 Protection flags (nil where none): B ph O/C & E/F CAUSE: Unknown - suspect Opossum Location: ??? Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: cursory Weather (wind/rain): Wind & rain LFI (Y/N + Comments): Y Pole 370631 but had comms fail to them. -SAP13599203 Follow up Required (select advisory)? Additional fault restoration comments: Backfed TUH Sub SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Tuhitarata Sub Circuit that tripped: 33kV circuit from Bidwells Switching Station DTF (KM):n/a | .
4695 |  | JE24015429 | MCKEE SUB - CB A11 | Western | OTARAOA RD | 2024-05-02 | 9:27 | 2024-05-02 | 14:29 | 0.063753 | 0.00047178 | 171 | 23107 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB A11 Protection flags (nil where none): E/F, O/C B CAUSE: Broken Insulator & Burnt up cross arms Location: 760911 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): calm LFI (Y/N + Comments): y, LFI's at Sw/Gear 12285 operated Follow up Required (select advisory)? n Additional fault restoration comments: Isolated at Fuses 5208, cross arms & hardware replaced, full power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4696 |  | JE24015467 | HIKUAI | Eastern | HIKUAI | 2024-05-02 | 9:44 | 2024-05-02 | 12:26 | 0.0017886 | 1.1036e-05 | 4 | 648 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses IP82 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 12:25 Cause: unknown Weather (wind/rain): Follow up required (select advisory)? ABS IP82 independent Fuses also at ABS IP82 , request for photograph to be sent in for SCADA update | .
4697 |  | JE24015513 | MAKINO | Western | MAKINO | 2024-05-02 | 19:43 | 2024-05-02 | 21:06 | 0.029897 | 0.00036142 | 131 | 10836 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV ABS O13 Protection flags (nil where none): Part Power jobs in OMS CAUSE: Broken jumper at links O10/6 - Burnt off (fairly new section of O/H Lines) Location: Pole P17767 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes, Cursory Patrol. Weather (wind/rain): Light Rain. LFI (Y/N + Comments): Yes at Pole P17107 which is Offline. Please follow-up @ Performance Team. Follow up Required (select advisory)? Yes Additional fault restoration comments: Multiple No/Part Power jobs were being raised in OMS. Field Switcher was then dispatched to investigate and specifically around Recloser O10 site as it was showing O Amps and all the jobs raised were past this Recloser. Field Switcher investigated the area and during the second look he found the HV Jumper was broken off at Links O10/6 Once the fault was identified. We then focused on back feeding a portion of the Network from KIM7 through Recloser K31 towards ABS O18 which was Isolated prior. Further Isolations at ABS O14 and then taking the Power Off by opening Recloser O10 and then Isolating ABS O13 Earthing at either side of Pole P17767 and then carrying out the repairs under Access Permit 5513-01 Full Power was restored at 21:05 to the rem | .
4698 |  | JE24010659 | 216 KAIWHAIKI ROAD KAIWHAIKI WANGANUI | Western | MAKIRIKIRI | 2024-05-01 | 9:17 | 2024-05-01 | 15:23 | 0.14625 | 0.00040005 | 145 | 53008 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace multiple 11KV poles & X-Arms & Kidney Strains between poles 784786 & 790156 | .
4699 |  | JE24010941 | 31 WAIAU ROAD ATHENREE GORGE KATIKATI | Eastern | BOWENTOWN | 2024-05-01 | 9:01 | 2024-05-01 | 12:15 | 0.0048308 | 2.4831e-05 | 9 | 1751 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Defected HT pole 207435 | .
4700 |  | JE24010948 | 239 BOUCHER AVENUE TE PUKE TE PUKE | Eastern | ROADS | 2024-05-01 | 9:19 | 2024-05-01 | 12:08 | 0.11028 | 0.00065387 | 237 | 39970 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace blown surge arrestors at pole 223232 | .
4701 |  | JE24010951 | 296 KAWHATAU VALLEY ROAD MANGAWEKA MANGAWEKA | Western | MANGAWEKA | 2024-05-01 | 8:45 | 2024-05-01 | 13:57 | 0.00085937 | 2.759e-06 | 1 | 311 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Kawhatau recloser with new Tavrida recloser | .
4702 |  | JE24010954 | 57 RUATITI AIRSTRIP ROAD ORAUTOHA RAETIHI | Western | RAETIHI | 2024-05-01 | 9:15 | 2024-05-01 | 11:55 | 0.0026475 | 1.6554e-05 | 6 | 960 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 775601 | .
4703 |  | JE24010965 | 37 MASTERTON CASTLEPOINT ROAD TE ORE ORE MASTERTON | Western | TAUWERU | 2024-05-01 | 8:31 | 2024-05-01 | 15:42 | 0.13919 | 0.0003228 | 117 | 50451 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace multiple poles and hardware on the Tauweru Feeder | .
4704 |  | JE24010966 | 14 JOHNSON STREET BULLS BULLS | Western | PAREWANUI | 2024-05-01 | 9:01 | 2024-05-01 | 11:17 | 0.049886 | 0.00036694 | 133 | 18081 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV crossarms on poles 803705 and 803915. | .
4705 |  | JE24010988 | 1 NEVIS CRESCENT TOKOROA TOKOROA | Eastern | BROWNING ST | 2024-05-01 | 8:31 | 2024-05-01 | 14:35 | 0.068446 | 0.00018761 | 68 | 24809 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - IC1969-IC1964-IC1968-IC1966 | .
4706 |  | JE24010989 | 790 TAUMATA ROAD OMANAWA TAURANGA | Eastern | PYES PA | 2024-05-01 | 9:00 | 2024-05-01 | 13:28 | 0.0077664 | 3.0349e-05 | 11 | 2815 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace LV pole 217047, Replace LV cross arm @ pole 217048. Remove LV conductors between pole 217046 & 392374. Remove LV pole 217049. Commission new 4c 185mm LV cable from TX TP169 to new pillar at the base of removed pole 217049. Isolation's and issuer earths HV fuses at TP169 and Tf3 009 | .
4707 |  | JE24011158 | 973 FITZHERBERT EAST ROAD AOKAUTERE PALMERSTON NORTH | Western | AOKAUTERE | 2024-05-01 | 9:00 | 2024-05-01 | 14:50 | 0.023949 | 0.00018209 | 66 | 8680 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11KV poles & Xarms between rec 10367 & Temp 086 ICP's between ABS E74 & TEMP 086 advertised for 15Min at beginning & end of outage re Break/Make switching - No parallels KEG10 | .
4708 |  | JE24011637 | 1383 DEVON ROAD BRIXTON WAITARA | Western | DEVON RD | 2024-05-01 | 9:46 | 2024-05-01 | 12:24 | 0.0056627 | 3.5867e-05 | 13 | 2052 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replacing low Voltage equipment on Tx Structure 474 | .
4709 |  | JE24012420 | 1276 RANGIOTU ROAD TIAKITAHUNA PALMERSTON NORTH | Western | TAIKOREA | 2024-05-01 | 9:09 | 2024-05-01 | 12:45 | 0.00059718 | 2.759e-06 | 1 | 216 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE LEAKING TRANSFORMER 7260P | .
4710 |  | JE24012745 | 368 IRONWORKS ROAD HUNTERVILLE HUNTERVILLE | Western | HUNTERVILLE 22KV | 2024-05-01 | 9:16 | 2024-05-01 | 14:09 | 0.020293 | 8.8287e-05 | 32 | 7355 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 807673, 807674, 807675, 850106, 850108. Replace X-arms 807686. Replace pole & arms & install ABS 16153 at 807625. | .
4711 |  | JE24015264 | BROOKFIELD TCE | Eastern | BROOKFIELD TCE | 2024-05-01 | 5:20 | 2024-05-01 | 6:20 | 0.049998 | 0.00084148 | 305 | 18122 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Fuses SD4-333 Protection flags (nil where none): n CAUSE: Burnt DDO Location: Fuses SD4-333 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: cursory Weather (wind/rain): calm LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Line was isolated at ABS SD4-163 to replace full set of DDO 's at Fuses SD4-163 | .
4712 |  | JE24015265 | MAURICEVILLE | Western | MAURICEVILLE | 2024-05-01 | 1:02 | 2024-05-01 | 3:09 | 0.0038431 | 3.0349e-05 | 11 | 1393 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: U34 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 0308 Cause: unknown Weather (wind/rain): fine Follow up required (select advisory)? | .
4713 |  | JE24015269 | TURITEA SUB - CB8 - REC H131 | Western | LINTON | 2024-05-01 | 6:29 | 2024-05-01 | 7:56 | 0.051638 | 0.00071181 | 258 | 18717 | Unplanned | WILDLIFE - POSSUM | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec H131 Protection flags (nil where none): B Phase E/F CAUSE: Possum on Line Location: Pole P03650 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Weather (wind/rain): Fine LFI (Y/N + Comments): Yes But not Flashing Follow up Required (select advisory)? No Additional fault restoration comments: Removed with Hot Sticks | .
4714 |  | JE24015283 | LONGBUSH | Western | LONGBUSH | 2024-05-01 | 8:22 | 2024-05-01 | 10:44 | 0.0011685 | 8.2769e-06 | 3 | 424 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 8189 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 10:43 Cause: unknown Weather (wind/rain): Fine Follow up required (select advisory)? | .
4715 |  | JE24015317 | AUSTIN ROAD WEST , HAWERA | Western | TAWHITI RD | 2024-05-01 | 12:49 | 2024-05-01 | 15:25 | 0.013827 | 9.1046e-05 | 33 | 5012 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Twisted cross arm and defective hardware found at Pole 722084 Isolated at ABS CA413 & KA737 Cross Arms and Hardware Replaced, full power restored Outage area would have been smaller if Gas/Sw 8726 has Links installed on one side (very BAD Powerco Design) | .
4716 |  | JE24015342 | KUMENGA | Western | KUMENGA | 2024-05-01 | 15:16 | 2024-05-01 | 19:30 | 0.0021041 | 8.2769e-06 | 3 | 763 | Unplanned | WILDLIFE - BIRD | Carry Out Repairs to Lines after a Duck Hit it Isolated at Fuses 7312 Fix Conductor at Pole 799089 2 x 8 amp HV fuses | .
4717 |  | JE24015366 | CLOTON RD NORTH | Western | CLOTON RD NORTH | 2024-05-01 | 15:55 | 2024-05-01 | 17:55 | 0.00099511 | 8.2769e-06 | 3 | 361 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 6214 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 17:55 Cause: unknown Weather (wind/rain): rain Follow up required (select advisory)?n | .
4718 |  | JE24015367 | MARANGAI | Western | MARANGAI | 2024-05-01 | 15:55 | 2024-05-01 | 17:24 | 0.0034091 | 3.8625e-05 | 14 | 1236 | Unplanned | WILDLIFE - BIRD | Fuses Location: 707 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 17:23 Cause: Bird Weather (wind/rain): Fine Follow up required (select advisory)? | .
4719 |  | JE24015368 | 55 Domain Road, Putaruru, 3482 | Eastern | PUTARURU DOMAIN | 2024-05-01 | 19:05 | 2024-05-01 | 22:00 | 0.0029038 | 1.6554e-05 | 6 | 1053 | Unplanned | THIRD PARTY INTERFERENCE - OTHER | Log hit & broke pole M13020, line was isolated at ABS 13543 to replace the pole. Suspect came off logging truck. | .
4720 |  | JE24015377 | STRATHMORE | Western | STRATHMORE | 2024-05-01 | 18:47 | 2024-05-02 | 11:22 | 0.0082388 | 8.2769e-06 | 3 | 2986 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | REGULATORY INFORMATION Voltage & Device ID: 11kV Fuses 4977 Protection flags (nil where none): 1 x Fuse blown & remaining Fuse was still in the closed position, with this evidence from the Field Switcher the Line on the ground was energized. (Dual-Phase Spur Line) CAUSE: Unknown, will try investigate during daylight tomorrow. Location: Poles 708 761 to 708 760 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Heavy Rain LFI (Y/N + Comments): No Follow up Required (select advisory)? Yes Additional fault restoration comments: HV Lines down past Fuses 4977 Isolation point at Fuses 4977 Heavy rain and no visibility up the hill. Field Crew will return on 2/05/2024 to investigate. Line Fixed, Full power restored, 02/05/24, Line may have comedown due to bad weather causing a line clash. | .
4721 |  | JE24015383 | REVANS ST | Western | REVANS ST | 2024-05-01 | 21:48 | 2024-05-01 | 22:22 | 0.0016835 | 4.9661e-05 | 18 | 610 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faultman isolated transformer T4628 for safety to repair broken LV lines due to old joint that burnt out causing an open circuit. | .
4722 |  | JE24010603 | 959 TAUMATA ROAD OMANAWA | Eastern | PYES PA | 2024-04-30 | 8:55 | 2024-04-30 | 14:16 | 0.053278 | 0.00016554 | 60 | 19311 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV/400v Poles 216953, 216951, 216955, 216954, 268441,216957, 216958. | .
4723 |  | JE24010810 | 446 NORTH ROAD EKETAHUNA EKETAHUNA | Western | EKETAHUNA | 2024-04-30 | 8:33 | 2024-04-30 | 13:56 | 0.015149 | 4.6902e-05 | 17 | 5491 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 11kV P16590, replace 11kV crossarms on poles P16535, P16565, P16129, P16523 and repair damaged 11kV conductor at pole P27958. | .
4724 |  | JE24010831 | 412 PAREWANUI ROAD BULLS BULLS | Western | PAREWANUI | 2024-04-30 | 10:09 | 2024-04-30 | 15:22 | 0.0025947 | 8.2769e-06 | 3 | 940 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace four poles, 809354, 809355, 809356, 809357, replace X arms and transformer on pole 809358 TX X2388 | .
4725 |  | JE24011607 | MOKI ROAD & KIWI ROAD URUTI URENUI | Western | MAIN RD MOTONUI | 2024-04-30 | 9:50 | 2024-04-30 | 16:02 | 0.018461 | 4.9661e-05 | 18 | 6691 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | to replace 11kv poles 765165,764901 and 764902 all red tagged along moki and kiwi rds. | .
4726 |  | JE24012917 | 312 BLACK JACK ROAD KUAOTUNU WHITIANGA | Eastern | KUAOTUNU | 2024-04-30 | 9:16 | 2024-04-30 | 12:30 | 0.0026833 | 1.3795e-05 | 5 | 973 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To divert 11kV lines to new pole. | .
4727 |  | JE24015170 | PARIHAKA | Western | PARIHAKA | 2024-04-30 | 3:31 | 2024-04-30 | 6:15 | 0.003182 | 1.9313e-05 | 7 | 1153 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 6635 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 0615 Cause: unknown Weather (wind/rain): fine Follow up required (select advisory)? | .
4728 |  | JE24015175 | 3 Marshall Street, Paeroa | Eastern | WILLOUGHBY ST | 2024-04-30 | 22:02 | 2024-04-30 | 22:17 | 0.00050268 | 3.3108e-05 | 12 | 182 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Offload transformer TC3688 & Tap from Tap3 to Tap2 . | .
4729 |  | JE24015178 | KAIPI RD | Western | KAIPI RD | 2024-04-30 | 8:29 | 2024-04-30 | 13:41 | 0.00086112 | 2.759e-06 | 1 | 312 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: TX 285 No. Fuses: 2 Fuse Amp Size: 2 Amp TIME CLOSED: 09:14 & Fuses blew back. Cause: Deterioration (Old age) Weather (wind/rain): Clear Follow up required (select advisory)? No Transformer Fuses blew back upon re-livening after No Power job was raised. Transformer needs to be replaced. Isolation: TX 285 CAUSE: Deterioration Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Clear Follow up required (select advisory)?No Additional fault restoration comments: Busy arranging a new Transformer. New Transformer installed and Voltage checks carried out. Full Power restored at 13:41 | .
4730 |  | JE24015213 | TURAKINA | Western | TURAKINA | 2024-04-30 | 12:30 | 2024-04-30 | 13:56 | 0.00023715 | 2.759e-06 | 1 | 86 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 2977 No. Fuses: 2 Fuse Amp Size: 3 Amp TIME CLOSED: 13:56 Cause: Unknown Weather (wind/rain): Clear Follow up required (select advisory)? No | .
4731 |  | JE24015217 | MANAIA SUB - CB5 - REC 12139/2 | Western | AUROA | 2024-04-30 | 13:46 | 2024-04-30 | 21:11 | 0.092288 | 0.00081665 | 296 | 33450 | Unplanned | THIRD PARTY INTERFERENCE - OVERHEAD CONTACT | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 12139/2 Protection flags (nil where none): C Ø E/F CAUSE: Digger vs HV O/H Lines Location: Site 1.) Pole 463492 (Old Pole 716949 on GIS) Site 2.) Poles 717721 towards Poles 717727. (Broken Pole at 717721) Seems as the digger made contact at Site 2 & this in turn caused HV Lines to break at Site 1. Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Clear LFI (Y/N + Comments): Yes as per SCADA tile. None operated at NOC. Follow up Required (select advisory)? Additional fault restoration comments: Yes Feeder fault and crew have been dispatched. ETA 10mins Fire Comms have been advised HV Lines down at Pole 463492. Isolations have been carried out and ICP's are being back fed via Gas/Sw MA170. The other back feed that we were going to use at SEC 12567/2 (RTU Comms offline) was cancelled due to Field Switcher finding more HV Lines down along Upper Glen Rd. DIgger came into contact with HV/LV O/H Lines between Poles 717721 towards Poles 717727. (Broken Pole at 717721) NDR has been created by Field Switcher which managed to get all the details of the digger driver. TX M1160 400V Fuses Open until LV Lines have been inspected. Repairs are being carried out at Si | .
4732 |  | JE24015252 | MOUNT BRUCE | Western | MOUNT BRUCE | 2024-04-30 | 18:26 | 2024-04-30 | 19:39 | 0.0005998 | 8.2769e-06 | 3 | 217 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 7712 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 19:38 Cause: Unknown Weather (wind/rain): calm Follow up required (select advisory)? | .
4733 |  | JE24010910 | 13 FITZHERBERT AVENUE SPRINGVALE WANGANUI | Western | SPRINGVALE | 2024-04-29 | 9:07 | 2024-04-29 | 13:15 | 0.031474 | 0.00012691 | 46 | 11408 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11KV X-Arms & Kidney Strains on pole 706436 | .
4734 |  | JE24011154 | 43 Putahi Road Patea | Western | OTAUTU | 2024-04-29 | 9:01 | 2024-04-29 | 13:28 | 0.052387 | 0.00019589 | 71 | 18988 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Blitz Putahi Road project replace poles 727357,727358 & swap position of TX 50kva at L4212 to pole 727370 & 30kva at 5559E to pole 727390 | .
4735 |  | JE24011172 | 134 FOREMAN ROAD TIKORANGI WAITARA | Western | OTARAOA RD | 2024-04-29 | 9:16 | 2024-04-29 | 12:16 | 0.0054754 | 3.0349e-05 | 11 | 1985 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace cross arms on poles 760839 and 760838, re-sag conductors between poles 760859-760860 and 760857-760862 | .
4736 |  | JE24012936 | 568 MOREA ROAD ARARATA HAWERA | Western | TAWHITI RD | 2024-04-29 | 9:00 | 2024-04-29 | 12:43 | 0.00066937 | 1.3795e-05 | 5 | 243 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | create line break at pole 724997, this will be in place for duration of harvest for their safety. remove overhead lines from poles 725010 to 725016 & poles 725021 to 725026. | .
4737 |  | JE24013518 | 555A OLD HIGHWAY WHAKAMARAMA | Eastern | BARRETT RD | 2024-04-29 | 9:31 | 2024-04-29 | 14:15 | 0.025109 | 8.8287e-05 | 32 | 9101 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV Pole 209887. (Pole top photography) | .
4738 |  | JE24014494 | 195 MANGAWHERO ROAD PATETONGA MORRINSVILLE | Eastern | PATETONGA | 2024-04-29 | 9:31 | 2024-04-29 | 10:29 | 0.0058816 | 0.00010208 | 37 | 2132 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Level 1 HV pin cross arm assembly & tighten stay wire | .
4739 |  | JE24014499 | 1628 STATE HIGHWAY 1 PUTARURU PUTARURU | Eastern | TAUMANGI RD | 2024-04-29 | 9:46 | 2024-04-29 | 13:54 | 0.010945 | 4.4143e-05 | 16 | 3967 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Level 1 HV pin and Level 2 LV term arm | .
4740 |  | JE24014566 | 83 JELLICOE STREET TE PUKE TE PUKE | Eastern | CENTRAL RD | 2024-04-29 | 23:01 | 2024-04-30 | 2:34 | 0.018085 | 0.00039177 | 81 | 6555 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace T/X TE5-264 Leaking Transformer | .
4741 |  | JE24015025 | OHAUITI RD | Eastern | OHAUITI RD | 2024-04-29 | 3:58 | 2024-04-29 | 7:17 | 0.2783 | 0.0030956 | 1122 | 100870 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: CB 7, Rec 9209, Sec 13135 Protection flags (nil where none): EF, OC, A, B, OC CAUSE: Unknown Location: N/A Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Patrolled, Nothing Found SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4742 |  | JE24015030 | RANGIWAHIA | Western | RANGIWAHIA | 2024-04-29 | 6:53 | 2024-04-29 | 9:17 | 0.00039577 | 2.759e-06 | 1 | 143 | Unplanned | WILDLIFE - BIRD | Fuses Location: N27 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 09:16 Cause: Bird strike Weather (wind/rain): calm Follow up required (select advisory)?n Line patrol done | .
4743 |  | JE24015078 | VICTORIA ST | Eastern | VICTORIA ST | 2024-04-29 | 12:49 | 2024-04-30 | 15:08 | 0.031677 | 0.00050765 | 92 | 11482 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Transformer TC3423 Protection flags (nil where none): nil CAUSE: 11kV Cable Termination Fault Location: Transformer TC3423 Temp generation (state details when used): Connected 29/04 14:25; Removed 30/04 14:40 PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Calm LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): Check JE24015149 on Completion 11kV cable termination has faulted, One has already been replaced before. A generator will be installed to allow the termination & crossarm to be replaced tomorrow. 29/04/24 Trf TC3423 Fuses ORT 12:49 Generator connected ON time 14:25 Phase Rotation was changed when Generator was installed on one phase, and when Generator was removed the phase rotation was ok, but was not OK with the network. The rotation will be corrected in a planned shut | .
4744 |  | JE24015097 | U260424A | Eastern | BENNETT ST | 2024-04-29 | 12:46 | 2024-04-29 | 14:00 | 0.0066934 | 9.1046e-05 | 33 | 2426 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Related to planned NAPA 109858 and urgent work E00122 - work to repair cable falt and correct cable phasing at Sw/G 14794 and test Sw/G 14794. | .
4745 |  | JE24015102 | BOWENTOWN | Eastern | BOWENTOWN | 2024-04-29 | 12:30 | 2024-04-29 | 12:38 | 0.018084 | 0.0022623 | 820 | 6554 | Unplanned | HUMAN ERROR - POTENTIAL WORKMANSHIP | CB 1 & 2 tripped due to Transformer Maintenance being carried out by PBA. Oil was drained from the Bucholtz initating the trip of CB 1 & 2. These CB's are part of the Transformer protection scheme. Trip circuits had not been isolated. Downer Tech sent to isolate the trip circuits before allowing work to continue. TECH disabled protection | .
4746 |  | JE24015132 | COLYTON | Western | COLYTON | 2024-04-29 | 15:19 | 2024-04-29 | 15:59 | 0.00010967 | 2.759e-06 | 1 | 40 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Jumper was not connected to TFR T4/360 Bushing Isolated at TFR T4/360 Fuses Jumper fixed, full power restored customer has said some of his appliances may have been damaged due to missing phase causing low voltage, faultman advised customer to contact his insurance company | .
4747 |  | JE24015136 | AERODROME | Eastern | AERODROME | 2024-04-29 | 14:39 | 2024-05-02 | 0:20 | 0.02999 | 0.00070629 | 187 | 10870 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: CB 6 Protection flags (nil where none): EF, Phase A OC CAUSE: Cable Fault Location: Between Sw/Gear 9497/3 & 9404/3 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): None Follow up Required (select advisory)? Additional fault restoration comments: Cable Fault between Sw/Gear 9497/3 & 9494/3.To be tested 30/04/24. Cable restored to service under urgent work notice E00124 (advertised 01/05 at 15:50, outage is unplanned). | .
4748 |  | JE24015145 | KAIHERE | Eastern | KAIHERE | 2024-04-29 | 17:45 | 2024-04-29 | 19:50 | 0.0017147 | 1.3795e-05 | 5 | 622 | Unplanned | WILDLIFE - BIRD | Location: Pole 0185 TIME CLOSED: 19:49 Cause: Duck Strike, Caused Broken Squirrel Wire Weather (wind/rain): Windy Follow up required (select advisory)? | .
4749 |  | JE24015162 | TE PUNINGA | Eastern | TE PUNINGA | 2024-04-29 | 19:23 | 2024-04-29 | 20:11 | 0.0005282 | 1.1036e-05 | 4 | 191 | Unplanned | WILDLIFE - BIRD | Fuses Location: FP1333 No. Fuses: 2 Fuse Amp Size: 20 TIME CLOSED: 20:10 Cause: Swan Strike Weather (wind/rain): Windy Follow up required (select advisory)? | .
4750 |  | JE24015015 | HUKANUI | Western | HUKANUI | 2024-04-28 | 18:39 | 2024-04-28 | 19:57 | 0.00064797 | 8.2769e-06 | 3 | 235 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 10412 No. Fuses: 2 Fuse Amp Size: 3 Amp TIME CLOSED: 19:57 Cause: Suspected bird strike Weather (wind/rain): Calm Follow up required (select advisory)? N | .
4751 |  | JE24015018 | ROYDEN DOWNS RD | Eastern | ROYDEN DOWNS RD | 2024-04-28 | 20:06 | 2024-04-30 | 21:05 | 0.093398 | 0.00075871 | 274 | 33853 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 5 Protection flags (nil where none): A,B, E/F CAUSE: Car v Pole Location: 314 Old Coach Road -11kV Pole 225014 Temp generation (state details when used): installed @ DTX TF6-061 @ 02:15 PERFORMANCE DETAIL DNO (number or state No): NDR , ND120335 Circuit patrolled and type: no Weather (wind/rain): windy LFI (Y/N + Comments): no Follow up Required (select advisory)? Additional fault restoration comments: 11kV Cable from Fuses SF6-017 Damaged, Generator Installed to supply DTX TF6-061 Customer has 100K of Honey on site . Cable to be repaired under 2R Gen removed 30/04 | .
4752 |  | JE24015022 | TE KIRI | Western | TE KIRI | 2024-04-28 | 23:31 | 2024-04-29 | 3:13 | 0.051468 | 0.00044419 | 161 | 18655 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Recloser 12273 Protection flags (nil where none): A Ph E/F CAUSE: Line Down Location: Pole 71593 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Calm LFI (Y/N + Comments): N not active at Pole P467127 Follow up Required (select advisory)? Additional fault restoration comments: Fault was past LFI's, LFI's didn't activate. Isolated at ABS's TA914 & TA 876 plus Links 12273/6 Line repaired Cause Age SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4753 |  | JE24014950 | WILSON RD | Eastern | WILSON RD | 2024-04-27 | 8:34 | 2024-04-27 | 10:19 | 0.011847 | 0.00011312 | 41 | 4294 | Unplanned | WILDLIFE - BIRD | Fuses Location: dtx No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 10:19 Cause: Duck strike Weather (wind/rain): fine Follow up required (select advisory)? | .
4754 |  | JE24014951 | INLAND COAST | Western | INLAND COAST | 2024-04-27 | 8:57 | 2024-04-27 | 10:18 | 0.0002729 | 5.5179e-06 | 2 | 99 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses 6508 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 1017 Cause: bird strike Weather (wind/rain): fine Follow up required (select advisory)? | .
4755 |  | JE24014961 | PIONEER RD | Western | PIONEER RD | 2024-04-27 | 9:18 | 2024-04-27 | 10:38 | 0.0046289 | 5.7938e-05 | 21 | 1678 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 8406 No. Fuses: 2 Fuse Amp Size: 15A TIME CLOSED: 1037 Cause: unknown Weather (wind/rain): fine Follow up required (select advisory)? | .
4756 |  | JE24014981 | CLOTON RD SOUTH | Western | CLOTON RD SOUTH | 2024-04-27 | 20:35 | 2024-04-27 | 22:36 | 0.037525 | 0.001912 | 693 | 13601 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Cloton Rd CB 3 Protection flags (nil where none): B phase & EF CAUSE: Unknown Location: past LFI;s SAP13599232 (past ABS 5755) Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Calm LFI (Y/N + Comments): Y Active at Poles 738894 & 737366 Follow up Required (select advisory)? N Additional fault restoration comments: Feeder sectionalised past ABS 5755 with no fault found SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): N/A | .
4757 |  | JE24014985 | MAXWELL | Western | MAXWELL | 2024-04-27 | 21:55 | 2024-04-27 | 23:36 | 0.010013 | 9.9323e-05 | 36 | 3629 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 287 No. Fuses: 2 Fuse Amp Size: 20 Amp TIME CLOSED: 23:35 Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)? N | .
4758 |  | JE24014128 | 488 SHW1 TIRAU | Eastern | CAMBRIDGE RD TIRAU | 2024-04-26 | 9:46 | 2024-04-26 | 11:38 | 0.0058851 | 5.242e-05 | 19 | 2133 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE ROTTON HV AND LV CROSSARMS AT TRANSFORMER TC6274 | .
4759 |  | JE24014141 | 134 KEY ROAD TOKOROA | Eastern | ASHWORTH ST | 2024-04-26 | 10:00 | 2024-04-26 | 11:14 | 0.0069505 | 9.3805e-05 | 34 | 2519 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLANT POLE 856031 - 2M INLINE DUE TO LAND EROSION POLE AND HARDWARE GOOD CONDITION - RE-USE | .
4760 |  | JE24014834 | PAREWANUI | Western | PAREWANUI | 2024-04-26 | 5:38 | 2024-04-26 | 8:45 | 0.0020695 | 1.1036e-05 | 4 | 750 | Unplanned | WILDLIFE - BIRD | Fuses Location: 4946 No. Fuses: 2 Fuse Amp Size: 8 TIME CLOSED: 08:45 Cause: Bird Strike Weather (wind/rain): calm Follow up required (select advisory)?n | .
4761 |  | JE24014835 | KAKARAMEA | Western | KAKARAMEA | 2024-04-26 | 8:35 | 2024-04-26 | 9:57 | 0.0024896 | 3.0349e-05 | 11 | 902 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV Fuses LI725 Protection flags (nil when none): n CAUSE: Branch on lines Location: 729997 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state no): n Circuit patrolled & type: Cursory Weather (wind/rain): windy Follow up required (select advisory)? n Additional fault restoration comments: Line isolated and branch removed. 2X 15 amp fuses replaced | .
4762 |  | JE24014842 | LEEDSTOWN 22KV | Western | LEEDSTOWN 22KV | 2024-04-26 | 7:31 | 2024-04-26 | 10:06 | 0.0055178 | 3.5867e-05 | 13 | 2000 | Unplanned | WILDLIFE - BIRD | Fuses Location: 538 No. Fuses: 2 Fuse Amp Size: 15 TIME CLOSED: 10:05 Cause: Bird strike Weather (wind/rain): wind Follow up required (select advisory)?n | .
4763 |  | JE24014858 | PARAPARA | Western | PARAPARA | 2024-04-26 | 8:43 | 2024-04-26 | 11:22 | 0.00043955 | 2.759e-06 | 1 | 159 | Unplanned | OTHER | No ICPS on transformer 6581W for a new Cell Site. Part of NAPA 110090 | .
4764 |  | JE24014864 | MANGAWEKA | Western | MANGAWEKA | 2024-04-26 | 9:55 | 2024-04-26 | 10:26 | 0.0019523 | 6.3456e-05 | 23 | 708 | Unplanned | WILDLIFE - BIRD | Fuses Location: 2813 No. Fuses: 2 Fuse Amp Size: 15 TIME CLOSED: 10:25 Cause: Twisted lines due to Duck strike - see SIS Weather (wind/rain): wind Follow up required (select advisory)?n | .
4765 |  | JE24014875 | 5540 STATE HIGHWAY 27, WAITOA, 3380 | Eastern | CAMPBELL RD | 2024-04-26 | 12:10 | 2024-04-26 | 12:21 | 5.895e-05 | 5.5179e-06 | 2 | 21 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: DTX was on Tap 5, Now on Tap 1. Loop tests completed: 0.5 @ House 0.1 @ Dtx Test results: Voltage at TX: 260,261,263, 448V, Tap 5 Voltage at house: 260,261,262, 440V Transformer dropped from Tap 5 to Tap 3 Neutral Tap Voltage at TX: 247,248,247, 426V, Tap 3 Voltage at house: 244,245,244, 421V Have all connections been checked? yes PQI Ref #: N/A Additional Info: Problem Fixed | .
4766 |  | JE24014885 | MANGAWEKA | Western | MANGAWEKA | 2024-04-26 | 14:53 | 2024-04-27 | 11:01 | 0.076638 | 6.3456e-05 | 23 | 27778 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faultman will return in morning to repair line down in gully, as had to go get motor bike and gear, to dangerous to work in dark as has to walk into gully , Faultman advised customer of the problem and are happy, most of the Tfr's feed wool sheds. Isolation at Fuses 2813 Repair 1 x line down at Pole 810406 | .
4767 |  | JE24014934 | RAWHITI AVE | Eastern | RAWHITI AVE | 2024-04-26 | 21:41 | 2024-04-27 | 3:49 | 0.033582 | 9.1046e-05 | 33 | 12172 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | LV frame burning up on TC3943 DNO2404012 LV frame must be replaced , short term fix in place, older LV frame parts no longer available for Transformer has burped oil on blue phase bushing and should be tested, may require replacement possibly has been over loaded, a load check should also be done. | .
4768 |  | JE24015801 | BENNETT ST | Eastern | BENNETT ST | 2024-04-26 | 9:50 | 2024-04-26 | 16:54 | 0.0072852 | 0.00018209 | 33 | 2641 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Urgent work notice E00122 - advertised 24/04 at 18:45, outage is planned. Related to planned NAPA 109858 - work to repair cable falt and correct cable phasing at Sw/G 14794. Generation connection to TC3514 (connected and removed same day). | .
4769 |  | JE24014743 | CLOTON RD NORTH | Western | CLOTON RD NORTH | 2024-04-25 | 4:21 | 2024-04-25 | 5:49 | 0.18555 | 0.0025934 | 913 | 67255 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV, CB 5 Protection flags (nil where none): O/C A-B-C phase CAUSE: Unk Location: Unk Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): SAP 13750696 no comms. Had not operated when checked onsite Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4770 |  | JE24014756 | KUMENGA | Western | KUMENGA | 2024-04-25 | 9:02 | 2024-04-25 | 11:46 | 0.0031626 | 1.9313e-05 | 7 | 1146 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: 11226 No. Fuses: 2 Fuse Amp Size: 8 TIME CLOSED: 11:45 Cause: wind Weather (wind/rain): Follow up required (select advisory)? | .
4771 |  | JE24014777 | CLOTON RD NORTH | Western | CLOTON RD NORTH | 2024-04-25 | 16:18 | 2024-04-25 | 19:40 | 0.065441 | 0.0010098 | 366 | 23719 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Recloser 6616 Protection flags (nil where none): B, C Ph O/C, E/F CAUSE: Lines down (Broken Cross arm) Location: Pole 741608 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Raining LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Isolated at FABS 5539, cross arm replaced, line repaired, full power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4772 |  | JE24014783 | FORDELL | Western | FORDELL | 2024-04-25 | 18:02 | 2024-04-26 | 6:31 | 0.32209 | 0.0022872 | 829 | 116742 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 4, CB 3 A/R Protection flags (nil where none): A Ph, E/F CAUSE: Tree Through lines Location: ABS 452 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Fine LFI (Y/N + Comments): Nil Follow up Required (select advisory)? Additional fault restoration comments: CB 3 opened when Fire services reported the tree through lines. Isolated at CB's 3 & 4, ABS's 606, 889, 702. Back feeds installed Repairs carried out (Replaced 3 x Cross arms and 1x pole) Break before make switching required to return feeder to Normal configuration | .
4773 |  | JE24014787 | WAITARA EAST TOWN | Western | WAITARA EAST TOWN | 2024-04-25 | 19:14 | 2024-04-25 | 21:53 | 0.17417 | 0.0022623 | 820 | 63128 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | REGULATORY INFORMATION Voltage & Device ID: 33kV CB 702 & 613, 11kV CB 10 Protection flags (nil where none): E/F, O/C A, B & C CAUSE: Broken jumper connection to ABS 5044 Location: ABS 5044 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): wind, rain LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: CB 10 A/R and 33kV between Waitara East & West tripped out, CB U20 back feed off CB U10 faultman started to patrol the 33kV line, then a lot of jobs came in past 11kV ABS 5044, A broken jumper connection was found at ABS 5044, Feeder de-energised as jumper was moving in the wind, faulted area was isolated and back feeds put in place Isolated at Sw/Gear 12689/1, ABS 5097, 12383/1 & Links 12383/4 Jumper connection to ABS 5044 was repaired, full power restored Protection issue :- 33kV CB 702 & 613 Tripped as well | .
4774 |  | JE24014806 | OTAKEHO | Western | OTAKEHO | 2024-04-25 | 18:03 | 2024-04-25 | 19:56 | 0.011532 | 0.00010208 | 37 | 4180 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: TA868 No. Fuses: 2 Fuse Amp Size: 25A TIME CLOSED: 19:55 Cause: unknown Weather (wind/rain): wind, rain Follow up required (select advisory)? | .
4775 |  | JE24014829 | MANUTAHI | Western | MANUTAHI | 2024-04-25 | 21:27 | 2024-04-26 | 3:48 | 0.090025 | 0.00047178 | 161 | 32630 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 1 Protection flags (nil where none): E/F, O/C A CAUSE: Broken Insulator caused double cross arm to burn up Location: Pole 728279 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: op Weather (wind/rain): wind, rain LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Isolated at ABS WH191, 12413/1 & Links 12413/4, double cross arm and hardware replaced, full power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4776 |  | JE24010291 | 909 RAUMAI ROAD SANTOFT BULLS | Western | LAKE ALICE | 2024-04-24 | 9:36 | 2024-04-24 | 14:04 | 0.0059226 | 2.2072e-05 | 8 | 2147 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace three poles 803997. 803998, 809100 | .
4777 |  | JE24010413 | MAXWELL | Western | MAXWELL | 2024-04-24 | 8:48 | 2024-04-24 | 13:55 | 0.06608 | 0.0002152 | 78 | 23952 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install temporary pole and recloser temp133, Maxwell feeder mid-span | .
4778 |  | JE24010464 | 34 TITOKI ROAD MAKURI PAHIATUA | Western | COONOOR | 2024-04-24 | 9:08 | 2024-04-24 | 11:35 | 0.020743 | 0.00014071 | 51 | 7518 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove TEMP voltage regulator 10301/2 at pole 446721 | .
4779 |  | JE24010597 | 551 VALLEY ROAD ASHHURST FEILDING | Western | POHANGINA | 2024-04-24 | 9:30 | 2024-04-24 | 13:18 | 0.035777 | 0.00015726 | 57 | 12968 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replacing all crossarms and Tx on pole P45549, replace crossarm on pole P14704 | .
4780 |  | JE24010628 | 1329 Tanawa Rd | Western | CASTLEPOINT | 2024-04-24 | 9:16 | 2024-04-24 | 15:00 | 0.09794 | 0.00028417 | 103 | 35499 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles and defects past ABS S86 | .
4781 |  | JE24010640 | 40 WORCESTER STREET ASHHURST ASHHURST | Western | ASHHURST | 2024-04-24 | 8:31 | 2024-04-24 | 15:24 | 0.059256 | 0.00014347 | 52 | 21478 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove OH TX(T4/13-300kVA), dismantle Pole P07329 & P07328, Extend conductor from P07329 to new pole, Install new GM 300kVA (7810P) (Links TEMP118 will be installed under NAPA 108678 before the shutdown) | .
4782 |  | JE24010797 | 238 SANDON BLOCK ROAD OHINGAITI HUNTERVILLE | Western | RANGIWAHIA | 2024-04-24 | 10:16 | 2024-04-24 | 11:01 | 0.0065582 | 0.00014623 | 53 | 2377 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace defected crossarm P08414 | .
4783 |  | JE24010799 | 75 RANGITIKEI VALLEY ROAD WAITUNA WEST REWA | Western | RANGIWAHIA | 2024-04-24 | 13:00 | 2024-04-24 | 13:51 | 0.0012577 | 2.4831e-05 | 9 | 456 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace broken 11kv strain disc at Pole P08316 | .
4784 |  | JE24010803 | 1159 FITZHERBERT EAST ROAD AOKAUTERE PALMERSTON NORTH | Western | AOKAUTERE | 2024-04-24 | 10:45 | 2024-04-24 | 16:58 | 0.015068 | 0.00011588 | 42 | 5461 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11KV poles Between Temp 084 and Temp 086 | .
4785 |  | JE24010955 | 567 MATAU NORTH ROAD MATAU STRATFORD | Western | HUIROA | 2024-04-24 | 9:31 | 2024-04-24 | 16:01 | 0.0043036 | 1.1036e-05 | 4 | 1560 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | asplundh to cut trees between poles 709482 & 709485 | .
4786 |  | JE24010967 | 8 GEORGE STREET ELTHAM ELTHAM | Western | ELTHAM TOWN NORTH | 2024-04-24 | 9:00 | 2024-04-24 | 14:47 | 0.11279 | 0.00032556 | 118 | 40881 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace poles 732402 732511 732508 | .
4787 |  | JE24011145 | 7 SAXTON ROAD UPPER VOGELTOWN NEW PLYMOUTH | Western | BROOKLANDS 7 | 2024-04-24 | 10:30 | 2024-04-24 | 12:10 | 0.021741 | 0.00021796 | 79 | 7880 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Tx 1037, investigate and repair tx sight glass leak. | .
4788 |  | JE24011932 | 1334 OTARAOA ROAD TIKORANGI WAITARA | Western | OTARAOA RD | 2024-04-24 | 10:08 | 2024-04-24 | 16:08 | 0.037793 | 0.00010484 | 38 | 13698 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace ABS 5129, remove TX2976T, pole 760826 and span of wire, re sag-conductors between poles 760826-760825, 760824-760821, 759892-759895, 760680-760679, 760832-760829 | .
4789 |  | JE24013553 | PUTTICK RD, LINTON ARMY CAMP | Western | LINTON EXPRESSWAY | 2024-04-24 | 12:30 | 2024-04-24 | 14:29 | 0.050747 | 0.00042764 | 155 | 18393 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | MAKE NECESSARY REPAIRS TO FAULTY 11KV CABLE - DNO 2404001 | .
4790 |  | JE24014406 | 1834 MORRINSVILLE-TAHUNA ROAD TAHUNA MORRINSVILLE | Eastern | HORRELLS RD | 2024-04-24 | 10:01 | 2024-04-24 | 13:27 | 0.014704 | 7.4492e-05 | 27 | 5330 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Investigate the Plastic smell in CB4 cubical at Tahuna Sub. Red Defect. | .
4791 |  | JE24014610 | MAIN RD MOTONUI | Western | MAIN RD MOTONUI | 2024-04-24 | 3:02 | 2024-04-24 | 12:08 | 0.033201 | 0.00040281 | 61 | 12034 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: Sectionaliser 12131 Protection flags (nil where none): EF CAUSE: Broken Insulator Location: Pol;e 765121 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Operational Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Repalced insulator at Pole 765121 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4792 |  | JE24014618 | 284 AWAITI WEST ROAD, AWAITI, PAEROA, 3672 | Eastern | AWAITI | 2024-04-24 | 8:22 | 2024-04-24 | 12:23 | 0.0073282 | 3.0349e-05 | 11 | 2656 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole 013409 isolated at ABS IC 1226 to change cross arm | .
4793 |  | JE24014633 | BROOKLANDS 7 | Western | BROOKLANDS 7 | 2024-04-24 | 8:43 | 2024-04-24 | 15:34 | 0.04436 | 0.0024555 | 890 | 16078 | Unplanned | VEGETATION - INSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: Sectionaliser 12353 Protection flags (nil where none): Phase C , EF CAUSE: Tree on Lines, Lines Down Location: Pole 702127 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Operational Weather (wind/rain): Calm LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Pole 702127 to be replaced under NDR, new NAPA application Trees removed lines repaired and re energised Planned NAPA to repplace pole to follow as pole is cracked | .
4794 |  | JE24014709 | THORP ST | Eastern | THORP ST | 2024-04-24 | 16:36 | 2024-04-24 | 16:41 | 0.0029921 | 0.00066491 | 241 | 1085 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | During livening switching for NAPA 109858 (JE 24010937) feeder was tripped when cable failed from new switch gear 14794/2 towards ABS 544. Feeder from CB6 to ABS 544 was lost Protection EF & C phase Transformer TC3514 was off generation and was being reinstated as part of the switching and is on the cable from 14794/1 to sw/gear 9210/1 and was reinstated after the fault was isolated. Short notice outage scheduled for 26/04 using generation has been advertised to make cable repair and correct phasing issue Advertised for TC3514 to connect generation & disconnect generation on E00122, advertised 24/04 at 18:45 01/05/2024 - Short notice - U260424A started on the 26/04/2024 completed 01/05/2024. MDP | .
4795 |  | JE24014726 | COLOGNE ST | Western | COLOGNE ST | 2024-04-24 | 20:54 | 2024-04-25 | 0:12 | 0.0087578 | 4.4143e-05 | 16 | 3174 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 7379 No. Fuses: 2 Fuse Amp Size: 10 Amp TIME CLOSED: 00:12 Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)? No | .
4796 |  | JE24010289 | 799 TURAKINA VALLEY ROAD TURAKINA WANGANUI | Western | TUTAENUI | 2024-04-23 | 9:21 | 2024-04-23 | 14:11 | 0.067312 | 0.00023175 | 84 | 24398 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace wooden poles at multiple sites, 794321, 794314, 794315, 794316, 794337, 794336, 794338, 794339, 794341, 794388, 794347 | .
4797 |  | JE24010293 | MT STEWART | Western | MT STEWART | 2024-04-23 | 8:31 | 2024-04-23 | 12:06 | 0.0047403 | 2.2072e-05 | 8 | 1719 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace crossarms between P09668 and P09605. Remove redundant LV. | .
4798 |  | JE24010321 | 2803 STATE HIGHWAY 4 MANGAMAHU WANGANUI | Western | MAKIRIKIRI | 2024-04-23 | 9:06 | 2024-04-23 | 14:06 | 0.055435 | 0.00018485 | 67 | 20093 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11KV X-Arms at poles 783376, 783594 & 783618 | .
4799 |  | JE24010334 | RAETIHI | Western | RAETIHI | 2024-04-23 | 9:45 | 2024-04-23 | 15:10 | 0.068087 | 0.00020968 | 76 | 24678 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Shut2 Replace structure 777510/ 777509 using a digger. | .
4800 |  | JE24010345 | 975 STATE HIGHWAY 3 KAI IWI WANGANUI | Western | WATERWORKS RD | 2024-04-23 | 8:50 | 2024-04-23 | 14:57 | 0.13135 | 0.00036142 | 131 | 47610 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install temporary pole and recloser on the waterworks feeder mid-span between 375206 & ABS 105 | .
4801 |  | JE24010401 | 22 PEAKES ROAD SAINT JOHNS HILL WANGANUI | Western | BRASSEY ROAD | 2024-04-23 | 9:39 | 2024-04-23 | 10:23 | 0.0080502 | 0.00018485 | 67 | 2918 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Top up transformer X368 up with oil via oil valve at base | .
4802 |  | JE24010426 | 756 ROBERTS LINE BUNNYTHORPE PALMERSTON NORTH | Western | BUNNYTHORPE | 2024-04-23 | 9:25 | 2024-04-23 | 12:09 | 0.019546 | 0.00011864 | 43 | 7084 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Perform ABS Maintenance at 4258/1 and D74 and recloser maintenance at 4258/2 | .
4803 |  | JE24010429 | 1522 NAPIER ROAD ASHHURST ASHHURST | Western | ASHHURST | 2024-04-23 | 10:00 | 2024-04-23 | 15:56 | 0.019611 | 5.5179e-05 | 20 | 7108 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles & Xarms between ABS E74 & Temp 083 | .
4804 |  | JE24010453 | 959 Taumata road | Eastern | PYES PA | 2024-04-23 | 8:52 | 2024-04-23 | 15:06 | 0.061834 | 0.00016554 | 60 | 22412 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | NAPA# 108735: Replace 11kv/400vt poles 216949, 216947. Replace 11kv/400vt cross arms and transformer @ pole 217058 and cross arms @ pole 216948. Install stay @ pole 493697. Replace HV overhead conductors between poles 216949 & 493697 with 3W Magpie. Isolation point @ Temp 22: Issuers earths @ pole 217055 (217058 side). | .
4805 |  | JE24010643 | 230 POHANGINA VALLEY EAST ROAD POHANGINA ASHHURST | Western | POHANGINA | 2024-04-23 | 9:54 | 2024-04-23 | 11:03 | 0.019619 | 0.00028141 | 102 | 7111 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Perform ABS maintenance on F28 and recloser maintenance at F26 | .
4806 |  | JE24010811 | 343 KORU ROAD KORU NEW PLYMOUTH | Western | PIONEER RD | 2024-04-23 | 8:46 | 2024-04-23 | 13:34 | 0.090591 | 0.00031452 | 114 | 32835 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Worksite - Straighten and re-block pole 367247 and string 7 x span of Ferret conductor from pole 755181-367216 | .
4807 |  | JE24010824 | 218 TARATA ROAD INGLEWOOD INGLEWOOD | Western | KAIMATA | 2024-04-23 | 10:01 | 2024-04-23 | 13:02 | 0.0074961 | 4.1384e-05 | 15 | 2717 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace stays on pole 760512 | .
4808 |  | JE24010837 | 43 Putahi Road Patea | Western | OTAUTU | 2024-04-23 | 9:01 | 2024-04-23 | 13:06 | 0.01287 | 5.242e-05 | 19 | 4665 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Blitz Putahi Road project wire run from pole 727359 to 727374 | .
4809 |  | JE24010937 | 1 RAROA ROAD PAEROA PAEROA | Eastern | THORP ST | 2024-04-23 | 8:45 | 2024-04-24 | 16:55 | 0.011836 | 0.00018209 | 33 | 4290 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV SD Switchgear 3168 /72 /74 with CCC Safelink 14794 with SCADA control on all switches. 24/04: Cable failed on re-livening captured in JE24014709 Generation removed and TX restored via backfeed. 26/04: urgent outage E00122 for testing and repairs - not completed. 29/04: Additional outage to ICPs, work ongoing. 01/05/24 - Phasing repaired and tested. Network normalised. | .
4810 |  | JE24014466 | WAITARA RD | Western | WAITARA RD | 2024-04-23 | 0:58 | 2024-04-23 | 3:39 | 0.025548 | 0.00029797 | 108 | 9260 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: SZR 12229, Rec 12237 A/R Protection flags (nil where none): C phase EF CAUSE: 1 xLine down Location: Pole 742485 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): fine LFI (Y/N + Comments): N Follow up Required (select advisory)? Additional fault restoration comments: Line down repaired but cross arm is damaged and will need to be replaced. 2r to remain open so crew can apply for urgent NAPA to replace cross arm Pole been defected by FM ( Defect # 300780058) SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4811 |  | JE24014479 | PARK RD | Western | PARK RD | 2024-04-23 | 8:02 | 2024-04-23 | 12:11 | 1.1087 | 0.0070492 | 2555 | 401852 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB C839 Protection flags (nil where none): E/F CAUSE: Line down Location: Between Poles 473664 & 446688 Temp generation (state details when used): n PERFORMANCE DETAIL DNO (number or state No): n Circuit patrolled and type: op Weather (wind/rain): calm LFI (Y/N + Comments): y (SAP13601387 did not operate) Follow up Required (select advisory)? n Additional fault restoration comments: feeder was backfeeding a large area as Kempton TFR was removed from service for maintenance NAPA 109173, (most of Kempton sub being backfed via CLV C839 and C838) Lines down reported 2hrs after trip, Line was being patrolled when call came in, Faulted area Isolated at ABS 11393, Links 11252 & S310/4, Line repaired Full power restored, damage found on the line that had come down | .
4812 |  | JE24014546 | TAINUI | Eastern | TAINUI | 2024-04-23 | 17:00 | 2024-04-23 | 17:39 | 0.01901 | 0.00048558 | 176 | 6890 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV ABS IP506 Protection flags (nil where none): Nil CAUSE: Deterioration Location: Pole 387 418 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Clear, wind. LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: At Pole 387418 - Burnt cross-arm on pin Pole Field Switcher is busy arranging material and a bucket truck. No immediate danger/risk at the moment. Busy carrying out repairs under AP 4546-01 All repairs have been completed and Full Power restored at 17:39 | .
4813 |  | JE24014560 | BENNETT ST | Eastern | BENNETT ST | 2024-04-23 | 15:26 | 2024-04-23 | 17:22 | 0.049777 | 0.00042764 | 155 | 18042 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV ABS IC400 Protection flags (nil where none): Nil CAUSE: Digger vs Pole Location: Pole N2652 ( 8 Alley Memorial Rd, Komata, Paeroa ) Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Clear LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Digger hit the Pole N2652, no HV Lines were brought down. Pole is cracked & leaning over at an angle. Busy arranging material and the bucket Truck before Power is switched off. Isolation points will be at ABS IC400 & Links TEMP036 All repairs have been carried out and Power restored at 17:22. SAFETY MANAGER | .
4814 |  | JE24014581 | 26 BROWN ROAD, TE POI, MATAMATA | Eastern | RANGITANUKU RD | 2024-04-23 | 17:41 | 2024-04-23 | 17:51 | 0.00018959 | 1.9313e-05 | 7 | 69 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | High Voltages at TC2160 Transformer TC2160 Fuses ORT 17:41, UTC 17:50 At tap 2 RED 251V WHITE 251V BLUE 249V Tapped down from Tap 2 to Tap 1 Voltages RED 244V WHITE 244V BLUE 243V | .
4815 |  | JE24014606 | WAIONE | Western | WAIONE | 2024-04-23 | 20:07 | 2024-04-23 | 22:22 | 0.0037137 | 2.759e-05 | 10 | 1346 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: V44 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 22:21 hrs Cause: Suspect Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? | .
4816 |  | JE24014608 | PURIRI | Eastern | PURIRI | 2024-04-23 | 23:37 | 2024-04-24 | 1:01 | 0.0025603 | 3.0349e-05 | 11 | 928 | Unplanned | WILDLIFE - BIRD | Fuses Location: FP1332 No. Fuses: 2 Fuse Amp Size: 10 Amp TIME CLOSED: 01:01 Cause: Bird strike Weather (wind/rain): Calm Follow up required (select advisory)? N | .
4817 |  | JE24010038 | 973 FITZHERBERT EAST ROAD AOKAUTERE PALMERSTON NORTH | Western | AOKAUTERE | 2024-04-22 | 10:02 | 2024-04-22 | 15:59 | 0.045438 | 0.00018209 | 66 | 16469 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11KV poles & Xarms Between 367024 & rec 10367 install TEMP086 ABS on pole367024 | .
4818 |  | JE24010059 | 960 NORFOLK ROAD UPPER PLAIN CARTERTON | Western | HOLDSWORTH | 2024-04-22 | 9:30 | 2024-04-22 | 15:38 | 0.12286 | 0.00033383 | 121 | 44530 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace xarms between S321 and S114 | .
4819 |  | JE24010187 | PAREWANUI | Western | PAREWANUI | 2024-04-22 | 9:31 | 2024-04-22 | 14:08 | 0.041351 | 0.00014898 | 54 | 14988 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Repair oil leak on transformer 1363W | .
4820 |  | JE24010195 | 25 ALFREDTON ROAD EKETAHUNA EKETAHUNA | Western | EKETAHUNA | 2024-04-22 | 8:59 | 2024-04-22 | 16:46 | 0.12999 | 0.00027866 | 101 | 47115 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove OH 15kva(T8/20), Install GM 300kva(7807P), dismantle P16833/P16834, replace with 11m Busck pole, Install new Fuses (10881), Install EP106 pillar fitted with relays to supply OH streetlight & hot water pilots NOTE: Job ran over time mainly because phase rotation was incorrect, so had to be altered befoe livening the LV supply to customers | .
4821 |  | JE24010229 | 516 MAKARA ROAD HALCOMBE FEILDING | Western | MT STEWART | 2024-04-22 | 8:45 | 2024-04-22 | 13:00 | 0.0021041 | 8.2769e-06 | 3 | 763 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace crossarm at P09882 and resag conductor between P09882 and 942858. | .
4822 |  | JE24010282 | 79 PURNELL STREET COLLEGE ESTATE WANGANUI | Western | COLLEGE | 2024-04-22 | 9:45 | 2024-04-22 | 13:20 | 0.0011827 | 5.5179e-06 | 2 | 429 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11KV X-Arms & Kidney Strains on pole 705414 | .
4823 |  | JE24010285 | 2336 STATE HIGHWAY 4 MANGAMAHU WANGANUI | Western | MAKIRIKIRI | 2024-04-22 | 9:15 | 2024-04-22 | 12:19 | 0.03042 | 0.00016554 | 60 | 11026 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11KV X-Arms on pole 783331 | .
4824 |  | JE24010436 | 785 GRENADA STREET PAPAMOA BEACH TAURANGA | Eastern | EVANS RD | 2024-04-22 | 7:33 | 2024-04-22 | 14:57 | 0.0012255 | 2.759e-06 | 1 | 444 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace SD switchgear (SDAF3) base unit only, (rusted out). | .
4825 |  | JE24010763 | 10 KAHAROA ROAD PATEA PATEA | Western | OTAUTU | 2024-04-22 | 9:25 | 2024-04-22 | 13:14 | 0.038574 | 0.0001683 | 61 | 13981 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace pole 723976 and install new stay wire & anchor | .
4826 |  | JE24013500 | 399 wright rd | Eastern | LOCKINGTON ROAD | 2024-04-22 | 9:30 | 2024-04-22 | 13:32 | 0.13981 | 0.00057938 | 210 | 50673 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV Pole 204988. (Pole top photography) | .
4827 |  | JE24014312 | OAONUI | Western | OAONUI | 2024-04-22 | 5:25 | 2024-04-22 | 7:20 | 0.00031787 | 2.759e-06 | 1 | 115 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 6486 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 07:20 Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)? No | .
4828 |  | JE24014323 | CAMBRIA LS | Western | CAMBRIA LS | 2024-04-22 | 11:20 | 2024-04-22 | 13:52 | 0.0077117 | 5.7938e-05 | 21 | 2795 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Replaced all three fuses at Transformer C5403 - isolation at Links CA704 (had to do individual offloads, see child jobs) | .
4829 |  | JE24014324 | NGAERE | Western | NGAERE | 2024-04-22 | 7:36 | 2024-04-22 | 8:48 | 0.0011859 | 1.6554e-05 | 6 | 430 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses 4982 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 08:47 Cause: Bird Weather (wind/rain): Calm Follow up required (select advisory)?No | .
4830 |  | JE24014327 | 262 WAITEKAURI ROAD, WAIHI, 3682 | Eastern | WAITAWHETA | 2024-04-22 | 9:10 | 2024-04-22 | 11:36 | 0.016092 | 0.00011036 | 40 | 5833 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV ABS 248 Protection flags (nil where none): Nil CAUSE: Deterioration Location: Pole P2205 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Clear LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Field switcher on site, cross-arm is rotten and needs to be changed ASAP and Conductor is holding on by a PG Clamp. Isolation will be at ABS 248 Busy carrying out repairs at the moment under AP 4327-01 Repairs completed and Power restored at 11:35 | .
4831 |  | JE24014354 | TIROHIA-KARANGAHAKE | Eastern | TIROHIA-KARANGAHAKE | 2024-04-22 | 9:24 | 2024-04-22 | 10:47 | 0.00022925 | 2.759e-06 | 1 | 83 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses FC2360 No. Fuses: 2 Fuse Amp Size: 6 Amp TIME CLOSED: 10:47 Cause: Bird Strike Weather (wind/rain): Rain Follow up required (select advisory)? No | .
4832 |  | JE24014433 | KAIHERE | Eastern | KAIHERE | 2024-04-22 | 14:49 | 2024-04-22 | 16:41 | 0.0015444 | 1.3795e-05 | 5 | 560 | Unplanned | WILDLIFE - BIRD | Fuses Location: FC762 No. Fuses: 3 Fuse Amp Size: 25 Amp TIME CLOSED: 16:40 Cause: Bird strike Weather (wind/rain): Clear Follow up required (select advisory)? No | .
4833 |  | JE24014451 | RANGIWAHIA | Western | RANGIWAHIA | 2024-04-22 | 17:43 | 2024-04-22 | 17:49 | 0.0014782 | 0.00025658 | 93 | 536 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | CB 6 indicated tripped and open but was still indicating current on the analogue. Went to put in a back feed and noticed that when REC N21 was opened the analogue on CB 6 dropped by he same amount of current that was showing at N21. Closed N21 to see if we get calls from customers. Crew sent to check indication at KIM Sub and that no normally open points were left closed. Crew checked ABS N16, N40, N34, N6 & P37 CB 6 indicated closed at 2016. No customers called to report no power Suspect that CB 6 did an auto reclose but the close indication did not come through. | .
4834 |  | JE24014462 | WARATAH ST | Eastern | WARATAH ST | 2024-04-22 | 22:21 | 2024-04-22 | 23:28 | 0.04894 | 0.0021161 | 423 | 17738 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 5 Protection flags (nil where none): O/C, E/F CAUSE: Cable fault Location: Between Sw/Gear's SC4-454 & 13798-1 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Clear LFI (Y/N + Comments): Y at multiple Sw/Gear units Follow up Required (select advisory)? Additional fault restoration comments: 2R left open for testing of cable in morning SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): No Circuit that tripped: CB 5 DTF (KM): Update: HV Cable has been tested under Test Permit and results show the Cable has faulted. Digger is required to access the faulty section, repairs will be carried out on 24/04/2024 Restored to normal after repairs made 24/04/24 | .
4835 |  | JE24014464 | WAREA | Western | WAREA | 2024-04-22 | 22:58 | 2024-04-23 | 0:55 | 0.00681 | 5.7938e-05 | 21 | 2468 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: PU231 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 0055 Cause: Unknown Weather (wind/rain): Fine Follow up required (select advisory)? | .
4836 |  | JE24014260 | dtx_TC4378 | Eastern | MVILLE SOUTH | 2024-04-21 | 19:05 | 2024-04-21 | 20:00 | 0.0080278 | 0.00014623 | 53 | 2910 | Unplanned | HUMAN ERROR - POTENTIAL WORKMANSHIP | Cause: Failed Electrical Contactor ( Cascade ) What was replaced? 4 x andalec Fuses & Carriers Where was it replaced (pole/TX/pillar box)? DTX TC3826 Is 2R required? Y/N Yes 2R Y - What is the timeframe for repairs? Additional Info: Safety Incident, Flashover in 400V Side of Transformer while Contractor trying to Fix Street Light Contactor, Downers Investigating, Contractor sent to Hospital for observation. Isolation at HV fuse switch 14245/2 | .
4837 |  | JE24014274 | TARATA | Western | TARATA | 2024-04-21 | 10:08 | 2024-04-21 | 11:43 | 0.00025956 | 2.759e-06 | 1 | 94 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: LV fault at Central Metering Point on customers property What was replaced? 2x 2A HV fuses Where was it replaced (pole/TX/pillar box)? Txfr 3045T Is 2R required? N 2R Y - What is the timeframe for repairs? Additional Info: Property was disconnected as customer needs to get a sparky to make repairs. Disco Tag # A34395 Tag Reg Updated Retailer e-mailed - Meridian & Mercury | .
4838 |  | JE24014294 | OLD CAMBRIDGE RD | Eastern | OLD CAMBRIDGE RD | 2024-04-21 | 15:09 | 2024-04-21 | 16:20 | 0.049874 | 0.00097116 | 352 | 18077 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: CB 3 Protection flags (nil where none): A, B, C Fault, EF CAUSE: Unknown Location: N/a Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Line patrolled, no fault found SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4839 |  | JE24014300 | NGAMOTU RD | Western | NGAMOTU RD | 2024-04-21 | 17:40 | 2024-04-21 | 19:17 | 0.18919 | 0.002221 | 805 | 68572 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: CB 6 Protection flags (nil where none): B & C phase OC CAUSE: Swan on the ground by ABS 553 Location: ABS 553 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: cursory Weather (wind/rain): fine LFI (Y/N + Comments): N but it would have been helpful with a automated back feed and a feeder that splits Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4840 |  | JE24014304 | 1295A 3, WAVERLEY, WAVERLEY, 4591 | Western | RANGIKURA | 2024-04-21 | 19:30 | 2024-04-21 | 24:00 | 0.0037214 | 1.3795e-05 | 5 | 1349 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Power Pole on Fire down the driveway (Transformer Pole) Contact Paul, on 027710541 Jumper burning on crossarm. Replace crossarms | .
4841 |  | JE24014305 | TE ROTI | Western | TE ROTI | 2024-04-21 | 18:26 | 2024-04-21 | 20:01 | 0.002867 | 3.0349e-05 | 11 | 1039 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses 5987 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 2000 Cause: Bird, Canadian Geese Weather (wind/rain): fine Follow up required (select advisory)? | .
4842 |  | JE24014073 | recloser_9834:2 | Eastern | MAUNGARANGI RD | 2024-04-20 | 9:24 | 2024-04-20 | 9:58 | 0.00055814 | 1.6554e-05 | 6 | 202 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | AC mains fail technician to investigate during business hours Repaired the LV lines feeding Recloser 9834 Supply. Fed from From TE6-128 Transformer Fuses TE6-128 400V Fuses Open, Lock & Tag- 09:24, UTC 09:57 | .
4843 |  | JE24014199 | MAIN RD MOTONUI | Western | MAIN RD MOTONUI | 2024-04-20 | 3:50 | 2024-04-20 | 8:06 | 0.024758 | 0.0001683 | 61 | 8974 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Reclosure 12131/2 Protection flags (nil where none): E/F CAUSE: Unknwon Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Calm LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Crew advises that this Recloser has tripped a few times recently. Follow up to look at an operational patrol? SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4844 |  | JE24014200 | KAIHERE | Eastern | KAIHERE | 2024-04-20 | 4:51 | 2024-04-20 | 5:44 | 0.10296 | 0.0094329 | 3419 | 37320 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 17 & 19 Protection flags (nil where none): B, C E/F CAUSE: Unknown fault Location: KPE Sub Temp generation (state details when used): NO PERFORMANCE DETAIL DNO (number or state No): NO Circuit patrolled and type: Cursory Weather (wind/rain): Fine LFI (Y/N + Comments): Yes 13587219 A,B OC Perm Follow up Required (select advisory)? Yes Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): KPE Circuit that tripped: CB 17 & 19 DTF (KM): Nil 24/04/24 protection files down loaded & being sent to PCO protection team | .
4845 |  | JE24014218 | MAIN RD MOTONUI | Western | MAIN RD MOTONUI | 2024-04-20 | 9:42 | 2024-04-20 | 13:33 | 0.023589 | 0.0001683 | 61 | 8550 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: REC 12131 Protection flags (nil where none): EF CAUSE: Unknown Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Phil Barnes installed LFI's at Pole 765011 to try and narrow down faulted area in case it trips again. There have been a number of trippings this week. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4846 |  | JE24014223 | PUTORINO | Western | PUTORINO | 2024-04-20 | 7:31 | 2024-04-20 | 10:41 | 0.0062897 | 3.3108e-05 | 12 | 2280 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: FABS 4172 No. Fuses: 2 Fuse Amp Size: 20A TIME CLOSED: 1040 Cause: Unknown Weather (wind/rain): light rain Follow up required (select advisory)? | .
4847 |  | JE24010003 | 104 HAMILTONS LINE TIAKITAHUNA PALMERSTON NORTH | Western | BAINESSE | 2024-04-19 | 8:30 | 2024-04-19 | 12:13 | 0.0079701 | 3.5867e-05 | 13 | 2889 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles and crossarms between pole P43682 and pole P45203. | .
4848 |  | JE24010007 | 431 MORIKAU ROAD RANANA WANGANUI | Western | RAETIHI | 2024-04-19 | 10:11 | 2024-04-19 | 12:35 | 0.032318 | 0.00022348 | 81 | 11714 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 777789 using line truck | .
4849 |  | JE24010052 | 2107 LAKE FERRY ROAD PIRINOA FEATHERSTON | Western | BURNSIDE | 2024-04-19 | 9:30 | 2024-04-19 | 12:39 | 0.0015591 | 8.2769e-06 | 3 | 565 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re sag 1kv line and straighten pole 464284 | .
4850 |  | JE24010157 | 1752 WAIHI VALLEY ROAD, PONGOROA | Western | HOROEKA | 2024-04-19 | 9:03 | 2024-04-19 | 10:18 | 0.02263 | 0.00030073 | 109 | 8202 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Perform ABS Maintenance at V15 & V7, recloser maintenance at V5, Remove TEMP119 at pole P04875 Possible follow up as to why a weather assessment was not done before switching began and the customer outage began. We burnt over 1 hour of SADI on this switching and got no work done. | .
4851 |  | JE24010470 | 40 TEBBUTT ROAD WAIROA TAURANGA | Eastern | KAIMAI DRIVE | 2024-04-19 | 9:15 | 2024-04-19 | 15:31 | 0.031081 | 8.2769e-05 | 30 | 11266 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv overhead conductors between pole 217771 & 499812. | .
4852 |  | JE24010642 | 43B PUTAHI ROAD PATEA PATEA | Western | OTAUTU | 2024-04-19 | 9:01 | 2024-04-19 | 12:42 | 0.011601 | 5.242e-05 | 19 | 4205 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Blitz Putahi Road project wire run from poles 727375 to 727390 replace existing conductor | .
4853 |  | JE24010688 | 435 KINA ROAD OAONUI OPUNAKE | Western | SOUTH RD NGARIKI | 2024-04-19 | 9:59 | 2024-04-19 | 14:20 | 0.0028782 | 1.1036e-05 | 4 | 1043 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace tx N3307 with like-for-like unit. Install crucifix on pole 712635 term. | .
4854 |  | JE24010753 | 1284 JUNCTION ROAD INGLEWOOD INGLEWOOD | Western | JUNCTION RD | 2024-04-19 | 10:00 | 2024-04-19 | 14:06 | 0.037334 | 0.00015174 | 55 | 13532 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To upgrade Tx 1012 to a 50 kva PQI upgrade | .
4855 |  | JE24011887 | 975 STATE HIGHWAY 3 KAI IWI WANGANUI | Western | KAI IWI 33KV | 2024-04-19 | 9:17 | 2024-04-19 | 15:15 | 0.21871 | 0.00062904 | 228 | 79272 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 468794, liven new local service transformer site, remove 11kv line between poles 468794 and 782126 move 33kv supply onto new structure | .
4856 |  | JE24013838 | 1 PEMBROKE ROAD PEMBROKE STRATFORD | Western | CLOTON RD NORTH | 2024-04-19 | 8:51 | 2024-04-19 | 9:30 | 0.02038 | 0.00052144 | 189 | 7387 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11KV poles 734020 DNO ABS 5720. Replace LV arms 734021, 734429, 734430 and 734431 Job was cancelled due to road reseal causing access problems on work site so of safety Phil Webby cancelled the work, they will reapply to have ABS 5720 (DNO TAG 2308016) replaced. | .
4857 |  | JE24013892 | OWERA RD | Eastern | OWERA RD | 2024-04-19 | 8:28 | 2024-04-19 | 14:09 | 0.041196 | 0.000309 | 112 | 14932 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove temporary Generation and replace faulty Transformer TC4041. Close 11kV cable break at pole W13240. LV Outage no oms job created as of yet | .
4858 |  | JE24014098 | TAIRUA NORTH | Eastern | TAIRUA NORTH | 2024-04-19 | 9:13 | 2024-04-19 | 12:40 | 0.096034 | 0.0028804 | 1044 | 34808 | Unplanned | THIRD PARTY INTERFERENCE - OVERHEAD CONTACT | A,B, E?F Protection flags. Digger Brought Lines Down at 385 Pacfic Coast Highway - Hazard on Linked Job* Digger Never had permit he was reportedly driving under lines @ 7.3m Clearance and hit Rackoon wire wirh extended Long boom @ Pole 264013 site | .
4859 |  | JE24014115 | REVANS ST | Western | REVANS ST | 2024-04-19 | 10:24 | 2024-04-19 | 11:49 | 0.00047046 | 5.5179e-06 | 2 | 171 | Unplanned | WILDLIFE - BIRD | Fuses Location: Fuses 7144 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 1148 Cause: Bird Weather (wind/rain): windy Follow up required (select advisory)? | .
4860 |  | JE24014146 | MOAWHANGO | Western | MOAWHANGO | 2024-04-19 | 13:14 | 2024-04-19 | 15:33 | 0.0015422 | 1.1036e-05 | 4 | 559 | Unplanned | THIRD PARTY INTERFERENCE - TREES | Fuses Location: 4189 No. Fuses: 3 Fuse Amp Size: 8 TIME CLOSED: 15:33 Cause: Tree cutter dropped branch on lines causing lines to twist, lines were untwisted with hot line stick, tree cutters did not have CAC, Faultman got all info. Weather (wind/rain): calm Follow up required (select advisory)?Y | .
4861 |  | JE24014148 | 464 CHELTENHAM CROSS ROAD, FEILDING | Western | WAITUNA | 2024-04-19 | 16:36 | 2024-04-19 | 17:15 | 0.001498 | 3.8625e-05 | 14 | 543 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Lines spragged at Pole P22983. Isolate at Fuses K30 to repair. | .
4862 |  | JE24014193 | INLAND COAST | Western | INLAND COAST | 2024-04-19 | 21:20 | 2024-04-19 | 22:15 | 0.0012293 | 2.2072e-05 | 8 | 446 | Unplanned | WILDLIFE - BIRD | Fuses Location: 6510 No. Fuses: 2 Fuse Amp Size: 15 Amp TIME CLOSED: 22:15 Cause: Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? N | .
4863 |  | JE24014197 | PILLANS POINT | Eastern | PILLANS POINT | 2024-04-19 | 23:55 | 2024-04-20 | 1:23 | 0.044984 | 0.00051041 | 185 | 16305 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Mechanical failure of Drop Out Fuse holder for TC4-010 (failing to hold fuse) Isolated from ABS SC4-022 to Links 14591/4 All three DOF's replaced | .
4864 |  | JE24009917 | 7 POUTINI STREET WHANGANUI EAST WANGANUI | Western | EASTOWN RD | 2024-04-18 | 9:15 | 2024-04-18 | 13:21 | 0.084643 | 0.00034487 | 125 | 30679 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace transformer 1347W due to oil leak and rust | .
4865 |  | JE24009918 | 677 STANWAY ROAD HALCOMBE FEILDING | Western | MT STEWART | 2024-04-18 | 8:31 | 2024-04-18 | 12:39 | 0.034236 | 0.00013795 | 50 | 12409 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles and crossarms between P06134 and P05035. | .
4866 |  | JE24010089 | 349 NORFOLK ROAD WAINGAWA CARTERTON | Western | HOLDSWORTH | 2024-04-18 | 8:45 | 2024-04-18 | 14:36 | 0.11698 | 0.00033383 | 121 | 42398 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv pole 826536 and hardware on pole 826550 | .
4867 |  | JE24010397 | PYES PA | Eastern | PYES PA | 2024-04-18 | 8:56 | 2024-04-18 | 15:36 | 0.066143 | 0.00016554 | 60 | 23974 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV/400V poles 384144, 217055, 217056, 217057. Replace 11kV/400V cross arms @ pole 390202. | .
4868 |  | JE24010416 | 1 SATCO DRIVE TOKOROA TOKOROA | Eastern | ASHWORTH ST | 2024-04-18 | 17:31 | 2024-04-18 | 21:26 | 0.0078101 | 3.3108e-05 | 12 | 2831 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance IC1472-IC1490-FC2748-IC1486 | .
4869 |  | JE24010596 | 535 SOUTH ROAD OKAIAWA HAWERA | Western | KETEMARAE RD | 2024-04-18 | 9:01 | 2024-04-18 | 12:15 | 0.012884 | 6.6215e-05 | 24 | 4670 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace HV cross arms at pole 723103 | .
4870 |  | JE24010608 | 103 OMATA ROAD MARFELL NEW PLYMOUTH | Western | OMATA RD | 2024-04-18 | 9:31 | 2024-04-18 | 14:49 | 0.2388 | 0.00075044 | 272 | 86555 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace cracked pole 750154 damaged by car accident | .
4871 |  | JE24010615 | 794 OHANGAI ROAD OHANGAI HAWERA | Western | MEREMERE | 2024-04-18 | 8:45 | 2024-04-18 | 15:06 | 0.015765 | 4.1384e-05 | 15 | 5714 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | asplundh to cut trees between poles 725420 & 725408 | .
4872 |  | JE24010629 | 248 PLYMOUTH ROAD OMATA NEW PLYMOUTH | Western | PIONEER RD | 2024-04-18 | 9:16 | 2024-04-18 | 14:21 | 0.040867 | 0.00014071 | 51 | 14813 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | String 4 x span of Squirrel conductor from pole 755207-755211 | .
4873 |  | JE24010638 | 20 BRADSHAW ROAD KOMATA PAEROA | Eastern | BENNETT ST | 2024-04-18 | 9:22 | 2024-04-18 | 11:56 | 0.006367 | 4.1384e-05 | 15 | 2308 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REMOVE AND BYPASS 11KV RECLOSURE 9901/2 (FOR SERVICING) | .
4874 |  | JE24012940 | 120B WOOD ROAD TATUANUI WAITOA | Eastern | NGARUA | 2024-04-18 | 9:47 | 2024-04-18 | 11:35 | 0.00089294 | 8.2769e-06 | 3 | 324 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace decayed 11kv arms identified by PTP at poles L12412, L12413, L12414 | .
4875 |  | JE24013964 | PILLANS POINT | Eastern | PILLANS POINT | 2024-04-18 | 10:43 | 2024-04-18 | 13:42 | 0.093498 | 0.002243 | 813 | 33889 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Dump Truck Hit 400v Lines & flicked up into 11kV Lines tripping CB 4 (A/R, Houses Tested for High Low contact damage , all ok, Restored 13:45 NOC opened CB 4 for safety | .
4876 |  | JE24014007 | SHAW AVE | Eastern | SHAW AVE | 2024-04-18 | 13:01 | 2024-04-18 | 14:12 | 0.065505 | 0.00099323 | 360 | 23743 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV POA CB 4 Protection flags (nil where none): A B C Ø O/C & E/F CAUSE: Overload/Loose connection. Location: 71 Shaw Avenue/ Pole N12533 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Clear LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: HV Cable failed at crucifix (Pole N12533) Fault was repaired under AP Cable was then tested under Test Permit. Network normalized at 11:20 on 22/04 | .
4877 |  | JE24014020 | SOUTH RD CHAPEL | Western | SOUTH RD CHAPEL | 2024-04-18 | 9:46 | 2024-04-18 | 14:24 | 0.00076534 | 2.759e-06 | 1 | 277 | Unplanned | OTHER | Cause: Planned HV shut Napa 105176 What was replaced? NA Where was it replaced (pole/TX/pillar box)? NA Is 2R required? N 2R Y - What is the timeframe for repairs? NA Additional Info: T1338 the correct open point is at pole 419787 - T306 Part off HV shut 105176 AI team emailed: Yes ICP not advertised - unplanned outage for this ICP | .
4878 |  | JE24014059 | KAKARAMEA | Western | KAKARAMEA | 2024-04-18 | 17:26 | 2024-04-18 | 18:35 | 0.00018807 | 2.759e-06 | 1 | 68 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Suspected Blown HV Fuse found by Obertech while doing private work at property - Reece Wineera - 027 225 9900 Found High Test results when got there Replaced all 3 Fuses with 3amp and all tests were good also replaced 3 x barrels Lien at 18:34 | .
4879 |  | JE24009888 | 308 NORFOLK ROAD WAINGAWA CARTERTON | Western | HOLDSWORTH | 2024-04-17 | 8:46 | 2024-04-17 | 14:05 | 0.0035245 | 1.1036e-05 | 4 | 1277 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace hardware on pole 826543 | .
4880 |  | JE24009892 | 3244 NGAHAPE ROAD STRONVAR MASTERTON | Western | WERAITI | 2024-04-17 | 9:15 | 2024-04-17 | 15:17 | 0.018994 | 5.242e-05 | 19 | 6884 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace hardware and conductor past links 7113 | .
4881 |  | JE24009949 | 182 OWAIRUA ROAD PIPIRIKI WANGANUI | Western | RAETIHI | 2024-04-17 | 9:31 | 2024-04-17 | 14:40 | 0.0076851 | 2.4831e-05 | 9 | 2786 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 3x poles 777984, 777985 & TX pole 777986. | .
4882 |  | JE24009952 | 104 HAMILTONS LINE TIAKITAHUNA PALMERSTON NORTH | Western | BAINESSE | 2024-04-17 | 8:41 | 2024-04-17 | 10:13 | 0.00025566 | 2.759e-06 | 1 | 93 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV crossarms on poles P45207 and P45206. | .
4883 |  | JE24009956 | 2047 MAKINO ROAD HALCOMBE FEILDING | Western | MT STEWART | 2024-04-17 | 10:16 | 2024-04-17 | 13:55 | 0.018125 | 8.2769e-05 | 30 | 6570 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace all crossarms on pole P17896, replace | .
4884 |  | JE24010014 | 324 STANWAY ROAD HALCOMBE FEILDING | Western | MT STEWART | 2024-04-17 | 10:15 | 2024-04-17 | 11:44 | 0.0021901 | 2.4831e-05 | 9 | 794 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace 11kv crossarm pole P09855 | .
4885 |  | JE24010301 | 102 KEREPEHI TOWN ROAD KEREPEHI PAEROA | Eastern | KAIHERE | 2024-04-17 | 9:16 | 2024-04-17 | 14:06 | 0.12307 | 0.00042488 | 154 | 44606 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV pole O13711 & O13709 Kerepehi Town Rd. | .
4886 |  | JE24010343 | 32 BROWNING STREET TOKOROA TOKOROA | Eastern | LOMOND AVE | 2024-04-17 | 23:30 | 2024-04-18 | 2:32 | 0.001003 | 5.5179e-06 | 2 | 364 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9143-1/2/3 | .
4887 |  | JE24010409 | 8559 SH2 Waikino | Eastern | WAITAWHETA | 2024-04-17 | 9:33 | 2024-04-17 | 14:55 | 0.22301 | 0.00072285 | 262 | 80830 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole P13045 (IC1223) SH 2 & Old Waitekauri Rd | .
4888 |  | JE24010414 | 956 WHAKAMARAMA ROAD WHAKAMARAMA | Eastern | WHAKAMARAMA | 2024-04-17 | 10:04 | 2024-04-17 | 13:02 | 0.02989 | 0.0001683 | 61 | 10834 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install 11kV Surge Arrestors at 11kV Pole 481460. | .
4889 |  | JE24010441 | 266 BARRETT ROAD WHALERS GATE NEW PLYMOUTH | Western | HURFORD RD | 2024-04-17 | 9:46 | 2024-04-17 | 12:02 | 0.00037687 | 2.759e-06 | 1 | 137 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To isolate Hv fuses 6603 to carry out repairs on the lv Under built lines | .
4890 |  | JE24012762 | 58 WAINUI STREET KOITIATA WANGANUI | Western | TURAKINA | 2024-04-17 | 10:15 | 2024-04-17 | 15:18 | 0.11034 | 0.00037798 | 137 | 39992 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Defected 11kV Pole 794925. | .
4891 |  | JE24013105 | 155 WEST ROAD HUNTERVILLE HUNTERVILLE | Western | HUNTERVILLE 22KV | 2024-04-17 | 8:34 | 2024-04-17 | 15:59 | 0.0049091 | 1.1036e-05 | 4 | 1779 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Drop 11kv line both sides of pole 806858 for the removal of trees | .
4892 |  | JE24013779 | 503A TE PUKE HIGHWAY, TE PUKE, 3187 | Eastern | BLACK STUMP | 2024-04-17 | 10:00 | 2024-04-17 | 11:37 | 0.010161 | 0.00010484 | 38 | 3683 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole fire at base of pole surrounded by scrub 2x in last week. 17/04/24 Short notice outage to investigate and correct issue Isolation between sw/gear 14107/1 & ABS IP112 Found that lug on one phase had blown apart and was dropping molten metal to the ground. All jumpers & insulators replaced on the pole and lugs replaced Requested photos and samples of damaged equipment be sent to Ken Pattie | .
4893 |  | JE24013819 | WESTMERE PEAT ST | Western | WESTMERE PEAT ST | 2024-04-17 | 11:57 | 2024-04-17 | 13:30 | 0.0010282 | 1.1036e-05 | 4 | 373 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Burnt off Neutral found at bushing on Transformer X3172 Isolated at HV fuses for transformer Jumper repaired | .
4894 |  | JE24013852 | REVANS ST | Western | REVANS ST | 2024-04-17 | 10:23 | 2024-04-17 | 10:32 | 4.8905e-05 | 5.5179e-06 | 2 | 18 | Unplanned | WILDLIFE - BIRD | Fuses Location: Transformer 7144 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 10:32 Cause: Bird Strike at Pole 842279 Weather (wind/rain): Fine Follow up required (select advisory)? NIL | .
4895 |  | JE24013854 | MAIN RD MOTONUI | Western | MAIN RD MOTONUI | 2024-04-17 | 10:37 | 2024-04-17 | 14:12 | 0.022022 | 0.0001683 | 61 | 7982 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Recloser 12131/2 tripped on E/F, line was sectionalised and patrolled and no fault was found. | .
4896 |  | JE24013867 | MANGOREWA | Eastern | MANGOREWA | 2024-04-17 | 12:17 | 2024-04-17 | 13:35 | 0.0032155 | 4.1384e-05 | 15 | 1165 | Unplanned | WILDLIFE - BIRD | Fuses Location: 11kV Fuses SE6-084 No. Fuses: 2 Fuse Amp Size: 25 TIME CLOSED: 13:32 Cause: bird Weather (wind/rain): Follow up required (select advisory)? | .
4897 |  | JE24013873 | HOLDSWORTH | Western | HOLDSWORTH | 2024-04-17 | 8:46 | 2024-04-17 | 14:05 | 0.00088112 | 2.759e-06 | 1 | 319 | Unplanned | OTHER | Cause: Part of NAPA 108770 IS 2R required? N Additional Info: ICP not advertised - unplanned outage for this ICP | .
4898 |  | JE24013880 | KAIMAI DRIVE | Eastern | KAIMAI DRIVE | 2024-04-17 | 13:18 | 2024-04-17 | 14:34 | 0.081538 | 0.0013353 | 484 | 29554 | Unplanned | THIRD PARTY INTERFERENCE - OVERHEAD CONTACT | REGULATORY INFORMATION Voltage & Device ID: 11KV RECLOSER 9275 Protection flags (nil where none): EF CAUSE: Suspected line contact via 20 tonne digger found parked under line on low bed, truck warm no one around Requested faultman to leave CAC form under windscreen wipers with note "" required when within 4 metres of Powerco lines Location: Thorn road, faultman has further details if required (photos etc) Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4899 |  | JE24013891 | OLD TAURANGA RD | Eastern | OLD TAURANGA RD | 2024-04-17 | 18:28 | 2024-04-17 | 19:21 | 0.00086769 | 1.6554e-05 | 6 | 315 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Cause: Unk What was replaced? Nil Where was it replaced (pole/TX/pillar box)? N/A Is 2R required? Y 2R Y - What is the timeframe for repairs? Completed Additional Info: Fault isolated via HV as no LV Transformer fuses. Sectionalising and patrol of LV circuits carried out with no fault found | .
4900 |  | JE24013912 | KAIHERE | Eastern | KAIHERE | 2024-04-17 | 19:32 | 2024-04-17 | 21:01 | 0.00049248 | 5.5179e-06 | 2 | 179 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: FC828 No. Fuses: 2 Fuse Amp Size: 3Amp TIME CLOSED: 21:00 Cause: Suspect Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? | .
4901 |  | JE24013917 | BUCKLAND RD | Eastern | BUCKLAND RD | 2024-04-17 | 21:36 | 2024-04-17 | 22:58 | 0.028415 | 0.00046351 | 168 | 10299 | Unplanned | WILDLIFE - POSSUM | REGULATORY INFORMATION Voltage & Device ID: 11kV, Rec 13261/2 Protection flags (nil where none): E/F 1 CAUSE: Opossum Location: E0177 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Yes / Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): Yes. LFI did not indicate a fault after the initial trip to lockout. LFI's at Pole E1220 operated correctly when sectionalising Follow up Required (select advisory)? 2R left open to return tomorrow and install possum guard as one was not fitted on this pole. Additional fault restoration comments: Possum cleared from line using Hot Stick. Opossum guard was install on pole E0177 under the 2R this morning. | .
4902 |  | JE24009618 | 120 STANWAY ROAD HALCOMBE FEILDING | Western | MT STEWART | 2024-04-16 | 8:31 | 2024-04-16 | 14:19 | 0.096012 | 0.0002759 | 100 | 34800 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace crossarms between P09105 and P06163. Replace ABS M57. | .
4903 |  | JE24009862 | 1546 KIMBOLTON ROAD CHELTENHAM FEILDING | Western | WAITUNA | 2024-04-16 | 8:45 | 2024-04-16 | 14:02 | 0.024505 | 7.7251e-05 | 28 | 8882 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole and all hardware including TX T5/226 at pole P38298/P38299. Replace pole and crossarms at pole P38297. Replace all crossarms on poles P38250 and P38257. | .
4904 |  | JE24009879 | 386 MT HOLDSWORTH ROAD MOUNT HOLDSWORTH CARTERTON | Western | HOLDSWORTH | 2024-04-16 | 9:15 | 2024-04-16 | 13:51 | 0.015978 | 5.7938e-05 | 21 | 5791 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles past fuses 7064 | .
4905 |  | JE24010185 | 45 Bridge St Karangahake | Eastern | TIROHIA-KARANGAHAKE | 2024-04-16 | 9:00 | 2024-04-16 | 14:05 | 0.073005 | 0.00024003 | 87 | 26461 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV TX Pole N1777, TP979 45 Bridge St Karangahake | .
4906 |  | JE24010241 | 113 Putahi Road Patea | Western | OTAUTU | 2024-04-16 | 9:21 | 2024-04-16 | 15:19 | 0.018762 | 5.242e-05 | 19 | 6800 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Blitz Putahi road project replace poles from poles 727385 to 727390 Putahi Road. Remove poles 727391,727392,482047,481783 Nicholson Rd & install new poles opposite side of Nicholson Road1,2,3,4 reinstate TX L4205 connect new 11kv lines run | .
4907 |  | JE24010270 | 432 INGAHAPE ROAD MANUTAHI HAWERA | Western | WHAKAMARA | 2024-04-16 | 10:01 | 2024-04-16 | 14:38 | 0.012253 | 4.4143e-05 | 16 | 4441 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | asplundh to cut trees from poles 729769 to 728844 | .
4908 |  | JE24010313 | 2 HUTTLOC DRIVE TOKOROA TOKOROA | Eastern | LOMOND AVE | 2024-04-16 | 23:00 | 2024-04-17 | 3:47 | 0.065561 | 0.00022899 | 83 | 23763 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9061-1/2/3/4 | .
4909 |  | JE24010317 | 80 TEBBUTT ROAD WAIROA TAURANGA | Eastern | KAIMAI DRIVE | 2024-04-16 | 9:16 | 2024-04-16 | 14:11 | 0.024417 | 8.2769e-05 | 30 | 8850 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | NAPA#108638 : Replace 11kv/400vt poles 217783,217784 & 217782. Replace cross arms @ poles 217781 & 217790. Remove back stay and ground anchors from pole 499812. Isolation point SD3-159 Issuer earths @ pole 217781 (217780 side). | .
4910 |  | JE24010374 | 343 KORU ROAD KORU NEW PLYMOUTH | Western | PIONEER RD | 2024-04-16 | 9:31 | 2024-04-16 | 13:52 | 0.034994 | 0.00014071 | 51 | 12684 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Crew 1: Replace pole 755208 (Digger), and 755210 Crew 2: Replace pole 755181, and 755161 Crew 3: Replace pole 755182 (stay pole), 755160, and 755159 Crew 4: Replace poles 755158, 755157, and 755160 | .
4911 |  | JE24011874 | 101 WAIRAKEI AVENUE PAPAMOA BEACH TAURANGA | Eastern | PALM SPRINGS | 2024-04-16 | 6:06 | 2024-04-16 | 16:45 | 0.045917 | 0.00088287 | 160 | 16643 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install generators at transformers TP337 & TP420 LV. Replace SDAF fuse-switch base FP450 (rust / leaking). Remove generators from transformers TP337 & TP420 LV. | .
4912 |  | JE24013662 | OVERDALE RD | Eastern | OVERDALE RD | 2024-04-16 | 5:18 | 2024-04-16 | 12:02 | 0.29003 | 0.00097116 | 352 | 105123 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: Recloser 9948 Protection flags (nil where none): Phase B OC CAUSE: Car vs Pole Location: Pole 499544 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Car V Pole called in by fire services Event Number F3956051, ETA requested SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): Tag Reg Update Retailer E-Mailed Yes Pole replaced Power restored 12:03Hrs Safety Disconnection at 15 Griffiths Street Tag number A37409. No one home Tag left at front of Door. | .
4913 |  | JE24013671 | GONVILLE AVE | Western | GONVILLE AVE | 2024-04-16 | 10:51 | 2024-04-16 | 13:16 | 0.0027913 | 1.9313e-05 | 7 | 1012 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Replaced Transformer X1575 - isolation at TX fuses | .
4914 |  | JE24013698 | WHIRITOA | Eastern | WHIRITOA | 2024-04-16 | 12:08 | 2024-04-17 | 1:14 | 0.74496 | 0.017955 | 6508 | 270014 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 33kV 3252, 11kV CB 1 Protection flags (nil where none): Nil CAUSE: Truck Vs Pole Location: WHIWGM175 Temp generation (state details when used): Nil PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Fine LFI (Y/N + Comments): Nil Follow up Required (select advisory)? No Additional fault restoration comments: 33& 11kV CB's opened for safety due to risk of pole falling over & driver still in the truck. Lines isolated & Pole replaced. BESS unavailable due to Planned Maintenance SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Whanagamata Circuit that tripped: 33kV CB 3252 Opened for safety DTF (KM): Nil | .
4915 |  | JE24013723 | DAIRY FACTORY | Western | DAIRY FACTORY | 2024-04-16 | 15:16 | 2024-04-16 | 17:03 | 0.015337 | 0.00014347 | 52 | 5559 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Replaced 1 X pin Arm compete Isolated at ABS S501ABS S530 ABS11352-1 & Links 11352-4 Back Feed in at S548 | .
4916 |  | JE24009187 | 5026 WHANGANUI RIVER ROAD RANANA WANGANUI | Western | RAETIHI | 2024-04-15 | 9:16 | 2024-04-15 | 13:51 | 0.0015161 | 5.5179e-06 | 2 | 550 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 2x HV poles 778494 & 778491 using helicopter. | .
4917 |  | JE24009591 | 915 COLYTON ROAD BUNNYTHORPE FEILDING | Western | COLYTON | 2024-04-15 | 8:30 | 2024-04-15 | 15:46 | 0.0024055 | 5.5179e-06 | 2 | 872 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Vegetation clearance between P17091-P28363 & P28360-P17090 | .
4918 |  | JE24010175 | 6377 STATE HIGHWAY 2 NETHERTON PAEROA | Eastern | AWAITI | 2024-04-15 | 9:09 | 2024-04-15 | 16:19 | 0.090291 | 0.00020968 | 76 | 32727 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV poles 268699, O2422 & O2123 SH2 Kerepehi. | .
4919 |  | JE24010181 | 275 PLYMOUTH ROAD OMATA NEW PLYMOUTH | Western | PIONEER RD | 2024-04-15 | 9:00 | 2024-04-15 | 15:31 | 0.05295 | 0.00014071 | 51 | 19192 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 755211 Replace pole 755209 (Digger) Replace pole 755207, and 755206 Replace poles 755204, 755203, and crossarms on pole 853248 | .
4920 |  | JE24010196 | 58B CUTFIELD ROAD NEW PLYMOUTH NEW PLYMOUTH | Western | CITY 9 | 2024-04-15 | 9:31 | 2024-04-15 | 11:28 | 0.023564 | 0.0002014 | 73 | 8541 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Isolate tx 738 to install LV fuses for saidi midigation for a pole change on the 19th of april | .
4921 |  | JE24010850 | 889 OTARAOA ROAD TIKORANGI WAITARA | Western | OTARAOA RD | 2024-04-15 | 10:14 | 2024-04-15 | 12:47 | 0.021526 | 0.00014071 | 51 | 7802 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Repair and re-sag conductors between poles 760914 and 760915 | .
4922 |  | JE24010909 | 8 KARAKA STREET MANAIA MANAIA | Western | MANAIA | 2024-04-15 | 9:20 | 2024-04-15 | 14:41 | 0.038098 | 0.00054627 | 198 | 13809 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 719517 and Replace DDO's at pole 719373 | .
4923 |  | JE24012584 | 196 TUAPIRO ROAD TAHAWAI | Eastern | BOWENTOWN | 2024-04-15 | 12:35 | 2024-04-15 | 14:55 | 0.0010773 | 8.2769e-06 | 3 | 390 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Remove Generator from Transformer TA2-087 and then connect new cable between TA2-087 & TA2-088. | .
4924 |  | JE24013207 | 1A ALTHORP AVENUE PYES PA TAURANGA | Eastern | GREEN PARK | 2024-04-15 | 10:15 | 2024-04-15 | 10:29 | 0.0038353 | 0.00028693 | 104 | 1390 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | lower tap changer on T4803 due to high voltage | .
4925 |  | JE24013556 | 239 TURAKINA VALLEY ROAD TURAKINA WANGANUI | Western | TURAKINA | 2024-04-15 | 13:28 | 2024-04-15 | 15:48 | 0.0015472 | 1.1036e-05 | 4 | 561 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: Fuses 550 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 15:48 Cause: Unknown/detrioration Weather (wind/rain): Follow up required (select advisory)? No Tony has been advised to log a tickett with Jobs that get stuck. Leave 2R open, Got to come back and replace the Fuse Unit deteriorated 20/05/2024 - Update from the hub - to be completed in July.MDP 04/07/2024 - Update - 11kv Fuses, have been wired in temporarily. This is with Jeremy Hill. HV Fuses 550. Napa # 111426 PCO was pushing out till 22/07. MDP | .
4926 |  | JE24013572 | MOUNT BRUCE | Western | MOUNT BRUCE | 2024-04-15 | 15:50 | 2024-04-15 | 18:40 | 0.0051456 | 3.0349e-05 | 11 | 1865 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Car V Pole, Isolated at Fuses 7013. Pole replaced | .
4927 |  | JE24013585 | KATERE 9 | Western | KATERE 9 | 2024-04-15 | 16:09 | 2024-04-15 | 16:39 | 8.3872e-05 | 2.759e-06 | 1 | 30 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Replaced 3 x Dead Ends at Pole 746918 - isolation at Sw/G 12376/3 | .
4928 |  | JE24013605 | TE ARAKURA | Western | TE ARAKURA | 2024-04-15 | 18:28 | 2024-04-15 | 20:10 | 0.0016987 | 1.6554e-05 | 6 | 616 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: What was replaced? LV fuseholder & 80A fuse link Where was it replaced (pole/TX/pillar box)? Is 2R required? Y 2R Y - What is the timeframe for repairs? 19/04/24 Additional Info: Isolated via Transformer T2/769 HV fuses. Toi toi caught on fire which appears to have been started by an electrical fault on the LV. FM unsure of cause and someone will need to return tomorrow under the 2R to try to determine cause in daylight. U/G Service cable to old cowshed at 123 Hansens Line has been left disconnected due to fire damage to cable and meter box. Tag #A39185. Farmer aware of fire and will be talking to insurance company. NOTE: After further details collected tomorrow, job will need to be put into safety manager before completion | .
4929 |  | JE24013606 | BARRETT RD | Eastern | BARRETT RD | 2024-04-15 | 18:10 | 2024-04-15 | 19:56 | 0.085675 | 0.0055124 | 1081 | 31053 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 5 Protection flags (nil where none): B, C Ph O/C CAUSE: Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: Recloser 9764 Opened, back feed installed via Sec 9695 Sec 9695 auto reclosed on O/C a number of times spikes over 120 Amps No Lines down at 412A OLD HIGHWAY Recloser 9764 checked with no fault found Sec 9695 Opened 19:47 No Fault found during sectionalising Suspected bird strike SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4930 |  | JE24008722 | 206 JELLICOE CRESCENT THAMES THAMES | Eastern | TOTARA | 2024-04-14 | 9:30 | 2024-04-14 | 14:21 | 0.0064045 | 2.2072e-05 | 8 | 2321 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Poles T12601 & T12602 SAFETY INCIDENT Under Access Permit - 109 035-01 NOC was informed of a Safety Incident where a crew member was struck from an object above and then taken by helicopter to Hospital. Once NOC become aware I then called the Field Switcher and the Access Permit holder to see if they were safe and able to carry on with the scope of work. Upon speaking to the Permit holder he stated that the crew was rattled and a bit shaken up.( He was okay to carry on) A new Risk Assessment was carried out and the scope of work was considered. Only one Pole change was then carried out and the second crew were stood down. | .
4931 |  | JE24010459 | Canada St Service Lane Morrinsville (Burmisters Kiosk, Morrinsville) | Eastern | LORNE ST | 2024-04-14 | 23:45 | 2024-04-20 | 2:25 | 0.039764 | 0.00029797 | 54 | 14413 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace transformer TC733 with new 750KVA & upgrade fuses 14805/2 to 80amps, . Note-: On Monday 15th no work on site Standdown for workers. Burmisters Kiosk, Morrinsville. | .
4932 |  | JE24013396 | COLOGNE ST | Western | COLOGNE ST | 2024-04-14 | 1:17 | 2024-04-14 | 4:25 | 0.041911 | 0.00024279 | 88 | 15191 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Recloser 8156 Protection flags (nil where none): B Ph, E/F CAUSE: Unknown Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Raining & Windy LFI (Y/N + Comments): N no comms to LFI's at Pole 816636 Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4933 |  | JE24013405 | KUAOTUNU | Eastern | KUAOTUNU | 2024-04-14 | 7:58 | 2024-04-14 | 16:31 | 0.52405 | 0.0044088 | 854 | 189946 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 9226/2 Auto-reclosed & SEC 9219/2 Tripped Protection flags (nil where none): A, B, C Ø O/C (REC 9226/2 operated on E/F) CAUSE: 1. Flashover at Transformer TC4041.(Explosion) Cubicle black & HV Cables/terminations damaged. 2. Broken jumper at REC 9226/2 on the Load side. (A Ø) (Repaired) 3. Broken PG clamp at SEC 9219/2 on the source side. (A Ø) (Repaired) All three Lightning Arrestors were cut away/disconnected. Location: 1. At Pad mount Transformer TC4041 2. At REC 9226/2 (Pole 263 639) 3. At SEC 9219/2 source side. Follow up Required (select advisory)? Yes, Lightning Arrestors at SEC 9219/2 need to be replaced. Additional fault restoration comments: REC 9226/2 Auto-reclosed on E/F protection and then SEC 9219/2 Tripped on A B C Ø O/C Feeder Fault was dispatched by OCT on duty, we then received a call informing us of loud bang/smoke at Transformer TC4041. (Ground Mounted) Upon arriving on site, field switcher found no smoke but black marks on the door at TC4041 NOC was receiving calls of No Power & Part Power coming in. NOC asked the Field Switchers to Investigate at Voltage Regulators namely 9742/2 & 9743/2 and test Voltages at Transformers TP1277 & TC6017.(Voltage readings were very low & abnormal) Field Switcher then went to REC 9226/2 and fo | .
4934 |  | JE24013437 | MOAWHANGO | Western | MOAWHANGO | 2024-04-14 | 13:46 | 2024-04-14 | 14:53 | 0.027035 | 0.00040281 | 146 | 9799 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | FAULT 1 Cause: Tree branch on lines Location: Pole 786220 FAULT 2 Cause: Blown HV Jumper Location: Pole 786216 Materials Used: HV conductor joint Isolation: 459 & 244/4 Weather (wind/rain): Windy Follow up Required (select advisory)? No Additional fault restoration comments: Fault Current from branch on lines likely caused Jumper to blow. Both faults in same isolation area. | .
4935 |  | JE24013457 | MAIN RD MOTONUI | Western | MAIN RD MOTONUI | 2024-04-14 | 16:25 | 2024-04-14 | 18:56 | 0.024911 | 0.0001683 | 61 | 9029 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: REC 12131/2 Protection flags (nil where none): EF CAUSE: Unknwon Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: cursory Weather (wind/rain): fine LFI (Y/N + Comments): N Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4936 |  | JE24013278 | NGARUA | Eastern | NGARUA | 2024-04-13 | 7:31 | 2024-04-13 | 9:02 | 0.00050553 | 5.5179e-06 | 2 | 183 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Repair broken jumper at Fuses FC1435 | .
4937 |  | JE24013290 | CHURCH ST | Western | CHURCH ST | 2024-04-13 | 9:01 | 2024-04-13 | 10:32 | 0.0007503 | 8.2769e-06 | 3 | 272 | Unplanned | VEGETATION - INSIDE ZONE | Repaired lines down at pole 829450 via isolation at Fuses 7645 Power restored 10;31 NDR submitted confirming vines caused | .
4938 |  | JE24013291 | WILLOUGHBY ST | Eastern | WILLOUGHBY ST | 2024-04-13 | 7:48 | 2024-04-13 | 11:16 | 0.1129 | 0.0054986 | 1119 | 40922 | Unplanned | HUMAN ERROR - POTENTIAL SWITCHING ERROR | REGULATORY INFORMATION Voltage & Device ID: Recloser 9920 and CB2 Protection flags (nil where none): EF CAUSE: Switching Error Location: Sw/Gear 13124/3 POA 2 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? No Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): Recloser & CB tripped while faultman closed Earth/Sw 13124/3 ( NAPA 107248, non-outage) while circuit was live This led to recloser (9920 & CB 2 Paeroa) tripping Faultman notified his FRM and was ok to restore supply with control Carried out restoration with faultman after he confirmed he was okay to restore network to normal. Fault man stood down after restoration | .
4939 |  | JE24013302 | MANGATEPARU | Eastern | MANGATEPARU | 2024-04-13 | 9:58 | 2024-04-13 | 12:56 | 0.0049101 | 2.759e-05 | 10 | 1780 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: Fuses FC2147 No. Fuses: 3 Fuse Amp Size: 15A TIME CLOSED: 12:56 Cause: Wind Weather (wind/rain): windy Follow up required (select advisory)? No | .
4940 |  | JE24013314 | RANGITANUKU RD | Eastern | RANGITANUKU RD | 2024-04-13 | 12:09 | 2024-04-13 | 19:37 | 0.036493 | 0.00012415 | 45 | 13227 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | ABS 905 Isolated for safety, lines hanging low across the road. Fuses FC2257 MOVED FROM POLE E2915 TO POLE E0362 to reduce SAIDI. To replace pole E2915 with only TC1157 Off 2R left open as inspector required to do checks after HV contacted LV Pump shed - 0000055955UN0FC House - Locked meter board inside TAG Bottom house by the road A39416 Contact with customer for FM to test Iso inside house to be able to complete Reco House - Locked Meter board inside - Left fuses off TAG A39417 House on top of the hill. NDR Job Inspector to come out a second job. Charge 2nd Inspector under this 2R. Leave open for 2 weeks to close. Phoned Retailer to advise, contact details Hardwood Farms 027 492 7410/027 440 8332 Mr Butler advised that the 2 properties are not occupied. Owner of Properties contact details: Murray Anderson: 078259155/ 021 026 11957 Unable to reach Owner to get the acces code to the properties as, as Hardwood Farms is only leasing the Land not the Vacant houses. FM was unable to provide ICP's to notify the retailer. Found the meter boxes Tags canceled properties teste and reconnected. Properties vacant TAGS Removed | .
4941 |  | JE24013332 | Lower Auroa Rd | Western | RIVERLEA | 2024-04-13 | 14:23 | 2024-04-13 | 16:15 | 0.00062134 | 5.5179e-06 | 2 | 225 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: 5946 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 16:15hrs Cause: Wind Weather (wind/rain): Windy / Heavy Rain Follow up required (select advisory)? | .
4942 |  | JE24013344 | SEAWARD COAST | Western | SEAWARD COAST | 2024-04-13 | 14:30 | 2024-04-13 | 16:31 | 0.0016637 | 1.3795e-05 | 5 | 603 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FM found a broken deadend & blown HV fuse at Fuses 8407 Location: 758268 Cause: Adverse Weather: Wind & corrosion Isolation: Fuses 8407 Weather (wind/rain): Light Rain / Windy Comments: FM replaced all 3x HV deadends & 1x 3Amp HV fuse link Follow up required (select advisory)? | .
4943 |  | JE24013354 | PAPAKAI | Western | PAPAKAI | 2024-04-13 | 16:33 | 2024-04-13 | 22:40 | 0.076146 | 0.00037522 | 136 | 27599 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: REC 4705 Protection flags (nil where none): A/B phase OC CAUSE: floater Location: Pole 787297 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: cursory Weather (wind/rain): windy, raining LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Delays in isolating work area due to surface flooding. ABS 424 flickers are welded closed, DNO 2404007 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4944 |  | JE24013356 | PUNGAREHU | Western | PUNGAREHU | 2024-04-13 | 14:58 | 2024-04-13 | 18:41 | 0.0061527 | 2.759e-05 | 10 | 2230 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Cause: Broken deadend & 2x HV fuses blown at Fuses PU355 What was replaced? HV deadend & 2x 10A HV fuse links Location: 851807 Cause: Wind & Corrosion Weather: Windy / Heavy Rain Additional Info: | .
4945 |  | JE24013359 | MISSION RD | Western | MISSION RD | 2024-04-13 | 17:20 | 2024-04-13 | 18:43 | 0.010313 | 0.00012415 | 45 | 3738 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | Fuses Location: 109 No. Fuses: 3 Fuse Amp Size: 25A TIME CLOSED: 1842 Cause: branch on the lines at Pole 782708, removed using hot sticks Weather (wind/rain): Windy Follow up required (select advisory)? | .
4946 |  | JE24009180 | 331 KAIKOKOPU ROAD BRUNSWICK WANGANUI | Western | BRUNSWICK | 2024-04-12 | 9:10 | 2024-04-12 | 13:05 | 0.028505 | 0.00012139 | 44 | 10332 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11KV X-Arms on pole 782480 | .
4947 |  | JE24009190 | WEST TOWN | Western | WEST TOWN | 2024-04-12 | 8:31 | 2024-04-12 | 9:02 | 0.041139 | 0.0013271 | 481 | 14911 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Perform ABS maintenance at 10482-1 and recloser maintenance at 10482-2 | .
4948 |  | JE24009488 | 494 MT HOLDSWORTH ROAD TARARUA FOREST PARK CARTERTON | Western | HOLDSWORTH | 2024-04-12 | 8:46 | 2024-04-12 | 14:36 | 0.020289 | 5.7938e-05 | 21 | 7354 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles and hardware | .
4949 |  | JE24012893 | MANAIA RD | Western | MANAIA RD | 2024-04-12 | 9:35 | 2024-04-12 | 10:55 | 0.0035263 | 4.4143e-05 | 16 | 1278 | Unplanned | VEGETATION - INSIDE ZONE | Cause: What was replaced? 2 x 63 amp Fuses Where was it replaced (pole/TX/pillar box)? Transformer 4847T Is 2R required? Y/N Y 2R Y - What is the timeframe for repairs? the next day Additional Info: Due to the weather, awaiting bucket truck to go up the pole Had to remove Vine from Pole and Transformer to carry out repairs Fuses 5962 openned at 09-35 Closed at 10-55 | .
4950 |  | JE24013030 | IHAIA RD | Western | IHAIA RD | 2024-04-12 | 11:31 | 2024-04-12 | 12:12 | 0.00091745 | 2.2072e-05 | 8 | 333 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: TA139 No. Fuses: 2 Fuse Amp Size: TIME CLOSED: 12-12 Cause: Lines Down at Pole 715789 - see SIS Weather (wind/rain): Windy Follow up required (select advisory)? | .
4951 |  | JE24013032 | PALMER RD | Western | PALMER RD | 2024-04-12 | 6:07 | 2024-04-12 | 13:06 | 0.0011559 | 2.759e-06 | 1 | 419 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 5727 No. Fuses: 2 Fuse Amp Size: 8 TIME CLOSED: Cause: 1305 Weather (wind/rain): Wind Follow up required (select advisory)?n Brad was called and confirmed all supply restored 13:19 mjk Notes Please Call Brad 0274474513 once power is restored, eqipment needs to be restarted. Customer called in for an ETR. SMC advised that they are still attending to emergencies and feeder faults, then prioritizing No power from yester day. They have asked that customers be patient, they will ATTENED ASAP | .
4952 |  | JE24013035 | KTK Sub - CB1 | Eastern | TETLEY ROAD | 2024-04-12 | 6:13 | 2024-04-12 | 9:58 | 0.12322 | 0.001294 | 469 | 44663 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 1 Protection flags (nil where none): B, C Ph O/C E/F CAUSE: Cable Fault Location: Between Pole 201327 & CB 1 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): 2404006 Circuit patrolled and type: Cursory Weather (wind/rain): Wind & Rain LFI (Y/N + Comments): Nil Follow up Required (select advisory)? Additional fault restoration comments: Fuses FP56 found blown, Lightning Arrestor at Pole 201327 Isolated at ABS,s SB2-055 & IP560 and CB 1 Back Feed installed via ABS SB2-138 Cable Break made at Pole 201327, Blown Lightning Arrestor removed. Fuses Replaced at FP56 Feeder split across KTK 2 & 3 | .
4953 |  | JE24013044 | INLAND COAST | Western | INLAND COAST | 2024-04-12 | 8:31 | 2024-04-12 | 11:36 | 0.0030666 | 1.6554e-05 | 6 | 1112 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: 12212 No. Fuses: 2 Fuse Amp Size: TIME CLOSED: 11-35 Cause: Lines Down Due to wind at Pole 755698 - see SIS Weather (wind/rain): Windy Follow up required (select advisory)? | .
4954 |  | JE24013048 | KETEMARAE RD | Western | KETEMARAE RD | 2024-04-12 | 7:05 | 2024-04-12 | 8:06 | 0.052969 | 0.00087183 | 316 | 19199 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 12418 Protection flags (nil where none): CAUSE: Line down, Recloser opened for safety due to cows dead Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Cause: Wind Tag no: Yet to be confirmed Customer advised? Y Disco safety register + emailed retailer: Y Is 2R required? Additional Info: Waiting for FM to call back with tag number Line was still energised until isolated by FM 5 x dead cows. Tag no: A42862 | .
4955 |  | JE24013050 | ASHWORTH ST | Eastern | ASHWORTH ST | 2024-04-12 | 7:59 | 2024-04-12 | 9:11 | 0.0041918 | 5.7938e-05 | 21 | 1519 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: Fused ABS 718 No. Fuses: 2 Fuse Amp Size: 30 TIME CLOSED: 09-11 - see SIS Cause: Floating Conductor Weather (wind/rain): Wind Follow up required (select advisory)? | .
4956 |  | JE24013074 | MATAROA A | Western | MATAROA A | 2024-04-12 | 8:13 | 2024-04-12 | 9:31 | 0.00021321 | 2.759e-06 | 1 | 77 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: X1157 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 09:30hrs Cause: Suspect LV line clash in wind Weather (wind/rain): Windy Follow up required (select advisory)? | .
4957 |  | JE24013079 | OAONUI | Western | OAONUI | 2024-04-12 | 9:13 | 2024-04-12 | 10:58 | 0.0017387 | 1.6554e-05 | 6 | 630 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Turn transformer T3100off for safety to pull up L/V Lines very windy Off at 09-13 ON at 10-58 | .
4958 |  | JE24013086 | IHAIA RD | Western | IHAIA RD | 2024-04-12 | 17:03 | 2024-04-12 | 18:13 | 0.00096058 | 1.3795e-05 | 5 | 348 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: TA121 No. Fuses: 2 Fuse Amp Size: TIME CLOSED: 18-12 Cause: Replaced Crossarm Complete at Pole 715230 - see SIS Weather (wind/rain): Windy Follow up required (select advisory)? | .
4959 |  | JE24013088 | WEST TOWN | Western | WEST TOWN | 2024-04-12 | 8:31 | 2024-04-12 | 9:02 | 8.5528e-05 | 2.759e-06 | 1 | 31 | Unplanned | OTHER | ICP part of HV NAPA 108868 - not advertised. Correct DTX T3/313 | .
4960 |  | JE24013112 | 762 NO 2 ROAD, TE PUKE, 3182 | Eastern | ROADS | 2024-04-12 | 13:05 | 2024-04-12 | 18:10 | 0.0025251 | 8.2769e-06 | 3 | 915 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fault Transformer TF5-009 Replaced. Isolation at TX fuses. | .
4961 |  | JE24013127 | TAWHITI RD | Western | TAWHITI RD | 2024-04-12 | 9:42 | 2024-04-12 | 10:40 | 0.00080999 | 1.3795e-05 | 5 | 294 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: CA445 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 1040 Cause: Line Clash Weather (wind/rain): wind Follow up required (select advisory)? n | .
4962 |  | JE24013136 | PLUMMERS POINT | Eastern | PLUMMERS POINT | 2024-04-12 | 13:26 | 2024-04-12 | 13:29 | 8.4424e-05 | 2.4831e-05 | 9 | 31 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FM reports testing 249V at House. Too High. Tx at off at 1325. Tap Change Back on 1329. Now 237V at house. FM reported Pole 650406 to be red defected. | .
4963 |  | JE24013137 | MCKEE SOUTH 33KV | Western | MCKEE SOUTH 33KV | 2024-04-12 | 11:26 | 2024-04-12 | 12:16 | 0.011552 | 0.00040005 | 145 | 4187 | Unplanned | THIRD PARTY INTERFERENCE - OVERHEAD CONTACT | REGULATORY INFORMATION Voltage & Device ID: 11 kv CB I51 Also 33kv circuit Above Protection flags (nil where none): C Phase E/F CAUSE: Truck Hit Lines Location: Bristol Rd Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: McKee South 33Kv DTF (KM): Truck Hit Lines at 327 Bristol Rd and the LV Line went up and hit 11kV & 33Kv lines Transformer 4299t Left off as needs inspection and 2 Road crossings repaired Truck had left site by the time Faultman Got to site One of the people at site said it was a Orions Truck Orions Said that they had a truck down the road at that time. LV Truck took road crossing Each house was tested. TX 4299T Power have been restored 760386 Lv road crossing has been Re sagged. Pole 760388 Service from this pole across the road. was not needed as it snapped off the fm cut it away and made it safe. | .
4964 |  | JE24013156 | KAIMAI DRIVE | Eastern | KAIMAI DRIVE | 2024-04-12 | 12:37 | 2024-04-12 | 15:42 | 0.03995 | 0.0002152 | 78 | 14480 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Sect 13208 Protection flags (nil where none): E/F O/C CAUSE: Line Down Location: 217917 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: cursory Weather (wind/rain): Wind, Rain LFI (Y/N + Comments): Nil Follow up Required (select advisory)? No Additional fault restoration comments: FM still to check whether fault was caused by a line clash due to wind, or if it contacted trees. Will come through with job pack. | .
4965 |  | JE24013163 | OLD TAURANGA RD | Eastern | OLD TAURANGA RD | 2024-04-12 | 12:56 | 2024-04-12 | 14:09 | 0.049094 | 0.00073113 | 265 | 17794 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | REGULATORY INFORMATION Voltage & Device ID: 11kV, Sec 13005/2 Protection flags (nil where none): E/F, B phase CAUSE: Tree Branch sitting on lines Location: P1930 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Yes, Cursory Weather (wind/rain): Windy LFI (Y/N + Comments): Yes / SAP 13588589 operated correctly Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4966 |  | JE24013168 | PYES PA | Eastern | PYES PA | 2024-04-12 | 13:04 | 2024-04-12 | 14:42 | 0.10676 | 0.0014678 | 532 | 38695 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 1 Protection flags (nil where none): A,B,C E/F CAUSE: Bird Strike Location: IP581 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): NO Circuit patrolled and type: Cursory Weather (wind/rain): Wind Rain LFI (Y/N + Comments): Nil Follow up Required (select advisory)? No Additional fault restoration comments: FM found dead badly burnt pukeko | .
4967 |  | JE24013178 | WAIMAPU | Eastern | WAIMAPU | 2024-04-12 | 13:48 | 2024-04-12 | 15:05 | 0.029691 | 0.00038901 | 141 | 10762 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV, Sec 13273/2, Rec 9168 A/R Protection flags (nil where none): E/F, O/C B phase CAUSE: Unk Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): Windy / Heavy Rain LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4968 |  | JE24013194 | SMITH ST | Eastern | SMITH ST | 2024-04-12 | 14:18 | 2024-04-12 | 15:40 | 0.0018111 | 2.2072e-05 | 8 | 656 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: FC2177 No. Fuses: 2 Fuse Amp Size: 3Amp TIME CLOSED: 15:40 Cause: Weather Weather (wind/rain): Wind Rain Follow up required (select advisory)? No | .
4969 |  | JE24013200 | BOWENTOWN | Eastern | BOWENTOWN | 2024-04-12 | 14:29 | 2024-04-12 | 17:53 | 0.18481 | 0.0017078 | 619 | 66984 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 2 Protection flags (nil where none): Ph B Fault CAUSE: Line down due to weather Location: Pole 396202 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Wind Rain LFI (Y/N + Comments): Nil Follow up Required (select advisory)? Additional fault restoration comments: | .
4970 |  | JE24013240 | KAIMAI DRIVE | Eastern | KAIMAI DRIVE | 2024-04-12 | 17:11 | 2024-04-12 | 21:48 | 0.0038267 | 1.3795e-05 | 5 | 1387 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: TE2-008 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 21:48 Cause: LV LINES DOWN, REPAIRS MADE pole 423341 Weather (wind/rain): rain & wind Follow up required (select advisory)? | .
4971 |  | JE24013241 | MT STEWART | Western | MT STEWART | 2024-04-12 | 17:16 | 2024-04-12 | 20:06 | 0.035733 | 0.0017713 | 642 | 12952 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: CB 5 Protection flags (nil where none): B phase EF CAUSE: line down caused by a faulty insulator Location: Between Poles P31193 and P31195 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: cursory Weather (wind/rain): raining LFI (Y/N + Comments): N Follow up Required (select advisory)? n Additional fault restoration comments: Isolated at ABS 10829/1, L52 & L48, Insulator replaced, line repaired, full power restored SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
4972 |  | JE24013250 | KEENAN RD | Eastern | KEENAN RD | 2024-04-12 | 18:36 | 2024-04-13 | 13:31 | 0.0062612 | 5.5179e-06 | 2 | 2269 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | Fuses Location: Transformer TE3-133 No. Fuses: 3 Fuse Amp Size: 3A TIME CLOSED: 13:30 Cause: TREES Weather (wind/rain): Windy Follow up required (select advisory)?No | .
4973 |  | JE24013252 | WAIMAPU | Eastern | WAIMAPU | 2024-04-12 | 20:50 | 2024-04-13 | 10:00 | 0.0021788 | 2.759e-06 | 1 | 790 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Transformer TF4-051 replaced 12/04 ,Power on 10:00 Hrs via isolation at Transformer fuses. | .
4974 |  | JE24013254 | CLOTON RD NORTH | Western | CLOTON RD NORTH | 2024-04-12 | 14:01 | 2024-04-12 | 19:08 | 0.03728 | 0.00012139 | 44 | 13512 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Fuses Location: FABS 5539 No. Fuses: 2 Fuse Amp Size: 25 TIME CLOSED: 19:08 Cause: unknown Weather (wind/rain): wind and rain Follow up required (select advisory)?n | .
4975 |  | JE24013255 | 285 DENBIGH ROAD MIDHIRST STRATFORD | Western | CLOTON RD NORTH | 2024-04-12 | 19:50 | 2024-05-10 | 13:34 | 0.1102 | 2.759e-06 | 1 | 39944 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Low 11kV lines (unsafe to liven) to old cowshed that is only used for once a month by the farmer, Downer to arrange with farmer to pull up line and possible replace a pole that has sunk into the ground, fine weather required to access assets Fuses 6246 were found blown on a main line patrol on another fault Downer to apply for an urgent outage for switching to be written up 01/05/2024 - HV NAPA 110372 on the 10/05/2024. MDP Power off until planned job was completed | .
4976 |  | JE24013267 | TAVERNER ST | Western | TAVERNER ST | 2024-04-12 | 20:30 | 2024-04-12 | 21:56 | 0.030018 | 0.00035039 | 127 | 10880 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | 11kV Recloser C429 tripped OC B & C phase + EF Pole 821151 gum bark found over lines removed with hot sticks Recloser C429 out of scan when tripped take first call time Recloser C429 went out of scan when closed , dressed closed via scan inhibiting; faultman confirmed lights at their location take restore power time as 21:56 | .
4977 |  | JE24013273 | COROGLEN | Eastern | COROGLEN | 2024-04-12 | 22:20 | 2024-04-13 | 2:00 | 0.0060744 | 2.759e-05 | 10 | 2202 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses FC4133 2 x 3A 02:00 Cause Unknown Faultman stopped to confirm safety of crashed car driver before proceeding with job | .
4978 |  | JE24015214 | PAPANUI ST | Eastern | PAPANUI ST | 2024-04-12 | 16:46 | 2024-04-12 | 17:13 | 0.00050793 | 1.9313e-05 | 7 | 184 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Generator removal off transformer TC3363 part of Switching E00120 12/04/24 Advertised 11/04 at 14:55, outage is planned. | .
4979 |  | JE24009177 | 2 DAMPNEYS ROAD TIAKITAHUNA PALMERSTON NORTH | Western | BAINESSE | 2024-04-11 | 8:31 | 2024-04-11 | 12:24 | 0.021908 | 9.3805e-05 | 34 | 7941 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replacing poles and hardware between P45221 and P45236. Replacing 50kVA transformer T2/82. | .
4980 |  | JE24009551 | 307 BRUNSWICK ROAD BRUNSWICK WANGANUI | Western | BRUNSWICK | 2024-04-11 | 9:46 | 2024-04-11 | 15:52 | 0.037301 | 0.00010208 | 37 | 13520 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11KV poles & X-Arms between poles 706722 & 782728 & Remove TEMP 11KV ABS 136 from 706722 | .
4981 |  | JE24009556 | 1415 STATE HIGHWAY 53 MARTINBOROUGH MARTINBOROUGH | Western | TAWAHA | 2024-04-11 | 8:45 | 2024-04-11 | 12:22 | 0.00059971 | 2.759e-06 | 1 | 217 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Re conductor between fuses 7204 and T1907 | .
4982 |  | JE24009808 | 7313 STATE HIGHWAY 4 TOHUNGA JUNCTION RAETIHI | Western | RAETIHI | 2024-04-11 | 10:02 | 2024-04-11 | 15:32 | 0.12987 | 0.00039453 | 143 | 47072 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Tree contractor working between poles 776360 & 776351. | .
4983 |  | JE24010006 | 2 TAURANGA-A-IKA STREET MANAIA MANAIA | Western | OTAKEHO | 2024-04-11 | 9:00 | 2024-04-11 | 14:33 | 0.1276 | 0.0003835 | 139 | 46248 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11KV poles 719786, 719787 and 719736 | .
4984 |  | JE24010049 | 115 BALMORAL DRIVE TOKOROA TOKOROA | Eastern | LOMOND AVE | 2024-04-11 | 8:31 | 2024-04-11 | 11:07 | 0.038375 | 0.00024555 | 89 | 13909 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9110-1/2/3 | .
4985 |  | JE24010101 | 43B PUTAHI ROAD PATEA PATEA | Western | OTAUTU | 2024-04-11 | 9:15 | 2024-04-11 | 13:22 | 0.012933 | 5.242e-05 | 19 | 4688 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles for Blitz Putahi Road project between poles 727375 & 727384 | .
4986 |  | JE24010114 | 424 MOTUKAWA ROAD TARATA INGLEWOOD | Western | KAIMATA | 2024-04-11 | 9:35 | 2024-04-11 | 12:09 | 0.0072245 | 4.6902e-05 | 17 | 2619 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Asplundh vegetation clearance in between poles 758692 - 758689 | .
4987 |  | JE24010123 | 71 MOUNTAIN ROAD SENTRY HILL NEW PLYMOUTH | Western | WAITARA RD | 2024-04-11 | 9:53 | 2024-04-11 | 10:52 | 0.00245 | 4.1384e-05 | 15 | 888 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | to replace red defect arm on pole 745501 | .
4988 |  | JE24010128 | 484 CORBETT ROAD LEPPERTON NEW PLYMOUTH | Western | WAITARA RD | 2024-04-11 | 13:00 | 2024-04-11 | 13:43 | 0.0096678 | 0.00022623 | 82 | 3504 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace defective arm on pole 743778 | .
4989 |  | JE24010134 | 40 TEBBUTT ROAD WAIROA TAURANGA | Eastern | KAIMAI DRIVE | 2024-04-11 | 9:20 | 2024-04-11 | 14:58 | 0.027976 | 8.2769e-05 | 30 | 10140 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV/400V poles 217776 & 217778. Replace 11kV cross arms @ pole 217777. Replace 11kV overhead conductor between poles 217776 & 217778. | .
4990 |  | JE24010136 | 1580 WHITE ROCK ROAD TUTURUMURI MARTINBOROUGH | Western | FEATHERSTON 33KV | 2024-04-11 | 9:34 | 2024-04-11 | 12:15 | 0.08512 | 0.00052972 | 192 | 30852 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 33kv jumper at pole 811184 inspect VT at 33KV CB 3537 | .
4991 |  | JE24010159 | 1285 RUANUI ROAD TAIHAPE TAIHAPE | Western | MATAROA A | 2024-04-11 | 8:44 | 2024-04-11 | 14:45 | 0.00099847 | 2.759e-06 | 1 | 362 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT Replace rotten H-pole structure - Pole:785958 & 785959 | .
4992 |  | JE24012404 | 137 PENNY ROAD RONGOTEA PALMERSTON NORTH | Western | RONGOTEA | 2024-04-11 | 9:16 | 2024-04-11 | 11:34 | 0.00076193 | 5.5179e-06 | 2 | 276 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace TX arms and Tx T1/218 due to the arms being rotten needs to replaced | .
4993 |  | JE24012809 | IHAIA RD | Western | IHAIA RD | 2024-04-11 | 8:00 | 2024-04-11 | 10:30 | 0.0066097 | 4.4143e-05 | 16 | 2396 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Found lines down at 2 sites after Fuses TA 191 Repaired both sites Reloaded and liven | .
4994 |  | JE24012836 | GLOVER RD EAST | Western | GLOVER RD EAST | 2024-04-11 | 8:52 | 2024-04-11 | 12:23 | 0.15678 | 0.0010098 | 366 | 56826 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11KV Rec 6728 Protection flags (nil where none): A & B Phase E/F CAUSE: Lines down Location: Pole 726002 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Weather (wind/rain): Windy LFI (Y/N + Comments): No Follow up Required (select advisory)? Additional fault restoration comments: King Bolt at The pole rusted off causing Problem | .
4995 |  | JE24012849 | MANAIA | Western | MANAIA | 2024-04-11 | 9:00 | 2024-04-11 | 14:33 | 0.00091795 | 2.759e-06 | 1 | 333 | Unplanned | OTHER | Cause: Data incorrect What was replaced? FM confirmed customer is feeding of TX 5145E Ground mounted tX that feeds all OH Lines. Where was it replaced (pole/TX/pillar box)? Correct TX 5145E Is 2R required? N 2R Y - What is the timeframe for repairs? Additional Info: They are apart of HV NAPA 108275 AI emailed? Yes | .
4996 |  | JE24012852 | RIVERLEA | Western | RIVERLEA | 2024-04-11 | 9:26 | 2024-04-11 | 11:25 | 0.00065967 | 5.5179e-06 | 2 | 239 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: 5946 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 11-25 Cause: Lines out of sag will go back and repair when wind and other Jobs end Weather (wind/rain): Windy Follow up required (select advisory)? 20/05/2024 - All work has been completed under NAPA 110333 on the 09/05/2024. MDP | .
4997 |  | JE24012869 | PARIHAKA | Western | PARIHAKA | 2024-04-11 | 12:25 | 2024-04-12 | 8:51 | 0.040591 | 3.3108e-05 | 12 | 14712 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Left off over night as crossarm needed replacing and high winds Went back next day 12/04/24 and talked to owner and going to put in a job to repair a few faults on line Liven up on the 12/04/24 at 08-51 | .
4998 |  | JE24012876 | TAWHITI RD | Western | TAWHITI RD | 2024-04-11 | 11:34 | 2024-04-11 | 15:50 | 0.0035339 | 1.3795e-05 | 5 | 1281 | Unplanned | VEGETATION - OUTSIDE ZONE | Fuses Location: CA465 No. Fuses: 3 Fuse Amp Size: TIME CLOSED: 15-50 Cause: Tree on Line Weather (wind/rain): Windy Follow up required (select advisory)? all 3 fuses blown - see SIS | .
4999 |  | JE24012903 | WATERWORKS RD | Western | WATERWORKS RD | 2024-04-11 | 13:05 | 2024-04-12 | 14:57 | 0.12612 | 0.00014071 | 40 | 45712 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 1026 Protection flags (nil where none): C fault, E/F CAUSE: lines down due to trees Location: between pole 784211 & 784213 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): Wind, Rain LFI (Y/N + Comments): Yes, indicated correctly Follow up Required (select advisory)? Protection review to see if line fusing is correct. Additional fault restoration comments: Line patrol called off at 17:30, crew will return in the morning. | .
5000 |  | JE24012909 | TUTAENUI | Western | TUTAENUI | 2024-04-11 | 13:26 | 2024-04-11 | 15:51 | 0.020854 | 0.00014347 | 52 | 7559 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 1kV Sec 4856, Rec 4237 A/R Protection flags (nil where none): A, B Ph O/D CAUSE: Line down due to weather (16mm copper) Location: pole 974480 | .
5001 |  | JE24012921 | MANAWAPOU RD | Western | MANAWAPOU RD | 2024-04-11 | 17:02 | 2024-04-11 | 18:09 | 0.0081112 | 0.00012139 | 44 | 2940 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Floating Conductor at Pole 728522 Isolation between ABS 6671 and Reg 12272. | .
5002 |  | JE24012923 | RAHOTU 33KV | Western | RAHOTU 33KV | 2024-04-11 | 14:00 | 2024-04-11 | 17:57 | 0.25033 | 0.0015919 | 577 | 90733 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 33kV CB 3212 Protection flags (nil where none): T1787 LV DEFT EF CAUSE: Transformer T1 Tripped Location: Ngariki Temp generation (state details when used): Nil PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): High Wind Rain LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Ngariki Circuit that tripped: 3212 DTF (KM): N/A NOC job created to get crews going as job defaulted to Tauranga North AOR. SMC couldn't dispatch Fault staff A floating conductor was found at Pole 711422 which is on NG2 this was the only thing found that MAY have caused outage Repaired after Liven up the sub and all good | .
5003 |  | JE24012926 | IHAIA RD | Western | IHAIA RD | 2024-04-11 | 14:07 | 2024-04-11 | 19:12 | 0.010081 | 3.3108e-05 | 12 | 3654 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fuses Location: Fuses TA189 No. Fuses: 2 Fuse Amp Size: 8 TIME CLOSED: 19:11 Cause: wind Weather (wind/rain): Windy Follow up required (select advisory)? no | .
5004 |  | JE24012927 | TE ROTI | Western | TE ROTI | 2024-04-11 | 14:12 | 2024-04-11 | 19:51 | 0.0074774 | 2.2072e-05 | 8 | 2710 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 6088 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 19:50 Cause: Unknown lines patrolled Weather (wind/rain): High wind Follow up required (select advisory)? no | .
5005 |  | JE24012932 | FORDELL | Western | FORDELL | 2024-04-11 | 14:22 | 2024-04-11 | 15:21 | 0.0011531 | 1.9313e-05 | 7 | 418 | Unplanned | VEGETATION - INSIDE ZONE | Fuses Location: X427 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 1521 Cause: trees in the LV lines Weather (wind/rain): raining, windy Follow up required (select advisory)? also replaced 3 x63A fuses as 80A fuses were too high causing the HV fuses to blow for trees in the LV. Fuses found blown when Gary was driving by | .
5006 |  | JE24012945 | INLAND COAST | Western | INLAND COAST | 2024-04-11 | 18:46 | 2024-04-11 | 20:31 | 0.0017439 | 1.6554e-05 | 6 | 632 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: Fuses 12212 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: Cause: Blown Insulator at Pole 755687 Weather (wind/rain): Wet & Windy Follow up required (select advisory)? 1 x HV pin cross arm replaced under access permit - see SIS | .
5007 |  | JE24012952 | OPUNAKE | Western | OPUNAKE | 2024-04-11 | 19:49 | 2024-04-11 | 21:00 | 0.018827 | 0.00026486 | 96 | 6824 | Unplanned | DEFECTIVE EQUIPMENT - LINE CLASH | Fault beyond Fuses 6253 Deemed unsafe to liven due to clashing in high wind. HV jumpers clashing in the wind Back feed transformer over night and on the 12/04/24 Fitted terminations and re liven Transformer Downer is going to defect the pole | .
5008 |  | JE24012961 | IRIRANGI | Western | IRIRANGI | 2024-04-11 | 20:12 | 2024-04-12 | 13:30 | 0.080184 | 7.7251e-05 | 28 | 29063 | Unplanned | VEGETATION - INSIDE ZONE | Fuses Location: 2601 No. Fuses: 2 Fuse Amp Size: 8A TIME CLOSED: 1330 Cause: Weather / large trees touching lines in high winds Weather (wind/rain): Wind & Rain Follow up required (select advisory)? Trees need to be cut in the morning. Removed using hot sticks, restored 1330 - see SIS | .
5009 |  | JE24012963 | NGARIKI RD | Western | NGARIKI RD | 2024-04-11 | 16:48 | 2024-04-11 | 21:42 | 0.0097516 | 3.3108e-05 | 12 | 3535 | Unplanned | VEGETATION - WIND-BLOWN DEBRIS - TREES | Fuses Location: NG406 No. Fuses: 2 Fuse Amp Size: 15A TIME CLOSED: 21:42 Cause: Branch blown onto lines removed with hot stick Weather (wind/rain): High wind / rain Follow up required (select advisory)? No | .
5010 |  | JE24012976 | BRUNSWICK | Western | BRUNSWICK | 2024-04-11 | 15:25 | 2024-04-11 | 17:31 | 0.0041583 | 3.3108e-05 | 12 | 1507 | Unplanned | VEGETATION - OUTSIDE ZONE | Fuses Location: 986 No. Fuses: 2 Fuse Amp Size: 10 TIME CLOSED: 1730 Cause: Wind and suspected Tree contact Weather (wind/rain): Wind Follow up required (select advisory)? n | .
5011 |  | JE24012978 | IRIRANGI | Western | IRIRANGI | 2024-04-11 | 17:25 | 2024-04-11 | 20:20 | 0.0052981 | 3.0349e-05 | 11 | 1920 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 2563 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 20:20 Cause: Unknown lines patrolled Weather (wind/rain): High winds Follow up required (select advisory)? No | .
5012 |  | JE24012988 | BRUNSWICK | Western | BRUNSWICK | 2024-04-11 | 18:03 | 2024-04-11 | 21:00 | 0.0014639 | 8.2769e-06 | 3 | 531 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Y26 No. Fuses: 2 Glass type Fuse Amp Size: 3A TIME CLOSED: 21:00 Cause: Unknown, line patrolled. Weather (wind/rain): High wind Follow up required (select advisory)? No | .
5013 |  | JE24012991 | PUNGAREHU | Western | PUNGAREHU | 2024-04-11 | 19:12 | 2024-04-11 | 21:46 | 0.013194 | 8.5528e-05 | 31 | 4782 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Fuses PU369 Protection flags (nil where none): Nil CAUSE: Lines down due to corrosion Location: Pole 711180 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: F4, cursory patrol past Fuses PU369 Weather (wind/rain): High wind / rain LFI (Y/N + Comments): Not fitted Follow up Required (select advisory)? No Additional fault restoration comments: 5m x 16mm² HD Cu conductor 3 x 16mm² MST sleeves SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
5014 |  | JE24013002 | GORDON | Eastern | GORDON | 2024-04-11 | 19:40 | 2024-04-14 | 15:09 | 0.067023 | 1.6554e-05 | 6 | 24293 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | 14/04 Access was made, Fuses FC2297 were blown. Power On at 15:08. 2 x 3 Amp Fuses. Cause: Suspect Strong winds Full Power has been restored. 11/04 Charlie reported that it is too windy to go up the Hill to the repeater station, Te Weraiti. LFIs at ABS IC1066 are flashing towards the Repeater stn. Charlie coming back in the morning to look at Fuses FC2297. The Repeater station has a generator which can run for a week, while repairs are taking place 2R left open for further checks during daylight 12/04/2024 14:34 - Still cloudy - Peter Malone advised that. another guy today and it is still windy, and unsafe. 13/04 - Called SMC for an update, they will call back and advise what is happening at site today. 13/04 - Customer has a generator, repeater site currently has power, track is washed out and FM will return when the weather is better. customer advised that their generator will last one week 13/04 - Customer call in again regarding this job, advised the the FM had spoken with them and they said it maybe be another provider as there are multiple providers on this site. This customer does have a generator as well, but is only good for 24 - 48hrs. SMC was updated FM confirmed Barton road is one job. Customer with the gene 14/04 Access was made, Fuses FC2297 were blown. Power On at 15:08. 2 x 3 Amp | .
5015 |  | JE24013017 | RAWHITIROA | Western | RAWHITIROA | 2024-04-11 | 22:17 | 2024-04-12 | 15:49 | 0.02978 | 0.00021796 | 42 | 10794 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 12246 Protection flags (nil where none): E/F B Ø CAUSE: Found Floating Conductor at Pole 736393 PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): LFI (Y/N + Comments): Follow up Required (select advisory)? Additional fault restoration comments: Fuses 6029 Open & tagged, lines to be patrolled in the morning. 12/04 - Taken out Polaris 4WD for access to lines for scoping - As per Jacob Northcott | .
5016 |  | JE24013019 | MAUNGAKAWA ROAD | Eastern | MAUNGAKAWA ROAD | 2024-04-11 | 22:34 | 2024-04-12 | 8:10 | 0.17205 | 0.0012691 | 396 | 62362 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | REGULATORY INFORMATION Voltage & Device ID: CB 5 Protection flags (nil where none): Phase B, C Fault, OC CAUSE: Damaged Jumpers Location: Fault at ABS IC2111 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Raining, Windy LFI (Y/N + Comments): N Follow up Required (select advisory)? N Additional fault restoration comments: Isolated at CB 5 & ABS 649 Back Feeds installed Jumpers replaced SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
5017 |  | JE24013020 | BRUNSWICK | Western | BRUNSWICK | 2024-04-11 | 20:43 | 2024-04-12 | 10:16 | 0.026918 | 3.3108e-05 | 12 | 9757 | Unplanned | VEGETATION - OUTSIDE ZONE | Fuses Location: 986 No. Fuses:2 Fuse Amp Size: 8 TIME CLOSED: 1015 Cause: Trees over the lines due to high winds Weather (wind/rain): High Wind, Rain Follow up required (select advisory)? no | .
5018 |  | JE24013129 | IRIRANGI | Western | IRIRANGI | 2024-04-11 | 21:08 | 2024-04-12 | 10:45 | 0.024808 | 3.0349e-05 | 11 | 8992 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: 2563 No. Fuses: 2 Fuse Amp Size: 8A TIME CLOSED: 10:45hrs Cause: Wind Weather (wind/rain): Windy / Heavy Rain Follow up required (select advisory)? | .
5019 |  | JE24008761 | 1000 TORA ROAD TORA MARTINBOROUGH | Western | TUTURUMURI | 2024-04-10 | 8:46 | 2024-04-10 | 15:34 | 0.11944 | 0.00029245 | 106 | 43292 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT-vegetation tree cutting between poles site 1 pole 363438 to 811936, site 2 pole 848555 to 816057 | .
5020 |  | JE24009165 | 434 RUAHINE ROAD MANGAWEKA KIMBOLTON | Western | MANGAWEKA | 2024-04-10 | 9:10 | 2024-04-10 | 11:45 | 0.0076859 | 4.9661e-05 | 18 | 2786 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT - Re-sag out of tolerance span 849937-849936 & Remove vegetation and re-sag span 843034-796751 | .
5021 |  | JE24009169 | 32 KARAMU STREET TAWHERO WANGANUI | Western | SPRINGVALE | 2024-04-10 | 9:00 | 2024-04-10 | 9:56 | 0.010619 | 0.00019037 | 69 | 3849 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Top up transformer 3042W with oil | .
5022 |  | JE24009170 | 90 KAKARIKI ROAD TAIHAPE TAIHAPE | Western | MOAWHANGO | 2024-04-10 | 9:16 | 2024-04-10 | 11:01 | 0.00028942 | 2.759e-06 | 1 | 105 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install new lightning arresters at transformer X463. | .
5023 |  | JE24009173 | 277 SNODGRASS ROAD WHAKAMARAMA | Eastern | TE PUNA | 2024-04-10 | 9:03 | 2024-04-10 | 15:16 | 0.0041094 | 1.1036e-05 | 4 | 1489 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install and commission new 11kv Recloser # 14815 @ pole 483530. Remove 400 amp links 13333. remove redundant 400vt pilot conductors between pole 210432 0 210434. Isolation and issuer earths @ links temp 25 and sw/gear 13890/3. | .
5024 |  | JE24009988 | 415A WAIHAPA ROAD PUKENGAHU STRATFORD | Western | CLOTON RD INDUSTRIAL | 2024-04-10 | 9:46 | 2024-04-10 | 13:17 | 0.0029144 | 1.3795e-05 | 5 | 1056 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace surge arrestors at ABS 5784. replace cross arms at pole 738443 | .
5025 |  | JE24010043 | 20 BOSCABEL DRIVE OHAUITI TAURANGA | Eastern | OHAUITI RD | 2024-04-10 | 12:16 | 2024-04-10 | 13:32 | 0.01509 | 0.00019865 | 72 | 5469 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To carry out 11kV Link Box maintenance on TD4-731 - PE0017 | .
5026 |  | JE24010131 | 33 PANORAMA DRIVE WELCOME BAY TAURANGA | Eastern | KAITEMAKO RD | 2024-04-10 | 8:47 | 2024-04-10 | 10:38 | 0.022669 | 0.00020416 | 74 | 8216 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To carry out 11kV Link Box maintenance on TD4-727 - PE0017 | .
5027 |  | JE24010156 | 122 No4 Line Ashhurst 4884 | Western | POHANGINA | 2024-04-10 | 9:15 | 2024-04-10 | 11:20 | 0.0017204 | 1.3795e-05 | 5 | 624 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT - Re-sag oh 11kv lines - 122 No4 Line P11724-P11725 | .
5028 |  | JE24010805 | 4 STATION ROAD HUNTERVILLE HUNTERVILLE | Western | HUNTERVILLE 22KV | 2024-04-10 | 9:03 | 2024-04-10 | 16:41 | 0.11076 | 0.00025107 | 91 | 40145 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Combined works : Downers - Replace switch, 22kV ABS 089 DNO 2311014 NPE - Replace Red Tag Poles 808034, 808035 | .
5029 |  | JE24012658 | NO 3 ROAD | Eastern | NO 3 ROAD | 2024-04-10 | 3:20 | 2024-04-10 | 6:28 | 0.25788 | 0.0019202 | 696 | 93469 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV ATU CB2 Protection flags (nil where none): A B C Ø O/C & E/F CAUSE: Unknown Location: Unknown Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Light Rain LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: Feeder fault on ATU CB2 Tripped, awaiting field switchers to start with the Line Patrol. Due to a break in the Network at Sw/Gear 13145/1, no option was available to back feed any ICP's as SEC 9878/2 was already closed via TPV4 ABS SE5-042 has been opened and a Line Patrol down the main line (No. 3 Road) towards Recloser RP10 is being carried out. Nothing abnormal was seen during the Line Patrol, NOC Opened Recloser RP10. CB 2 was closed in successfully at 04:39 and then REC RP10 closed in at 04:41. Field Switcher is busy with the section of O/H Line up to ABS IP549 which is open. ABS SE5-042 Closed in at 04:55 Section between ABS IP549 to the Open Point at Sw/Gear 9543/1 being investigated now. After carrying out a Line Patrol on this Feeder, no fault was found. Full Power restored to all ICP's at 06:27 | .
5030 |  | JE24012663 | DEVON RD | Western | DEVON RD | 2024-04-10 | 7:07 | 2024-04-10 | 8:48 | 0.086955 | 0.0010015 | 363 | 31517 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 12214 Protection flags (nil where none): O/C B - C Ø CAUSE: Unknown lines patrolled. Location: Unknown Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N/A Circuit patrolled and type: F1, cursory patrolled. Weather (wind/rain): Calm LFI (Y/N + Comments): Yes installed none activated. Follow up Required (select advisory)? No Additional fault restoration comments: Lines patrolled no fault cause could be found. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
5031 |  | JE24012734 | 454 NORFOLK ROAD UPPER, NORFOLK, INGLEWOOD, 4388 | Western | MOUNTAIN RD | 2024-04-10 | 13:20 | 2024-04-10 | 14:25 | 0.013312 | 0.00020692 | 75 | 4825 | Unplanned | HUMAN ERROR - POTENTIAL WORKMANSHIP | Poletech found two poles where the king bolts were on the way to fall out. ABS 5538 was opened and at pole 441075 & 444236 the king bolts were repaired. | .
5032 |  | JE24012799 | MANAIA | Western | MANAIA | 2024-04-10 | 17:41 | 2024-04-10 | 19:01 | 0.00021938 | 2.759e-06 | 1 | 80 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 6840 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 19:00 Cause: Unknown, lines patrolled. Weather (wind/rain): Calm Follow up required (select advisory)? No | .
5033 |  | JE24003058 | 25 PEMBROKE ROAD STRATFORD STRATFORD | Western | CLOTON RD WEST | 2024-04-09 | 9:46 | 2024-04-09 | 15:28 | 0.10302 | 0.00030073 | 109 | 37342 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11KV ABS 5712 pole structure 734044 ( DNO 2309012 ) | .
5034 |  | JE24008710 | 29 JACKEYTOWN ROAD TIAKITAHUNA PALMERSTON NORTH | Western | BAINESSE | 2024-04-09 | 8:36 | 2024-04-09 | 13:11 | 0.025754 | 9.3805e-05 | 34 | 9335 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replacing poles and hardware between poles P45242 and P43232. Replace 50kVA transformer T2/249 | .
5035 |  | JE24008738 | 1256 STATE HIGHWAY 3 MARTON MARTON | Western | LAKE ALICE | 2024-04-09 | 9:05 | 2024-04-09 | 14:29 | 0.028645 | 8.8287e-05 | 32 | 10382 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace multiple defected 6.6KV poles & x-arms past 6.6KV Fuses 973 between poles 806282 | .
5036 |  | JE24008741 | 2 HAMPTON PLACE SPRINGVALE WANGANUI | Western | SPRINGVALE | 2024-04-09 | 9:20 | 2024-04-09 | 10:18 | 0.014736 | 0.00025658 | 93 | 5341 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Top transformer 3140W with oil | .
5037 |  | JE24008758 | 6900 STATE HIGHWAY 1 MANGAWEKA TAIHAPE | Western | MANGAWEKA | 2024-04-09 | 10:31 | 2024-04-09 | 14:05 | 0.0041419 | 1.9313e-05 | 7 | 1501 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT - Replace pole 848296, Re-sag out of tolerance sags between 848296 - 807900 & 807921 - 807924 | .
5038 |  | JE24009067 | 1415 STATE HIGHWAY 53 MARTINBOROUGH MARTINBOROUGH | Western | TAWAHA | 2024-04-09 | 8:45 | 2024-04-09 | 13:46 | 0.00082819 | 2.759e-06 | 1 | 300 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 815063 and transformer pole T1907 | .
5039 |  | JE24009779 | (GLEN NUI ROAD )2314 RAWHITIROA ROAD MATEMATEAONGA ELTHAM | Western | RAWHITIROA | 2024-04-09 | 9:30 | 2024-04-09 | 15:41 | 0.015343 | 4.1384e-05 | 15 | 5561 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | asplundh to cut trees between poles 736449 & 736455 | .
5040 |  | JE24009885 | 43 Putahi Road Whenuakara | Western | OTAUTU | 2024-04-09 | 9:15 | 2024-04-09 | 14:28 | 0.016397 | 5.242e-05 | 19 | 5943 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles for Blitz Putahi Road project from pole 727359 to pole 727374 | .
5041 |  | JE24009891 | 183 PARAITE ROAD PARAITE NEW PLYMOUTH | Western | PARAITE RD | 2024-04-09 | 9:30 | 2024-04-09 | 15:04 | 0.036867 | 0.00011036 | 40 | 13363 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace red defect Pole 743565 | .
5042 |  | JE24009897 | 113 MANGATI ROAD BELL BLOCK NEW PLYMOUTH | Western | KATERE 12 | 2024-04-09 | 10:01 | 2024-04-09 | 13:20 | 0.083502 | 0.00041936 | 152 | 30266 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Clean enclosure, magnefix and HV cable terms site switch gear 1417. | .
5043 |  | JE24009992 | 155 WAITAHA ROAD WELCOME BAY TAURANGA | Eastern | VICTORY STREET | 2024-04-09 | 8:45 | 2024-04-09 | 10:11 | 0.050126 | 0.0005849 | 212 | 18168 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To carry out 11kV Link Box maintenance on TD4-572 - PE0017 | .
5044 |  | JE24010037 | 40 TEBBUTT ROAD WAIROA TAURANGA | Eastern | KAIMAI DRIVE | 2024-04-09 | 9:15 | 2024-04-09 | 14:56 | 0.028186 | 8.2769e-05 | 30 | 10216 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV/400V poles 217773, 217775 & 217780. Replace Transformer TD3-329. | .
5045 |  | JE24010041 | 40 MORVERN CRESCENT TOKOROA TOKOROA | Eastern | ARAWA ST | 2024-04-09 | 10:46 | 2024-04-09 | 14:00 | 0.044494 | 0.00022899 | 83 | 16127 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 11kv oil maintenance - 9192-1/2/3/4 | .
5046 |  | JE24010115 | 22 RESOLUTION ROAD WELCOME BAY TAURANGA | Eastern | WELCOME BAY | 2024-04-09 | 13:01 | 2024-04-09 | 14:18 | 0.018428 | 0.00023727 | 86 | 6679 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To carry out 11kV Link Box maintenance on TD4-566 - PE0017 | .
5047 |  | JE24011139 | 1095 TAIRUA ROAD WHANGAMATA WHANGAMATA | Eastern | OPOUTERE | 2024-04-09 | 9:05 | 2024-04-09 | 16:53 | 0.013203 | 3.3108e-05 | 12 | 4786 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Reconductor LV between poles 487830 and 248672. Reconductor LV between poles 248672 and R13002. | .
5048 |  | JE24012489 | HIKUAI | Eastern | HIKUAI | 2024-04-09 | 9:42 | 2024-04-09 | 11:20 | 0.00027061 | 2.759e-06 | 1 | 98 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV TAI CB3 Auto-reclosed at 18:59 Protection flags (nil where none): C Ø O/C & E/F CAUSE: ARCing ABS Location: ABS IC1205 (Pole 424780) Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Yes Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: ETA 50min - Fire Coms have been advised. Field Switcher found arcing ABS at IC1205 NOC closed in remotely at Sw/Gear 9770/1 (TAI4) Field Switcher then opened ABS IC1205. Arcing horn is missing, will return during daylight to investigate further. All Part/Flickering Power jobs have cleared. (Confirmed via voice with OCT's on duty) 09/04/24 ABS IC1205, Contacts repaired and arcing horns fitted and tested opearation | .
5049 |  | JE24012496 | AUROA | Western | AUROA | 2024-04-09 | 5:31 | 2024-04-09 | 5:50 | 0.0047967 | 0.00036418 | 132 | 1739 | Unplanned | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV Rec 12139/2 Protection flags (nil where none): E/F, O/C A-B phase CAUSE: Unk Location: Unk Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): NO Circuit patrolled and type: Partially Cursory Patrolled Weather (wind/rain): Calm LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Additional fault restoration comments: After Rec 12139/2 tripped, unbeknown to control, the area which was supposedly off, was still live due to ABS MA 208 still being closed. NOC opened Gas/Sw 6747 as part of sectionalising which created an outage (still unknown to control). FM then opened ABS MA158 as part of sectionalising, and reported power was still on as ABS arced. This alerted NOC to the possibility a back feed was still in place. Power was then fully restored and FM sent to locate and rectify the source of the backfeed. ABS MA208 was found to be closed onsite, this was showing Open on SCADA. | .
5050 |  | JE24012500 | WAITOTARA | Western | WAITOTARA | 2024-04-09 | 7:34 | 2024-04-09 | 11:40 | 0.060526 | 0.00024555 | 89 | 21938 | Unplanned | WILDLIFE - BIRD | REGULATORY INFORMATION Voltage & Device ID: 11kV Recloser 693 Protection flags (nil where none): A, B, C, E/F CAUSE: Bird Strike Location: 2 Sites, Pole 781766, & Pole 840096 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Calm LFI (Y/N + Comments): N/A Follow up Required (select advisory)? N Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
5051 |  | JE24012555 | MT STEWART | Western | MT STEWART | 2024-04-09 | 10:12 | 2024-04-09 | 12:02 | 0.0093875 | 8.5528e-05 | 31 | 3403 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: M56 No. Fuses: 2 Fuse Amp Size: 15 Amp TIME CLOSED: 12:01 Cause: Possible Bird strike Weather (wind/rain): Calm Follow up required (select advisory)? N | .
5052 |  | JE24012646 | GORDON | Eastern | GORDON | 2024-04-09 | 19:21 | 2024-04-09 | 19:51 | 0.000249 | 8.2769e-06 | 3 | 90 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Cause: Customer experiencing High Voltages and Inverter keeps cutting out. Location: Transformer TC350 Loop tests completed: No Voltage readings taken on arrival: Voltage at TX: 251 V (N - Ø) & 435 V (Ø - Ø) Voltage readings taken after Transformer was tapped down from 3 to 2. Voltage at TX: 243 V (N - Ø) & 420 V (Ø - Ø) Have all connections been checked? Yes PQI Ref #: No PQI has been done yet. Additional Info: Full Power restored at 19:50 | .
5053 |  | JE24012648 | DE HAVILLAND SOUTH | Western | DE HAVILLAND SOUTH | 2024-04-09 | 17:48 | 2024-04-09 | 19:09 | 0.0044985 | 0.00012691 | 29 | 1630 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 4 Protection flags (nil where none): O/C E/F CAUSE: 11kV Cable fault Location: Between Sw/Gear 8636/2 to Sw/Gear 966/2 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): 2404004 Circuit patrolled and type: op Weather (wind/rain): calm LFI (Y/N + Comments): n Follow up Required (select advisory)? n Additional fault restoration comments: Cable fault isolated, cable to be repaired under the DNO, Full power restored to feeder, back feed put in place for MCK Metals SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
5054 |  | JE24008609 | 198 PENNY ROAD RONGOTEA PALMERSTON NORTH | Western | RONGOTEA | 2024-04-08 | 9:45 | 2024-04-08 | 15:10 | 0.069893 | 0.0002152 | 78 | 25333 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Clear vegetation between poles P31753-P31751 & P33536-P33532 | .
5055 |  | JE24008616 | 10 MANGAETUROA SOUTH ROAD RAETIHI RAETIHI | Western | RAETIHI | 2024-04-08 | 9:15 | 2024-04-08 | 12:13 | 0.0024509 | 1.3795e-05 | 5 | 888 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Xarms at pole 777208, 777212 & Xarm plus Stay at 777211. | .
5056 |  | JE24008691 | 275 MAKIRIKIRI VALLEY ROAD UPOKONGARO WANGANUI | Western | MAKIRIKIRI | 2024-04-08 | 9:30 | 2024-04-08 | 14:14 | 0.03603 | 0.00012691 | 46 | 13059 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11KV X-Arms at poles 790638, 790629, 790542 & 790540 | .
5057 |  | JE24009562 | 134 FOREMAN ROAD TIKORANGI WAITARA | Western | OTARAOA RD | 2024-04-08 | 9:31 | 2024-04-08 | 11:39 | 0.0038952 | 3.0349e-05 | 11 | 1412 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Red defect arm replacement on pole 760838 | .
5058 |  | JE24009580 | 528 MARATOTO ROAD KOMATA PAEROA | Eastern | BENNETT ST | 2024-04-08 | 8:31 | 2024-04-08 | 13:42 | 0.048032 | 0.0001545 | 56 | 17409 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE SET OF 11KV FUSES FC1401 AT POLE N2414 | .
5059 |  | JE24011813 | 680 OLD TE AROHA ROAD OKAUIA MATAMATA | Eastern | GORDON | 2024-04-08 | 8:31 | 2024-04-08 | 10:38 | 0.038586 | 0.00030349 | 110 | 13986 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE ROTTON HV & LV CROSSARMS AT POLE F0920. RED DEFECT | .
5060 |  | JE24012358 | AUROA | Western | AUROA | 2024-04-08 | 9:47 | 2024-04-08 | 14:42 | 0.0032561 | 1.1036e-05 | 4 | 1180 | Unplanned | THIRD PARTY INTERFERENCE - OVERHEAD CONTACT | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 5 Autoreclosed Protection flags (nil where none): O/C Weather (wind/rain): Calm Follow up required (select advisory): No LFI Activation: No Voltage & Device ID: 11kV Rec 12139 Autoreclosed Protection flags (nil where none): O/C E/F Weather (wind/rain): Calm Follow up required (select advisory): No LFI Activation: Fault was upstream of LFIs Voltage & Device ID: 11kV Rec 12137 Autoreclosed Protection flags (nil where none): O/C E/F Weather (wind/rain): Calm Follow up required (select advisory): No LFI Activation: Fault was upstream of LFIs Voltage & Device ID: 11kV CB 5 Transformer M1040 Protection flags (nil where none): Fuses operated CAUSE: High load contacted LV lines Location: Transformer M1040 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): N//A Circuit patrolled and type: F4, only where damage was done. Weather (wind/rain): Calm LFI (Y/N + Comments): Yes / none activated Follow up Required (select advisory)? No Additional fault restoration comments: Lines brought down by high load being escorted by Downer faultman, The fuses at M1040 operated and 400V lines brought down. 80M 16mm² HD Cu conductor was replaced 2 x HV fuses barrels 3 x 6A HV fuses NDR ND 880235 09/04/24 After Fault on O | .
5061 |  | JE24012431 | 109 OLIVER ROAD, TAURANGA, 3171 | Eastern | WAIROA | 2024-04-08 | 17:27 | 2024-04-08 | 18:27 | 0.0042705 | 7.1733e-05 | 26 | 1548 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Isolation: Sw/Gear 9301/3 & Fuses S6028 CAUSE: Arcing jumper. Location: Pole 213 060 Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Calm Follow up required (select advisory)? No Additional fault restoration comments: Arcing jumper has been repaired at Pole 213 060 Full Power restored at 18:26 | .
5062 |  | JE24012469 | BLACK STUMP | Eastern | BLACK STUMP | 2024-04-08 | 17:14 | 2024-04-08 | 19:35 | 0.10523 | 0.00093805 | 340 | 38139 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | REGULATORY INFORMATION Voltage & Device ID: 11kV PMA CB3 Protection flags (nil where none): A B Ø O/C CAUSE: Suspect Tree branch fell across O/H Lines. Location: Suspect at Transformer TD5-096 (Pole 488828) Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Calm LFI (Y/N + Comments): No Follow up Required (select advisory)? No Additional fault restoration comments: ETA 20-30mins. Fire Coms have been advised. Field Switchers are busy carrying out a Line Patrol. No fault found & no HV O/H Lines were found on the ground. Suspect tree branch came down across the O/H Lines and this caused the feeder to trip and started the fire at the base of the Pole 488828. Full Power restored at 19:34 | .
5063 |  | JE24008659 | 56 NGATI MARU HIGHWAY KOPU THAMES | Eastern | TOTARA | 2024-04-07 | 9:02 | 2024-04-07 | 14:33 | 0.030981 | 9.3805e-05 | 34 | 11229 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles 874656, SO536 & S0516 | .
5064 |  | JE24012317 | BRISTOL RD | Western | BRISTOL RD | 2024-04-07 | 20:15 | 2024-04-07 | 21:40 | 0.00023389 | 2.759e-06 | 1 | 85 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 6744 No. Fuses: 2 Fuse Amp Size: 6Amp TIME CLOSED: 21:40 hrs Cause: Suspect Bird Strike Weather (wind/rain): Calm Follow up required (select advisory)? | .
5065 |  | JE24012318 | HUNTERVILLE 22KV | Western | HUNTERVILLE 22KV | 2024-04-07 | 18:17 | 2024-04-07 | 21:08 | 0.011352 | 6.6215e-05 | 24 | 4115 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 997 No. Fuses: 2 Fuse Amp Size: 10Amp TIME CLOSED: 21:08hrs Cause: Unk Weather (wind/rain): Calm Follow up required (select advisory)? | .
5066 |  | JE24009911 | 26 RIVERVIEW STREET PUTARURU PUTARURU | Eastern | OVERDALE RD | 2024-04-06 | 9:03 | 2024-04-06 | 12:34 | 0.030298 | 0.00014347 | 52 | 10982 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | AT POLE 873352 REPLACE 11KV PIN ARMS FOR TERM ARMS - RECONFIGURE 11KV JUMPERS TO ELIMINATE PHASE TO PHASE BIRD STRIKE | .
5067 |  | JE24012219 | WAITOTARA | Western | WAITOTARA | 2024-04-06 | 0:06 | 2024-04-06 | 7:35 | 0.15372 | 0.00034211 | 124 | 55715 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: REC 2754 Protection flags (nil where none): E/F, O/C 3 phase CAUSE: Car v Pole Location: Pole 774601 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Calm LFI (Y/N + Comments): N Follow up Required (select advisory)? Additional fault restoration comments: Police event number P058339786 SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
5068 |  | JE24012221 | BROOKLANDS 7 | Western | BROOKLANDS 7 | 2024-04-06 | 0:16 | 2024-04-06 | 3:58 | 0.097703 | 0.0024555 | 890 | 35413 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: CB 7 / REC 12353 Protection flags (nil where none): EF CAUSE: Car V Pole causing line down Location: Pole 478921 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: cursory Weather (wind/rain): fine LFI (Y/N + Comments): Yes, correctly operated Follow up Required (select advisory)? CB 7 also tripped, possible protection review? NDR to follow Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
5069 |  | JE24012224 | LINTON EXPRESSWAY | Western | LINTON EXPRESSWAY | 2024-04-06 | 1:52 | 2024-04-06 | 8:46 | 0.19526 | 0.00059594 | 216 | 70772 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | REGULATORY INFORMATION Voltage & Device ID: CB 6 / Linton Army Camp CB 4 Protection flags (nil where none): EF CAUSE: Blown Pothead Location: Pole P02949 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): 2404001 Circuit patrolled and type: Weather (wind/rain): Calm LFI (Y/N + Comments): N/A Follow up Required (select advisory)? Work to continue under DNO. Additional fault restoration comments: Faulted pothead has been isolated away from main line HV and the two transformers supplied have been LV backfed SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
5070 |  | JE24012245 | CLOTON RD INDUSTRIAL | Western | CLOTON RD INDUSTRIAL | 2024-04-06 | 8:46 | 2024-04-06 | 13:07 | 0.0021583 | 8.2769e-06 | 3 | 782 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: 3290T - two fuses found blown CAUSE: Faulty Transformer Temp generation (stage details when used): PERFORMANCE DETAIL DNO (number or state no): Circuit patrolled & type: Weather (wind/rain): Calm Follow up required (select advisory)? No Additional fault restoration comments:Replaced 15/11/3phase Transformer | .
5071 |  | JE24012253 | WAITARA RD | Western | WAITARA RD | 2024-04-06 | 11:51 | 2024-04-06 | 13:43 | 0.00092405 | 8.2769e-06 | 3 | 335 | Unplanned | WILDLIFE - BIRD | Fuses Location: 1342 No. Fuses: 2 Fuse Amp Size: 3A TIME CLOSED: 13:42hrs Cause: Magpie Weather (wind/rain): Calm Follow up required (select advisory)? | .
5072 |  | JE24012256 | BOWENTOWN | Eastern | BOWENTOWN | 2024-04-06 | 12:37 | 2024-04-06 | 18:31 | 0.0027899 | 8.2769e-06 | 3 | 1011 | Unplanned | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Fuses Location: SA2-022 No. Fuses: 1 Fuse Amp Size: TIME CLOSED: Cause: Suspect Cable Fault Weather (wind/rain): Follow up required (select advisory)? No Tried to Reload & Liven Fused ABS SA2-022 & they blew back. Suspect Cable might be faulty, will have to carry out testing first. Busy arranging Generators. Testing carried out on HV Cable indicates Cable between TA2-088 towards TA2-087 is faulty. (A Ø to Earth) TLB at TX TA2-088 (towards TA2-087 side) Fused ABS SA2-022 closed to energize Transformer TA2-088 LV line break made at Transformer TA2-087 and generator installed Power restored 18:30 15/04/2024 Job repaired and completed under NAPA 110 135 | .
5073 |  | JE24012257 | HOLDSWORTH | Western | HOLDSWORTH | 2024-04-06 | 14:10 | 2024-04-06 | 16:59 | 0.00046429 | 2.759e-06 | 1 | 168 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Isolation: Transformer T615 Fuses Location: Pole 826 763 CAUSE: Transformer leaking oil. (Tank ruptured) Temp generation (stage details when used): No PERFORMANCE DETAIL DNO (number or state no): No Circuit patrolled & type: Yes Weather (wind/rain): Clear Follow up required (select advisory)? No Additional fault restoration comments: Transformer T615 leaking oil and will be replaced under Access Permit. Busy with Isolation & Earthing at Transformer T615 Fuses How much oil has spilled/leaked out from the TX tank? Answer: Small amount as per Field Switcher. Full Power restored at 16:58 | .
5074 |  | JE24012260 | TOKO | Western | TOKO | 2024-04-06 | 13:50 | 2024-04-06 | 16:47 | 0.0019578 | 1.1036e-05 | 4 | 710 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: 4484T No. Fuses: 1 Fuse Amp Size: 6A TIME CLOSED: 16:47hrs Cause: Faulty Lightning Arrestor Weather (wind/rain): Calm Follow up required (select advisory)? NOTE: Replaced 3x Lightning Arrestors & 3x Jumpers - see SIS | .
5075 |  | JE24012266 | 277 NGATIRA ROAD, LICHFIELD, PUTARURU, 3482 | Eastern | LICHFIELD | 2024-04-06 | 16:14 | 2024-04-06 | 17:05 | 0.00084921 | 1.6554e-05 | 6 | 308 | Unplanned | VEGETATION - INSIDE ZONE | Isolation: Fuses FC2244 Cause: Trees within zone. What was replaced? Safety Disconnection for LV Service Lines Where was it replaced (pole/TX/pillar box)? Pole B12573 (TC3998) Is 2R required? No 2R Y - What is the timeframe for repairs? N/A Additional Info: Trees brought down LV Service Lines. HV Isolation to create a safety panel at Fuses 2244 Busy with repairs at the moment. HV Power restored at 17:05 LV Safety Disconnection at Pole B12573 Tag no: A37398 PRIVATE LINES - Contractor to carry out repairs. | .
5076 |  | JE24008586 | 935 POHANGINA ROAD POHANGINA ASHHURST | Western | POHANGINA | 2024-04-05 | 10:41 | 2024-04-05 | 11:54 | 0.019993 | 0.0002759 | 100 | 7247 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Perform ABS Maintenance at F57 and Recloser maintenance at F55 | .
5077 |  | JE24008591 | 109 PARKERS ROAD WEST TARATAHI CARTERTON | Western | CHESTER RD | 2024-04-05 | 9:02 | 2024-04-05 | 12:05 | 0.011655 | 6.3456e-05 | 23 | 4224 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace pole 821921 | .
5078 |  | JE24008593 | 2096 RIDGE ROAD POHANGINA FEILDING | Western | APITI | 2024-04-05 | 9:35 | 2024-04-05 | 10:36 | 0.0037228 | 6.0697e-05 | 22 | 1349 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | rebind 11Kv O/H wires on poles P12070, P12071 | .
5079 |  | JE24008597 | 1273 ANNEDALE ROAD TINUI TINUI | Western | ANNEDALE | 2024-04-05 | 9:26 | 2024-04-05 | 15:34 | 0.043581 | 0.00011864 | 43 | 15796 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT- Vegetation tree cutting around lines, site 1 pole 462311, site 2 pole 838459 to852019 | .
5080 |  | JE24009334 | White Rock Rd White Rock. | Western | TUTURUMURI | 2024-04-05 | 8:46 | 2024-04-05 | 14:42 | 0.017701 | 4.9661e-05 | 18 | 6416 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | to move 11kv poles 361744 & 7FCF376 and replace pole 811703 and turn pole 7FCFE67. | .
5081 |  | JE24009384 | 1 GILBERT ROAD (PUKEARUHE ROAD) WAIITI URENUI | Western | MAIN RD MOTONUI | 2024-04-05 | 9:31 | 2024-04-05 | 10:42 | 0.00649 | 9.1046e-05 | 33 | 2352 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace rotten hv Dead ends on pole 847947 | .
5082 |  | JE24009385 | 400 SOUTH ROAD HAWERA HAWERA | Western | KETEMARAE RD | 2024-04-05 | 9:00 | 2024-04-05 | 13:30 | 0.11616 | 0.0004304 | 156 | 42104 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace ABS 4657 and pole structure 721452 | .
5083 |  | JE24009421 | 207 FREESIA PLACE HAIRINI TAURANGA | Eastern | POIKE | 2024-04-05 | 8:40 | 2024-04-05 | 9:21 | 0.01046 | 0.00025658 | 93 | 3791 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To carry out 11kV Link Box maintenance on TD4-704 and SD4-492 - PE0017 | .
5084 |  | JE24012096 | TUTAENUI | Western | TUTAENUI | 2024-04-05 | 7:06 | 2024-04-05 | 10:07 | 0.00049979 | 2.759e-06 | 1 | 181 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 1177 No. Fuses: 3 Fuse Amp Size: 6A TIME CLOSED: 10:06 Cause: Unknown Weather (wind/rain): Calm Follow up required (select advisory)? No | .
5085 |  | JE24012123 | POHANGINA | Western | POHANGINA | 2024-04-05 | 9:42 | 2024-04-05 | 12:04 | 0.0015601 | 1.1036e-05 | 4 | 565 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Transformer T4/156 No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 12:03 Cause: Lightning Weather (wind/rain): Rain Follow up required (select advisory)? No | .
5086 |  | JE24012127 | APITI | Western | APITI | 2024-04-05 | 9:51 | 2024-04-05 | 10:39 | 0.00026793 | 5.5179e-06 | 2 | 97 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Transformer T4/329 No. Fuses: 3 Fuse Amp Size: 2A TIME CLOSED: 10:39 Cause: Lightning Weather (wind/rain): Calm Follow up required (select advisory)? No | .
5087 |  | JE24012132 | OPOUTERE | Eastern | OPOUTERE | 2024-04-05 | 10:28 | 2024-04-05 | 13:05 | 0.00086843 | 5.5179e-06 | 2 | 315 | Unplanned | WILDLIFE - BIRD | Fuses Location: FC900 No. Fuses: 2 Fuse Amp Size: 6A TIME CLOSED: 13:05 Cause: Bird strike Weather (wind/rain): wind Follow up required (select advisory)? No | .
5088 |  | JE24012146 | POHANGINA | Western | POHANGINA | 2024-04-05 | 11:32 | 2024-04-05 | 14:27 | 0.00096897 | 5.5179e-06 | 2 | 351 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: Transformer T4/326 No. Fuses: 3 Fuse Amp Size: 2A TIME CLOSED: 14:27 Cause: Lightning Weather (wind/rain): Calm Follow up required (select advisory)?No | .
5089 |  | JE24012168 | YOUNG RD | Eastern | YOUNG RD | 2024-04-05 | 15:06 | 2024-04-05 | 20:30 | 0.0026872 | 8.2769e-06 | 3 | 974 | Unplanned | THIRD PARTY INTERFERENCE - DIG IN | Cable hit by directional Drill FM checked operator ok Isolated at Fuses SE6-224 Cable has been repaired and full power restored. Confirmed by Controller Russel B. | .
5090 |  | JE24012194 | OTAMARAKAU | Eastern | OTAMARAKAU | 2024-04-05 | 16:52 | 2024-04-05 | 17:27 | 0.0012386 | 3.5867e-05 | 13 | 449 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Twisted Crossarm confirmed at Pole 227389 Isolated at FABS SE8-007 Cross arm re fixed | .
5091 |  | JE24012717 | JUNCTION RD | Western | JUNCTION RD | 2024-04-05 | 10:00 | 2024-04-05 | 12:05 | 0.012779 | 0.00010208 | 37 | 4632 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace crossarm at pole 747076. Advertised 03/04 at 16:10 - outage is planned | .
5092 |  | JE24008248 | 309 WEST BUSH ROAD UPPER PLAIN MASTERTON | Western | MOUNT BRUCE | 2024-04-04 | 8:45 | 2024-04-04 | 14:51 | 0.0010102 | 2.759e-06 | 1 | 366 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Clearing vegetation under access permit between poles 832836 and 832838 | .
5093 |  | JE24008256 | 1005 TAONUI ROAD COLYTON FEILDING | Western | POHANGINA | 2024-04-04 | 10:01 | 2024-04-04 | 11:12 | 0.022809 | 0.00032556 | 118 | 8267 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Perform ABS Maintenance at E35 & Recloser maintenance at E33 | .
5094 |  | JE24008420 | 2551 STATE HIGHWAY 1 HUNTERVILLE MARTON | Western | PUTORINO | 2024-04-04 | 9:16 | 2024-04-04 | 15:21 | 0.012083 | 3.3108e-05 | 12 | 4380 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace Red Tagged 11KV poles 805540 & 805541 | .
5095 |  | JE24008422 | 693 otaranoho Rd, Raetihi | Western | RAETIHI | 2024-04-04 | 11:00 | 2024-04-04 | 15:08 | 0.055497 | 0.00022348 | 81 | 20115 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 3x poles 777897, 777901, 777879 & repair 1 binder 777896. | .
5096 |  | JE24008557 | 2 PLUNKET STREET DURIE HILL WANGANUI | Western | BASTIA HILL | 2024-04-04 | 9:16 | 2024-04-04 | 14:46 | 0.17496 | 0.00056007 | 203 | 63414 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace DNO switch 783, replace kidney strains on pole 767929 | .
5097 |  | JE24008577 | PASCAL ST 9 | Western | PASCAL ST 9 | 2024-04-04 | 9:31 | 2024-04-04 | 13:50 | 0.029326 | 0.00011312 | 41 | 10629 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Asplundh to cut trees between poles P45045/P45046 and P45047. | .
5098 |  | JE24008579 | 63 WILSON STREET WHANGANUI WANGANUI | Western | GUYTON ST | 2024-04-04 | 6:00 | 2024-04-04 | 22:49 | 0.002006 | 0.00011588 | 22 | 727 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv cable that supplies transformer X182 | .
5099 |  | JE24008582 | 293 NO 1 LINE POHANGINA POHANGINA ASHHURST | Western | POHANGINA | 2024-04-04 | 10:16 | 2024-04-05 | 13:35 | 0.005021 | 1.6554e-05 | 3 | 1820 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT - Replace pole, clear vegetation and repair sags between and including poles P14146 & P14033 | .
5100 |  | JE24008587 | 1963 ANNEDALE ROAD TINUI TINUI | Western | ANNEDALE | 2024-04-04 | 9:46 | 2024-04-04 | 14:36 | 0.00080015 | 2.759e-06 | 1 | 290 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv poles past fuses 8192. Poles to be replaced are 837706, 837710 and 837715 | .
5101 |  | JE24009131 | 1751 SOUTH ROAD MANUTAHI PATEA | Western | MANUTAHI | 2024-04-04 | 8:55 | 2024-04-04 | 9:12 | 0.00051441 | 3.0349e-05 | 11 | 186 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | resag hv lines at pole 728071 | .
5102 |  | JE24009178 | 358 East Road, Stratford | Western | CLOTON RD SOUTH | 2024-04-04 | 9:37 | 2024-04-04 | 13:02 | 0.0039565 | 1.9313e-05 | 7 | 1434 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace insulators at ABS 5760 Replace TX structure 3191T pole 740516 | .
5103 |  | JE24009182 | 425 OMANAWA ROAD OMANAWA TAURANGA | Eastern | KEENAN RD | 2024-04-04 | 9:01 | 2024-04-04 | 15:24 | 0.0084619 | 2.2072e-05 | 8 | 3067 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV Transformer crossarm at Pole 211857 (TE3-096). | .
5104 |  | JE24009274 | 43 MILL ROAD LOWER VOGELTOWN NEW PLYMOUTH | Western | BROOKLANDS 8 | 2024-04-04 | 9:35 | 2024-04-04 | 14:21 | 0.18973 | 0.00066491 | 241 | 68769 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | NDR pole 753598 replacement damaged in car accident | .
5105 |  | JE24009300 | 750 STANLEY ROAD TE POPO STRATFORD | Western | CLOTON RD NORTH | 2024-04-04 | 9:46 | 2024-04-04 | 11:07 | 0.027068 | 0.00033108 | 120 | 9811 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | repair loose stay dead ends on pole 758340 | .
5106 |  | JE24009309 | 320 MAKINO ROAD HURLEYVILLE PATEA | Western | KAKARAMEA | 2024-04-04 | 11:01 | 2024-04-04 | 11:45 | 0.0013414 | 3.0349e-05 | 11 | 486 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | resag hv conductors at pole 728959 | .
5107 |  | JE24009331 | 250 INGAHAPE ROAD MANUTAHI HAWERA | Western | WHAKAMARA | 2024-04-04 | 13:33 | 2024-04-04 | 14:27 | 0.0026561 | 4.9661e-05 | 18 | 963 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | resag HV conductors at pole 729811 | .
5108 |  | JE24009397 | 30 RANGINUI ROAD WELCOME BAY TAURANGA | Eastern | WELCOME BAY | 2024-04-04 | 12:41 | 2024-04-04 | 13:11 | 0.0055856 | 0.00018485 | 67 | 2025 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To carry out 11kV Link Box maintenance on SD4-174 - PE0017 | .
5109 |  | JE24009403 | 12 ARAWATA AVENUE WELCOME BAY TAURANGA | Eastern | WELCOME BAY | 2024-04-04 | 8:31 | 2024-04-04 | 9:55 | 0.021414 | 0.00025382 | 92 | 7762 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To carry out 11kV Link Box maintenance on TD4-541 and SD4-156 - PE0017 | .
5110 |  | JE24010012 | 3357 WESTERN LAKE ROAD OCEAN BEACH FEATHERSTON | Western | PIRINOA | 2024-04-04 | 9:02 | 2024-04-04 | 13:31 | 0.04385 | 0.00016278 | 59 | 15894 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Reconductor sections of line from ABS S571 to end of line. | .
5111 |  | JE24010346 | 153 OMAHINE ROAD TE POI MATAMATA | Eastern | TE POI | 2024-04-04 | 10:17 | 2024-04-04 | 12:36 | 0.0026742 | 1.9313e-05 | 7 | 969 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | RED DEFECT--AT POLE F13059 REPLACE 11KV TERM ARMS - DDO ARM AND FUSING. AT POLE F13060 REPLACE OLD 8M WITH NEW 9M BUSCK (ROAD XING POLE) | .
5112 |  | JE24011933 | DYERVILLE | Western | DYERVILLE | 2024-04-04 | 9:15 | 2024-04-04 | 10:09 | 0.0042979 | 8.001e-05 | 29 | 1558 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | Blown Jumper found at Links 7330 Isolated at Fuses7330 Jumper repaired | .
5113 |  | JE24011956 | MOUNT BRUCE | Western | MOUNT BRUCE | 2024-04-04 | 9:23 | 2024-04-04 | 10:57 | 0.00078258 | 8.2769e-06 | 3 | 284 | Unplanned | WILDLIFE - BIRD | Fuses Location: 7712 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 1057 Cause: bird Weather (wind/rain): Clear & calm Follow up required (select advisory)? n | .
5114 |  | JE24012001 | CASTLEPOINT | Western | CASTLEPOINT | 2024-04-04 | 11:20 | 2024-04-04 | 16:32 | 0.19023 | 0.0017326 | 315 | 68949 | Unplanned | DEFECTIVE EQUIPMENT - JUMPER FAILURE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB C937 A/R, Recloser C225 Protection flags (nil where none): B, C Ph E/F CAUSE: Unknown Location: ??? Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Light Rain LFI (Y/N + Comments): N at Pole 838611 Follow up Required (select advisory)? N Additional fault restoration comments: No Fault found FM found blown jumper after closing job. Second job raised for repairs Isolated at ABS S167 Jumper repaired at Pole 838625 | .
5115 |  | JE24012005 | KOPANE | Western | KOPANE | 2024-04-04 | 14:10 | 2024-04-04 | 14:45 | 0.00028735 | 8.2769e-06 | 3 | 104 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Voltage found to be higher than transformers T1/340 & 7607P Transformer T1/69 isolated and Tapped down Off 14:10 on 14:45 Voltage before 249V to N, After 239V to N Now on Tap 3 | .
5116 |  | JE24012006 | BURETA RD | Eastern | BURETA RD | 2024-04-04 | 15:14 | 2024-04-04 | 15:26 | 0.0040383 | 0.00032832 | 119 | 1464 | Unplanned | WILDLIFE - BIRD | After performing various checks suspected a phase down at TC4-013 L2 Isolation at Fuses SC4-446 performed to safely check link box Confirmed 1 fuse (yellow phase blown) power restored when FC4-446 restored Power off via SC4-446 15:13 restored with full power (Including past TC4-013 L2) restored 15:26. While waiting for colleague to bring fuses for TC4-013 L2 before taking power off faultman found dead bird in grass, bird strike therefore confirmed not suspected. | .
5117 |  | JE24012011 | CHAPEL ST | Eastern | CHAPEL ST | 2024-04-04 | 11:48 | 2024-04-04 | 14:18 | 0.027571 | 0.00049937 | 181 | 9993 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 6 Protection flags (nil where none): E/F CAUSE: Truck Vs Pole, Line down Location: Pole 268 778 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Cursory Weather (wind/rain): Fine LFI (Y/N + Comments): Nil Follow up Required (select advisory)? No Additional fault restoration comments: Poe has been hit at least 2x and is in road shipping lane where drivers use large trucks to move shipping containers across the port of TGA. Would be worth under grounding the 5 spans of overhead or placing a protective bollard around the pole to stop future incidents | .
5118 |  | JE24012061 | HORAHORA | Eastern | HORAHORA | 2024-04-04 | 19:05 | 2024-04-04 | 21:09 | 0.0006845 | 5.5179e-06 | 2 | 248 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC5374 failed D/Out burnt end off crossarm, 3 x New D/Outs Fitted & Arm Replaced @ TC5374. Isolation from Fuses FP1008 | .
5119 |  | JE24012073 | BUNNYTHORPE-KELVIN GV 33KV | Western | BUNNYTHORPE-KELVIN GV 33KV | 2024-04-04 | 19:13 | 2024-04-05 | 9:56 | 0.00487 | 5.5179e-06 | 2 | 1765 | Unplanned | UNKNOWN - OPERATIONAL PATROLLED - CAUSE UNKNOWN | Rec 10060 Trip, O/C, E/F, B Phase Faultman will return in morning as can not patrol the line past half way as the fog is to thick and down to ground level with visibility down to zero. Patrolled in daylight. No fault found. Suspect Lightning Strike as lightning was in the area at the time | .
5120 |  | JE24012075 | HUNTERVILLE 22KV | Western | HUNTERVILLE 22KV | 2024-04-04 | 20:36 | 2024-04-04 | 22:59 | 0.0066789 | 4.6902e-05 | 17 | 2421 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: 092 No. Fuses: 2 Fuse Amp Size: 15 TIME CLOSED: 22:58 Cause: Suspect Bird Strike Weather (wind/rain): wind Follow up required (select advisory)?n | .
5121 |  | JE24012079 | POHANGINA | Western | POHANGINA | 2024-04-04 | 21:32 | 2024-04-04 | 22:44 | 0.00079962 | 1.1036e-05 | 4 | 290 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T4/80 No. Fuses: 3 Fuse Amp Size: 3 TIME CLOSED: 22:44 Cause: Lightning Weather (wind/rain): rain Follow up required (select advisory)?n | .
5122 |  | JE24012084 | POHANGINA | Western | POHANGINA | 2024-04-04 | 22:12 | 2024-04-04 | 23:18 | 0.00072161 | 1.1036e-05 | 4 | 262 | Unplanned | LIGHTNING - LIGHTNING STRIKE | Fuses Location: T4/84 No. Fuses: 2 Fuse Amp Size: 3 TIME CLOSED: 23:17 Cause: Lightning Weather (wind/rain): rain Follow up required (select advisory)?n | .
5123 |  | JE24008166 | 812 TE WHARAU ROAD KOURARAU HILL MASTERTON | Western | WERAITI | 2024-04-03 | 9:21 | 2024-04-03 | 14:50 | 0.012735 | 3.8625e-05 | 14 | 4616 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT- Vegetation tree cutting between poles 829122 to 829124 | .
5124 |  | JE24008177 | 853 ADMIRAL ROAD ADMIRAL HILL MASTERTON | Western | LONGBUSH | 2024-04-03 | 9:30 | 2024-04-03 | 16:00 | 0.001076 | 2.759e-06 | 1 | 390 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Create line break live line then replace pole 823402 and 823403 Re instate line break | .
5125 |  | JE24008189 | 150 POHANGINA ROAD ASHHURST PALMERSTON NORTH | Western | POHANGINA | 2024-04-03 | 9:30 | 2024-04-03 | 10:28 | 0.026061 | 0.00045799 | 166 | 9446 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Perform ABS maintenance at 10303-1 & Recloser maintenance at 10303-2 | .
5126 |  | JE24008194 | 458 MAKOPUA ROAD TAOROA JUNCTION TAIHAPE | Western | MANGAWEKA | 2024-04-03 | 9:35 | 2024-04-03 | 11:59 | 0.0023771 | 1.6554e-05 | 6 | 862 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT - Re-sag out of tolerance span between poles 796055-796057 | .
5127 |  | JE24008380 | 2411 COAST ROAD PONGAROA PONGAROA | Western | COAST ROAD | 2024-04-03 | 9:48 | 2024-04-03 | 12:27 | 0.05351 | 0.00033659 | 122 | 19395 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace two spans of rusty #8 conductor between poles P04629 & P26877 | .
5128 |  | JE24008584 | 2km past 1534 Masterton Strongvar Rd, Masterton | Western | WERAITI | 2024-04-03 | 9:00 | 2024-04-03 | 12:08 | 0.00051873 | 2.759e-06 | 1 | 188 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace xarm at pole 827488 and re sag 11kv lines at pole 827489 and 827492. | .
5129 |  | JE24008744 | 34 GLOUCESTER ROAD MOUNT MAUNGANUI TAURANGA | Eastern | EVERSHAM RD | 2024-04-03 | 8:30 | 2024-04-03 | 13:10 | 0.099648 | 0.00035591 | 129 | 36118 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Install generator to service pillar 173904 (TD5-114). Replace rusted out SDAF (9206/4) base unit and repair SDAF3 base unit (9206/1). Remove generator & connect service at pillar 173904 | .
5130 |  | JE24009055 | 227 QUEEN STREET MASTERTON MASTERTON | Western | COLOMBO RD | 2024-04-03 | 6:26 | 2024-04-05 | 23:50 | 0.023983 | 0.0004304 | 78 | 8693 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace RMU kuripuni C1020-C1023 | .
5131 |  | JE24009058 | 55 WILLS ROAD BELL BLOCK NEW PLYMOUTH | Western | MANGATI RD | 2024-04-03 | 9:48 | 2024-04-03 | 14:41 | 0.029908 | 0.00010208 | 37 | 10840 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Shut 2: Raise tx 2279N and extend all LV cables to suit. Install and connect new HV cable between FSU 8580/4 and Tx 2279N. Shut 2 can only be started after completion of Shut 1. Shut 1 on NAPA 108871. No HV Outage associated - LV Only | .
5132 |  | JE24009065 | 19 OTOIA ROAD KAKARAMEA PATEA | Western | KAKARAMEA | 2024-04-03 | 9:30 | 2024-04-03 | 9:51 | 0.0024037 | 0.00011312 | 41 | 871 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | resag HV lines at pole 728625 | .
5133 |  | JE24009091 | 6006 SOUTH ROAD RAHOTU OPUNAKE | Western | PUNGAREHU | 2024-04-03 | 10:01 | 2024-04-03 | 11:23 | 0.012713 | 0.00016554 | 60 | 4608 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | to repair 11kv jumbers and deadends on abs 6263 | .
5134 |  | JE24009102 | 268 WILSON ROAD PATEA PATEA | Western | KAKARAMEA | 2024-04-03 | 12:01 | 2024-04-03 | 13:09 | 0.0011406 | 1.6554e-05 | 6 | 413 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | resag hv conductors at pole 726972 | .
5135 |  | JE24009444 | 2 TEBBUTT ROAD WAIROA TAURANGA | Eastern | KAIMAI DRIVE | 2024-04-03 | 9:18 | 2024-04-03 | 15:02 | 0.068305 | 0.00019865 | 72 | 24758 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | NAPA # 108631: Replace 11kv/400vt poles 217770,217771 & 217774. Replace 11kv overhead conductors between poles 422981& 217771. Isolation points @ 14335/4 Issuer earths @ pole 422981 (480857 side) & 13725/4 issuer earths @ pole 422981 ( 481979 side). | .
5136 |  | JE24009563 | 32 FLEMINGTON ROAD ARAMOHO WANGANUI | Western | MAKIRIKIRI | 2024-04-03 | 10:00 | 2024-04-03 | 12:32 | 0.0041881 | 2.759e-05 | 10 | 1518 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace TX X2618 due to faulty Low Voltage Bushings | .
5137 |  | JE24010200 | 81 HAURAKI ROAD ORONGO THAMES | Eastern | HAURAKI RD | 2024-04-03 | 8:48 | 2024-04-03 | 15:19 | 0.057304 | 0.00075044 | 161 | 20770 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace poles O1342, O1354, O1356 & O1363 | .
5138 |  | JE24010395 | 3357 WESTERN LAKE ROAD OCEAN BEACH FEATHERSTON | Western | PIRINOA | 2024-04-03 | 10:15 | 2024-04-03 | 15:36 | 0.05216 | 0.00016278 | 59 | 18906 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Reconductor from S571 to end of line 11kv cable repairs to faulty cables found during previous shutdowns as discussed with Gavin Paget Cable term @ 7003 , cable term & through joint at S1205 . | .
5139 |  | JE24010446 | 2 MAUNGAWHARE PLACE OTUMOETAI TAURANGA | Eastern | CHERRYWOOD DRIVE | 2024-04-03 | 9:21 | 2024-04-03 | 13:58 | 0.072711 | 0.0002621 | 95 | 26355 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | replace leaking transformer 200kva TD4-085 | .
5140 |  | JE24010911 | 348 KAUAERANGA VALLEY ROAD THAMES THAMES | Eastern | TOTARA | 2024-04-03 | 9:45 | 2024-04-03 | 10:26 | 0.00022357 | 5.5179e-06 | 2 | 81 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Red Defect - Je24009266 - Replace HV pin insulator at pole 383548 | .
5141 |  | JE24011817 | KUAOTUNU | Eastern | KUAOTUNU | 2024-04-03 | 12:34 | 2024-04-03 | 16:06 | 0.038022 | 0.00017933 | 65 | 13781 | Unplanned | THIRD PARTY INTERFERENCE - DIG IN | Cause: Contractor dug up 400V cable Fault blew 10A HV Fuse also What was replaced? 400v Cable Repaired Where was it replaced (pole/TX/pillar box)? Cable Repaired & 10A HV Fuse Replaced x 3 Is 2R required? Y/N , Yes 2R Y - What is the timeframe for repairs? Additional Info: | .
5142 |  | JE24011854 | BLAIRLOGIE | Western | BLAIRLOGIE | 2024-04-03 | 12:29 | 2024-04-03 | 15:11 | 0.00044931 | 2.759e-06 | 1 | 163 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 8164 No. Fuses: 2 Fuse Amp Size: 10A TIME CLOSED: 1511 Cause: suspect bird Weather (wind/rain): fine Follow up required (select advisory)? | .
5143 |  | JE24011858 | BENNETT ST | Eastern | BENNETT ST | 2024-04-03 | 12:34 | 2024-04-03 | 14:48 | 0.0036925 | 2.759e-05 | 10 | 1338 | Unplanned | WILDLIFE - BIRD | Fuses Location: fc4069 No. Fuses: 2 Fuse Amp Size: 6 TIME CLOSED: 14:47 Cause: Swampy hit lines Pukeko Weather (wind/rain): fine Follow up required (select advisory)? | .
5144 |  | JE24011870 | RONGOTEA | Western | RONGOTEA | 2024-04-03 | 13:36 | 2024-04-03 | 17:25 | 0.00063161 | 2.759e-06 | 1 | 229 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Fuses Location: Fuses 047 No. Fuses: 2A Fuse Amp Size: 3 TIME CLOSED: 1725 Cause: unknown Weather (wind/rain): fine Follow up required (select advisory)? | .
5145 |  | JE24011889 | BURNSIDE | Western | BURNSIDE | 2024-04-03 | 15:33 | 2024-04-03 | 19:54 | 0.18231 | 0.0016719 | 606 | 66079 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: CB C928 Protection flags (nil where none): A & C phase fault CAUSE: trailer come of vehicle and taken out pole Location: Pole797701 Temp generation (state details when used): N PERFORMANCE DETAIL DNO (number or state No): N Circuit patrolled and type: N Weather (wind/rain): fine LFI (Y/N + Comments): LFI's are out of comms and so no use for fault finding Follow up Required (select advisory)? Additional fault restoration comments: SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): Pole 797701 replaced | .
5146 |  | JE24011920 | BUCKLAND RD | Eastern | BUCKLAND RD | 2024-04-03 | 20:45 | 2024-04-03 | 21:52 | 0.0003732 | 5.5179e-06 | 2 | 135 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | Sw/Gear 13614 (LAK 4) has been hit by a vehicle and damaged. Pls can a faultman check for safety Straightened switchgear. Inspected inside and no physical damage to terminations and switches. Switchgear can be energized Leave 2R Open for further repairs on switchgear. To be completed 11/07/24 Cover repaired/ Replaced | .
5147 |  | JE24011921 | HOLDSWORTH | Western | HOLDSWORTH | 2024-04-03 | 19:27 | 2024-04-03 | 20:59 | 0.00025406 | 2.759e-06 | 1 | 92 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses Location: Transformer T615 No. Fuses: 2 Fuse Amp Size: 2A TIME CLOSED: 20:58 Cause: DETERIORATION Weather (wind/rain): Cool Follow up required (select advisory)? No Transformer structure penciled for upgrade on the 12th of April | .
5148 |  | JE24005487 | 406 RUAKIWI ROAD KOURARAU HILL MASTERTON | Western | WESTMERE GLADSTONE | 2024-04-02 | 9:00 | 2024-04-02 | 15:45 | 0.013407 | 3.3108e-05 | 12 | 4859 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | FFT-vegetation tree cutting between poles site 1 pole 829623 to 829626, site 2 pole 829660 to 829663 | .
5149 |  | JE24008215 | 493 STATE HIGHWAY 4 UPOKONGARO WANGANUI | Western | MAKIRIKIRI | 2024-04-02 | 9:47 | 2024-04-02 | 14:11 | 0.048361 | 0.00040557 | 147 | 17529 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace loose king bolt pole 388042. Repair badly damaged line at pole 443493 and trim tree with contractor. | .
5150 |  | JE24008404 | 584 RICHMOND ROAD LEPPERTON NEW PLYMOUTH | Western | LEPPERTON | 2024-04-02 | 9:30 | 2024-04-02 | 15:00 | 0.0018208 | 5.5179e-06 | 2 | 660 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Shut 9 Isolate Hv line to rewire Lv conductor underbuilt | .
5151 |  | JE24008589 | 9455 PAEROA KOPU ROAD MATATOKI THAMES | Eastern | KOPU | 2024-04-02 | 9:32 | 2024-04-02 | 14:32 | 0.019041 | 6.3456e-05 | 23 | 6902 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kV pole S12452 and LV cross arms on poles S0562, S0571, S12456 & S0586. | .
5152 |  | JE24008732 | 55 WILLS ROAD BELL BLOCK NEW PLYMOUTH | Western | MANGATI RD | 2024-04-02 | 9:45 | 2024-04-02 | 15:04 | 0.075519 | 0.00023727 | 86 | 27372 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Shut 1: Replace extendable SD fuse unit 8580/4. After completion leave FSU 8580/4 isolated and earthed for shut 2. Shut 2 follows on NAPA 108872. | .
5153 |  | JE24009086 | 846 OROPI ROAD OROPI TAURANGA | Eastern | WAIMAPU | 2024-04-02 | 10:46 | 2024-04-02 | 13:02 | 0.0018747 | 1.3795e-05 | 5 | 679 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To carry out 11kV Link Box maintenance on SE4-043 and SE4-059 - PE0017 | .
5154 |  | JE24009099 | 3 WILLOUGHBY ROAD KATIKATI | Eastern | LINDERMANN RD | 2024-04-02 | 9:36 | 2024-04-02 | 10:18 | 0.0066435 | 0.00016002 | 58 | 2408 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace defective eyebolt in crossarm at 11kV Pole 204478. | .
5155 |  | JE24009335 | 142B UPPER TAUMAHA ROAD MANUTAHI PATEA | Western | MANUTAHI | 2024-04-02 | 9:20 | 2024-04-02 | 13:01 | 0.014636 | 6.6215e-05 | 24 | 5305 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace badly spalling pole 729867 | .
5156 |  | JE24009391 | 217 PIAKO ROAD TURUA THAMES | Eastern | HAURAKI RD | 2024-04-02 | 9:30 | 2024-04-02 | 12:10 | 0.046797 | 0.00029245 | 106 | 16962 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | To replace 11kV crossarms at Poles O2462 & O2463. | .
5157 |  | JE24009539 | 1234 RICHMOND ROAD EVERETT PARK INGLEWOOD | Western | WAITARA RD | 2024-04-02 | 9:11 | 2024-04-02 | 14:26 | 0.035589 | 0.00011312 | 41 | 12899 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | PQI upgrade of Tx structure 811 to a 100KVA Double pole | .
5158 |  | JE24009625 | 1898 WAIHI WHANGAMATA ROAD WHIRITOA WHANGAMATA | Eastern | WHIRITOA | 2024-04-02 | 8:45 | 2024-04-02 | 9:24 | 0.00021777 | 5.5179e-06 | 2 | 79 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Replace 11kv binder at pole R1534 | .
5159 |  | JE24009633 | 119 TE TUTU STREET WHANGAMATA WHANGAMATA | Eastern | OTAHU RD | 2024-04-02 | 11:31 | 2024-04-02 | 13:20 | 0.011203 | 0.00010208 | 37 | 4061 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE 11KV SINGLE PIN XARM AT POLE R0694 (AS SHOWN ON SAP) ACTUAL POLE NUMBER IS 874807 | .
5160 |  | JE24010107 | 105 Old TeAroha road Matamata | Eastern | GORDON | 2024-04-02 | 10:00 | 2024-04-02 | 11:47 | 0.00029263 | 2.759e-06 | 1 | 106 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | REPLACE 11KV TERM ARMS AT ENS OF POWERCO OWNED SPUR LINE -NO POLE NUMBERS | .
5161 |  | JE24010607 | 1507 CHELTENHAM HUNTERVILLE ROAD WAITUNA WEST REWA | Western | WAITUNA | 2024-04-02 | 9:23 | 2024-04-11 | 13:21 | 0.024985 | 8.8287e-05 | 29 | 9056 | Planned | PLANNED SHUTDOWN - CAPITAL WORKS | Dowers Works - shutdown required for treecontrol guys install 2 sets of mid spans temp085 at pole P09718 and temp087 at pole P09711. leave links open and earthed for 2 weeks and backfeed in place Via N34 Scanpowers Works - Replace TX pole & re-install TX on pole P09729 and replace crossarms on poles P11997, P09700, P09702, P09703, P09730. | .
5162 |  | JE24011598 | WHAKAMARA | Western | WHAKAMARA | 2024-04-02 | 6:55 | 2024-04-02 | 8:51 | 0.00031906 | 2.759e-06 | 1 | 116 | Unplanned | WILDLIFE - POSSUM | Fuses Location: WH270 No. Fuses: 3 Fuse Amp Size: 6A TIME CLOSED: 0850 Cause: POSSUM Weather (wind/rain): FINE Follow up required (select advisory)? N USING 2R to add possum guards to poles without them Poles 725755 - 725767 installed possum guard | .
5163 |  | JE24011601 | TAVERNER ST | Western | TAVERNER ST | 2024-04-02 | 8:46 | 2024-04-02 | 11:54 | 0.0082894 | 4.4143e-05 | 16 | 3005 | Unplanned | UNKNOWN - CURSORY PATROLLED - CAUSE UNKNOWN | Faultman found line down at pole 820310 - suspect due to bird strike, line was isolated at Fuses 7542 to repair the lines. | .
5164 |  | JE24011642 | DYERVILLE | Western | DYERVILLE | 2024-04-02 | 9:58 | 2024-04-02 | 12:16 | 0.048598 | 0.00035867 | 130 | 17615 | Unplanned | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Faultman found broken DDO's on transformer T1350 while driving pass, line was isolated at ABS 11236/1 & Links 11236/6 to replace the full set of DDO's on the T1350 | .
5165 |  | JE24011686 | TAWHITI RD | Western | TAWHITI RD | 2024-04-02 | 12:45 | 2024-04-03 | 15:45 | 0.035791 | 0.00011864 | 43 | 12973 | Unplanned | VEGETATION - OUTSIDE ZONE | REGULATORY INFORMATION Voltage & Device ID: Rec 6560 // Sec 12438 Protection flags (nil where none): E/F C Ø CAUSE: Trees through lines Location: Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Cursory Weather (wind/rain): Calm LFI (Y/N + Comments): Nil Follow up Required (select advisory)? Additional fault restoration comments: Fireman would not let faultman into area to fix fault incase fire started up again, Customers left off over night. Digger and Men replaced pole and all good now | .
5166 |  | JE24011699 | WARATAH ST | Eastern | WARATAH ST | 2024-04-02 | 13:17 | 2024-04-06 | 10:28 | 0.13685 | 0.0015781 | 372 | 49601 | Unplanned | THIRD PARTY INTERFERENCE - DIG IN | REGULATORY INFORMATION Voltage & Device ID: 11kV CB 5 Protection flags (nil where none): E/F DEF Time CAUSE: 12 Maxine Place Digger hit Network cable on customers property Location: 12 Maxine Place Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Calm LFI (Y/N + Comments): Yes 13798/3 Follow up Required (select advisory)? Additional fault restoration comments: Update needed by customer Lindsey @ 0221980956 - 5/4/2024 Update: 06/04/2024 HV Cable damaged by 3rd party was repaired and TLB was closed under Emergency outage E00119 | .
5167 |  | JE24011711 | WOODS RD | Eastern | WOODS RD | 2024-04-02 | 14:16 | 2024-04-02 | 15:18 | 0.00017096 | 2.759e-06 | 1 | 62 | Unplanned | THIRD PARTY INTERFERENCE - OVERHEAD CONTACT | REGULATORY INFORMATION Voltage & Device ID: Farmer Rd CB 2 11kV Protection flags (nil where none): E/F C Phase CAUSE: Digger Hit O/H Lines Location: Near ABS 2117 Temp generation (state details when used): PERFORMANCE DETAIL DNO (number or state No): Circuit patrolled and type: Weather (wind/rain): Fine LFI (Y/N + Comments): Cause rung in by Sean Molloy Follow up Required (select advisory)? Additional fault restoration comments: Sean Rung with details of who hit lines. SUBTRANSMISSION DETAIL LOS to sub (no, or sub name): Circuit that tripped: DTF (KM): | .
5168 |  | JE24011731 | switch_12708:3 | Western | CITY 10 | 2024-04-02 | 17:45 | 2024-04-02 | 21:03 | 0.023967 | 0.00012139 | 44 | 8687 | Unplanned | THIRD PARTY INTERFERENCE - DIG IN | SW/Gear 12708. CITY SUB, CB10. No power to 2513N. Possible HV cable damage. Reported by Power Related Services. Generator connected for TFR 2513N 21:02 Cable to be repaired 03/04/24 | .
5169 |  | JE24011588 | HAURAKI RD | Eastern | HAURAKI RD | 2024-04-01 | 21:07 | 2024-04-02 | 3:10 | 0.013011 | 3.5867e-05 | 13 | 4716 | Unplanned | THIRD PARTY INTERFERENCE - VEHICLE DAMAGE | REGULATORY INFORMATION Voltage & Device ID: 11kV REC 9161/2 ARC at 20:08 Protection flags (nil where none): C Ø O/C CAUSE: Car vs Pole Location: Pole O1418 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Calm LFI (Y/N + Comments): Yes and then cleared at Pole O1088 & O12692. Follow up Required (select advisory)? No Additional fault restoration comments: Timeline of events: REC9161/2 ARC at 20:08 on C Ø O/C HAZARD called in by Fire Services of Car vs Pole on Campbell Road & SH25 Field Switcher arrived on site, confirmed Car vs Pole, will identify Pole number once area has been made safe. Backfeed put in via KPE6 using SEC 97241/2 closed in by NOC at 20:49. Isolation points being between ABS IC442 & ABS IC2626 - 4 ICP's with No Power during repairs down Campbell Road. Repairs are being carried out under Access Permit 1588-01 All repairs are completed and the network was returned to normal configuration. Full Power restored at 03:10 NOTES: According to the Field Switcher when he arrived on site the one conductor was on the ground and the remaining two were hanging low. Energized line on the ground. | .
5170 |  | JE24011590 | RANGITANUKU RD | Eastern | RANGITANUKU RD | 2024-04-01 | 22:20 | 2024-04-02 | 0:53 | 0.032858 | 0.00033935 | 123 | 11909 | Unplanned | WILDLIFE - POSSUM | REGULATORY INFORMATION Voltage & Device ID: 11kV SEC SP15 Protection flags (nil where none): E/F & O/C CAUSE: Two possum's found on the O/H Lines. (Separate locations) Location: Pole E1043 & Pole E1003 Temp generation (state details when used): No PERFORMANCE DETAIL DNO (number or state No): No Circuit patrolled and type: Yes Weather (wind/rain): Calm LFI (Y/N + Comments): Yes at Pole E12784 on C Ø outgoing. Follow up Required (select advisory)? Yes, check for possum guards. Additional fault restoration comments: NOC contacted the Field Switcher and informed him of the LFI at Pole E12784 that operated. To please investigate in the field and if correct then open at ABS 1145 Once the above was carried out. NOC closed in SEC SP15 at 23:13 Field staff then carried out a Line Patrol from ABS 1145 towards SWER REC 9902/2 including all Spur Lines. Two possum's were found at separate locations and removed via hot stick. After this was carried out ABS 1145 was closed in at 00:52 with full Power being restored to all ICP's. | .
5171 |  | ¹ Extend table as necessary to disclose information for all individual interruptions